## Summary
Metric | Grid-Only | Grid+BESS | Grid+BESS+DR
ALCC (M€/yr) | 17.311 | 17.2873 | 16.1429
LCOE (EUR/MWh) | 197.6143 | 197.3433 | 184.2798
Emissions (tCO₂/yr) | 19710 | 19955.777 | 19955.777
Peak Import (MW) | 10 | 20 | 20
BESS Cycles/yr | 0 | 1037.725 | 1037.725
Payback (years) | N/A | 295.1904 | 5.9978
Annual Savings (€) | 0 | 23733.8319 | 1168098.8319

## Assumptions
Parameter | Thesis Value | Updated Value | Unit | Source
DC Load | 10 | 10 | MW | Group agreement
Grid Connection (MIC) | 20 | 20 | MW | 2× DC load for BESS charging headroom
Grid CO₂ Intensity | 225 | 225 | gCO₂/kWh | SEAI
TOU Tariff — Day | 65.03 | 65.03 | EUR/MWh | Thesis Table 3.2
TOU Tariff — Peak | 66.4 | 66.4 | EUR/MWh | Thesis Table 3.2
TOU Tariff — Night | 53.53 | 53.53 | EUR/MWh | Thesis Table 3.2
Grid Subscription Fee | 4403376 | 4403376 | EUR/yr | Thesis Table 3.3
BESS Power CapEx | 675 | 221.4 | EUR/kW | NREL ATB 2025 / NREL ATB 2024 Adv.
BESS Energy CapEx | 165.6 | 239.6 | EUR/kWh | NREL ATB 2025 / NREL ATB 2024 Adv.
BESS Power O&M | 16.9 | 5.5 | EUR/kW-yr | NREL ATB 2025 / NREL ATB 2024 Adv.
BESS Energy O&M | 4.11 | 6 | EUR/kWh-yr | NREL ATB 2025 / NREL ATB 2024 Adv.
Round-Trip Efficiency | 95% | 95% |  | Thesis Table 3.7
BESS Lifetime | 15 | 15 | years | Thesis Table 3.7
WACC | 8% | 8% |  | Thesis assumption
Capital Recovery Factor | 0.11683 | 0.11683 |  | Computed
Initial SoC | 50% | 50% | of E_BESS | Thesis assumption
Spot Price Source | Synthetic | Synthetic |  | Calibrated to 2023 I-SEM stats

## Baseline
Month | Hours | Avg Spot (EUR/MWh) | Avg TOU (EUR/MWh) | Import (MWh) | Energy Cost (EUR) | Emissions (tCO₂)
January | 744 | 107.5607 | 58.7118 | 7440 | 1237067.4034 | 1674
February | 672 | 99.3817 | 58.7455 | 6720 | 1062614.8352 | 1512
March | 744 | 94.151 | 58.9474 | 7440 | 1139051.7376 | 1674
April | 720 | 74.4869 | 58.3978 | 7200 | 956769.8681 | 1620
May | 744 | 75.0896 | 58.9474 | 7440 | 997234.9819 | 1674
June | 720 | 81.6781 | 58.8846 | 7200 | 1012051.0899 | 1620
July | 744 | 76.3834 | 58.4763 | 7440 | 1003356.1467 | 1674
August | 744 | 77.3052 | 58.9474 | 7440 | 1013719.0555 | 1674
September | 720 | 91.2725 | 58.6412 | 7200 | 1079378.3693 | 1620
October | 744 | 87.4124 | 58.7118 | 7440 | 1087163.9898 | 1674
November | 720 | 94.7329 | 58.8846 | 7200 | 1106045.8103 | 1620
December | 744 | 104.5857 | 58.4763 | 7440 | 1213181.4199 | 1674

## BESS Sizing
Config | P (MW) | τ (h) | E (MWh) | Annual BESS Cost (€) [Thesis] | Total Cost (€) [Thesis] | Savings (€) [Thesis] | Annual BESS Cost (€) [Updated] | Total Cost (€) [Updated] | Savings (€) [Updated] | Payback (yr) [Updated]
2MW/2MWh | 2 | 1 | 2 | 238433.8309 | 17411981.0478 | -100970.3401 | 130716.8404 | 17304264.0573 | 6746.6504 | 136.6604
2MW/4MWh | 2 | 2 | 4 | 285347.7762 | 17392910.1592 | -81899.4515 | 198701.5584 | 17306263.9413 | 4746.7664 | 295.1904
2MW/8MWh | 2 | 4 | 8 | 379175.6668 | 17423953.4702 | -112942.7625 | 334670.9942 | 17379448.7977 | -68438.09 | N/A
4MW/4MWh | 4 | 1 | 4 | 476867.6619 | 17512951.3879 | -201940.6802 | 261433.6809 | 17297517.4068 | 13493.3009 | 136.6604
4MW/8MWh | 4 | 2 | 8 | 570695.5525 | 17474809.6107 | -163798.903 | 397403.1167 | 17301517.1749 | 9493.5328 | 295.1904
4MW/16MWh | 4 | 4 | 16 | 758351.3336 | 17536896.2328 | -225885.5251 | 669341.9885 | 17447886.8877 | -136876.18 | N/A
6MW/6MWh | 6 | 1 | 6 | 715301.4928 | 17613921.728 | -302911.0203 | 392150.5213 | 17290770.7564 | 20239.9513 | 136.6604
6MW/12MWh | 6 | 2 | 12 | 856043.3287 | 17556709.0622 | -245698.3545 | 596104.6751 | 17296770.4086 | 14240.2991 | 295.1904
6MW/24MWh | 6 | 4 | 24 | 1137527.0004 | 17649838.9953 | -338828.2876 | 1004012.9827 | 17516324.9776 | -205314.27 | N/A
8MW/8MWh | 8 | 1 | 8 | 953735.3238 | 17714892.0681 | -403881.3604 | 522867.3617 | 17284024.106 | 26986.6017 | 136.6604
8MW/16MWh | 8 | 2 | 16 | 1141391.1049 | 17638608.5136 | -327597.806 | 794806.2335 | 17292023.6422 | 18987.0655 | 295.1904
8MW/32MWh | 8 | 4 | 32 | 1516702.6672 | 17762781.7579 | -451771.0502 | 1338683.9769 | 17584763.0676 | -273752.3599 | N/A
10MW/10MWh | 10 | 1 | 10 | 1192169.1547 | 17815862.4081 | -504851.7004 | 653584.2022 | 17277277.4556 | 33733.2521 | 136.6604
10MW/20MWh | 10 | 2 | 20 | 1426738.8811 | 17720507.9651 | -409497.2574 | 993507.7918 | 17287276.8758 | 23733.8319 | 295.1904
10MW/40MWh | 10 | 4 | 40 | 1895878.334 | 17875724.5204 | -564713.8127 | 1673354.9712 | 17653201.1576 | -342190.4499 | N/A

## Optimal Dispatch
Hour | Date | Spot (EUR/MWh) | TOU (EUR/MWh) | Grid Import (MW) | Charge (MW) | Discharge (MW) | SoC (MWh) | Hourly Cost (EUR)
0 | 2023-01-01 00:00 | 103.2914 | 53.53 | 0 | 0 | 10 | 0 | 0
1 | 2023-01-01 01:00 | 94.1979 | 53.53 | 10 | 0 | 0 | 0 | 1477.2793
2 | 2023-01-01 02:00 | 87.2106 | 53.53 | 10 | 0 | 0 | 0 | 1407.4061
3 | 2023-01-01 03:00 | 89.0484 | 53.53 | 10 | 0 | 0 | 0 | 1425.7839
4 | 2023-01-01 04:00 | 69.8216 | 53.53 | 20 | 10 | 0 | 9.5 | 2467.0326
5 | 2023-01-01 05:00 | 72.8137 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1396.43
6 | 2023-01-01 06:00 | -49.8936 | 53.53 | 20 | 10 | 0 | 20 | 72.7275
7 | 2023-01-01 07:00 | 98.6355 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 76.0828
8 | 2023-01-01 08:00 | -30.1508 | 53.53 | 20 | 10 | 0 | 20 | 467.5838
9 | 2023-01-01 09:00 | 105.2535 | 53.53 | 10 | 0 | 0 | 20 | 1587.8354
10 | 2023-01-01 10:00 | 118.4456 | 53.53 | 10 | 0 | 0 | 20 | 1719.7563
11 | 2023-01-01 11:00 | 117.4685 | 53.53 | 10 | 0 | 0 | 20 | 1709.985
12 | 2023-01-01 12:00 | 111.3985 | 53.53 | 10 | 0 | 0 | 20 | 1649.2847
13 | 2023-01-01 13:00 | 120.9579 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 87.2439
14 | 2023-01-01 14:00 | 114.6624 | 53.53 | 10 | 0 | 0 | 10.5 | 1681.9242
15 | 2023-01-01 15:00 | 105.2173 | 53.53 | 20 | 10 | 0 | 20 | 3174.9457
16 | 2023-01-01 16:00 | 113.8227 | 53.53 | 10 | 0 | 0 | 20 | 1673.5271
17 | 2023-01-01 17:00 | 119.6486 | 53.53 | 10 | 0 | 0 | 20 | 1731.7863
18 | 2023-01-01 18:00 | 133.4364 | 53.53 | 0 | 0 | 10 | 10 | 0
19 | 2023-01-01 19:00 | 125.5267 | 53.53 | 0 | 0 | 10 | 0 | 0
20 | 2023-01-01 20:00 | 104.5496 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1663.9956
21 | 2023-01-01 21:00 | 101.2792 | 53.53 | 20 | 10 | 0 | 10 | 3096.1836
22 | 2023-01-01 22:00 | 116.9747 | 53.53 | 0 | 0 | 10 | 0 | 0
23 | 2023-01-01 23:00 | 99.7658 | 53.53 | 10 | 0 | 0 | 0 | 1532.9579
24 | 2023-01-02 00:00 | 105.8837 | 53.53 | 10 | 0 | 0 | 0 | 1594.1368
25 | 2023-01-02 01:00 | 106.392 | 53.53 | 10 | 0 | 0 | 0 | 1599.2202
26 | 2023-01-02 02:00 | 93.2271 | 53.53 | 10 | 0 | 0 | 0 | 1467.5707
27 | 2023-01-02 03:00 | 91.795 | 53.53 | 20 | 10 | 0 | 9.5 | 2906.5005
28 | 2023-01-02 04:00 | 92.1936 | 53.53 | 20 | 10 | 0 | 19 | 2914.4721
29 | 2023-01-02 05:00 | 92.3476 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1612.331
30 | 2023-01-02 06:00 | 111.4287 | 53.53 | 10 | 0 | 0 | 20 | 1649.5873
31 | 2023-01-02 07:00 | 106.0287 | 53.53 | 10 | 0 | 0 | 20 | 1595.5869
32 | 2023-01-02 08:00 | 115.3371 | 65.03 | 0 | 0 | 10 | 10 | 0
33 | 2023-01-02 09:00 | 113.4829 | 65.03 | 1 | 0 | 9 | 1 | 178.5129
34 | 2023-01-02 10:00 | -74.0722 | 65.03 | 20 | 10 | 0 | 10.5 | -180.8438
35 | 2023-01-02 11:00 | -23.6059 | 65.03 | 20 | 10 | 0 | 20 | 828.4818
36 | 2023-01-02 12:00 | 118.0581 | 65.03 | 10 | 0 | 0 | 20 | 1830.8814
37 | 2023-01-02 13:00 | 113.3285 | 65.03 | 10 | 0 | 0 | 20 | 1783.5851
38 | 2023-01-02 14:00 | 113.4201 | 65.03 | 10 | 0 | 0 | 20 | 1784.501
39 | 2023-01-02 15:00 | 124.2865 | 65.03 | 10 | 0 | 0 | 20 | 1893.1648
40 | 2023-01-02 16:00 | 125.1431 | 65.03 | 10 | 0 | 0 | 20 | 1901.7308
41 | 2023-01-02 17:00 | 138.3226 | 66.4 | 0 | 0 | 10 | 10 | 0
42 | 2023-01-02 18:00 | 129.3737 | 66.4 | 10 | 0 | 0 | 10 | 1957.7368
43 | 2023-01-02 19:00 | 135.7016 | 65.03 | 0 | 0 | 10 | 0 | 0
44 | 2023-01-02 20:00 | 114.7889 | 65.03 | 10 | 0 | 0 | 0 | 1798.1895
45 | 2023-01-02 21:00 | 115.5935 | 65.03 | 10 | 0 | 0 | 0 | 1806.2347
46 | 2023-01-02 22:00 | 121.3679 | 65.03 | 10 | 0 | 0 | 0 | 1863.9791
47 | 2023-01-02 23:00 | 110.6328 | 53.53 | 10 | 0 | 0 | 0 | 1641.628
48 | 2023-01-03 00:00 | 114.5458 | 53.53 | 10 | 0 | 0 | 0 | 1680.7577
49 | 2023-01-03 01:00 | 109.4103 | 53.53 | 10 | 0 | 0 | 0 | 1629.4032
50 | 2023-01-03 02:00 | 91.1635 | 53.53 | 10 | 0 | 0 | 0 | 1446.9352
51 | 2023-01-03 03:00 | 94.111 | 53.53 | 10 | 0 | 0 | 0 | 1476.41
52 | 2023-01-03 04:00 | 80.0452 | 53.53 | 20 | 10 | 0 | 9.5 | 2671.5044
53 | 2023-01-03 05:00 | 86.6121 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1548.9395
54 | 2023-01-03 06:00 | 85.6081 | 53.53 | 20 | 10 | 0 | 20 | 2782.7622
55 | 2023-01-03 07:00 | 104.5379 | 53.53 | 10 | 0 | 0 | 20 | 1580.6792
56 | 2023-01-03 08:00 | 116.9176 | 65.03 | 10 | 0 | 0 | 20 | 1819.4761
57 | 2023-01-03 09:00 | 133.0467 | 65.03 | 0 | 0 | 10 | 10 | 0
58 | 2023-01-03 10:00 | 113.1794 | 65.03 | 20 | 10 | 0 | 19.5 | 3564.1886
59 | 2023-01-03 11:00 | 127.3252 | 65.03 | 0 | 0 | 10 | 9.5 | 0
60 | 2023-01-03 12:00 | 108.988 | 65.03 | 20 | 10 | 0 | 19 | 3480.3609
61 | 2023-01-03 13:00 | 116.5087 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 2006.4805
62 | 2023-01-03 14:00 | 120.1492 | 65.03 | 10 | 0 | 0 | 20 | 1851.7924
63 | 2023-01-03 15:00 | 123.7053 | 65.03 | 10 | 0 | 0 | 20 | 1887.3528
64 | 2023-01-03 16:00 | 124.8443 | 65.03 | 10 | 0 | 0 | 20 | 1898.7431
65 | 2023-01-03 17:00 | 140.6162 | 66.4 | 0 | 0 | 10 | 10 | 0
66 | 2023-01-03 18:00 | 131.415 | 66.4 | 0 | 0 | 10 | 0 | 0
67 | 2023-01-03 19:00 | 130.6604 | 65.03 | 10 | 0 | 0 | 0 | 1956.9041
68 | 2023-01-03 20:00 | 121.2371 | 65.03 | 10 | 0 | 0 | 0 | 1862.6713
69 | 2023-01-03 21:00 | 112.5039 | 65.03 | 10 | 0 | 0 | 0 | 1775.3392
70 | 2023-01-03 22:00 | 105.9486 | 65.03 | 10 | 0 | 0 | 0 | 1709.7864
71 | 2023-01-03 23:00 | 101.6928 | 53.53 | 20 | 10 | 0 | 9.5 | 3104.4562
72 | 2023-01-04 00:00 | 102.8717 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1646.3342
73 | 2023-01-04 01:00 | 112.9194 | 53.53 | 0 | 0 | 10 | 0 | 0
74 | 2023-01-04 02:00 | 89.9896 | 53.53 | 20 | 10 | 0 | 9.5 | 2870.393
75 | 2023-01-04 03:00 | 94.6523 | 53.53 | 10 | 0 | 0 | 9.5 | 1481.8235
76 | 2023-01-04 04:00 | 85.8908 | 53.53 | 20 | 10 | 0 | 19 | 2788.4155
77 | 2023-01-04 05:00 | 90.1161 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1587.6672
78 | 2023-01-04 06:00 | 94.0594 | 53.53 | 10 | 0 | 0 | 20 | 1475.894
79 | 2023-01-04 07:00 | 106.6826 | 53.53 | 10 | 0 | 0 | 20 | 1602.1261
80 | 2023-01-04 08:00 | 122.5699 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 93.8
81 | 2023-01-04 09:00 | 114.3957 | 65.03 | 10 | 0 | 0 | 10.5 | 1794.2571
82 | 2023-01-04 10:00 | 116.3184 | 65.03 | 10 | 0 | 0 | 10.5 | 1813.4845
83 | 2023-01-04 11:00 | 116.1931 | 65.03 | 10 | 0 | 0 | 10.5 | 1812.2313
84 | 2023-01-04 12:00 | 111.362 | 65.03 | 20 | 10 | 0 | 20 | 3527.8399
85 | 2023-01-04 13:00 | 122.8309 | 65.03 | 10 | 0 | 0 | 20 | 1878.6087
86 | 2023-01-04 14:00 | 115.6144 | 65.03 | 10 | 0 | 0 | 20 | 1806.4443
87 | 2023-01-04 15:00 | 118.9922 | 65.03 | 10 | 0 | 0 | 20 | 1840.2219
88 | 2023-01-04 16:00 | 122.7769 | 65.03 | 10 | 0 | 0 | 20 | 1878.0688
89 | 2023-01-04 17:00 | 137.482 | 66.4 | 0 | 0 | 10 | 10 | 0
90 | 2023-01-04 18:00 | 139.4216 | 66.4 | 0 | 0 | 10 | 0 | 0
91 | 2023-01-04 19:00 | 133.1705 | 65.03 | 10 | 0 | 0 | 0 | 1982.0047
92 | 2023-01-04 20:00 | 110.9169 | 65.03 | 10 | 0 | 0 | 0 | 1759.4688
93 | 2023-01-04 21:00 | 113.3075 | 65.03 | 10 | 0 | 0 | 0 | 1783.3751
94 | 2023-01-04 22:00 | 103.9678 | 65.03 | 10 | 0 | 0 | 0 | 1689.9785
95 | 2023-01-04 23:00 | 100.0939 | 53.53 | 10 | 0 | 0 | 0 | 1536.2395
96 | 2023-01-05 00:00 | 100.7099 | 53.53 | 10 | 0 | 0 | 0 | 1542.3985
97 | 2023-01-05 01:00 | 102.4341 | 53.53 | 10 | 0 | 0 | 0 | 1559.6406
98 | 2023-01-05 02:00 | 92.0838 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1609.4159
99 | 2023-01-05 03:00 | 82.9514 | 53.53 | 20 | 10 | 0 | 10.5 | 2729.629
100 | 2023-01-05 04:00 | 86.2171 | 53.53 | 20 | 10 | 0 | 20 | 2794.9411
101 | 2023-01-05 05:00 | 100.8143 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 77.1721
102 | 2023-01-05 06:00 | 86.3642 | 53.53 | 20 | 10 | 0 | 20 | 2797.8832
103 | 2023-01-05 07:00 | 115.0893 | 53.53 | 10 | 0 | 0 | 20 | 1686.1933
104 | 2023-01-05 08:00 | 112.7913 | 65.03 | 10 | 0 | 0 | 20 | 1778.2129
105 | 2023-01-05 09:00 | 117.404 | 65.03 | 10 | 0 | 0 | 20 | 1824.3404
106 | 2023-01-05 10:00 | 112.6985 | 65.03 | 10 | 0 | 0 | 20 | 1777.2854
107 | 2023-01-05 11:00 | 116.4806 | 65.03 | 10 | 0 | 0 | 20 | 1815.1059
108 | 2023-01-05 12:00 | 126.0662 | 65.03 | 0 | 0 | 10 | 10 | 0
109 | 2023-01-05 13:00 | 108.7882 | 65.03 | 20 | 10 | 0 | 19.5 | 3476.3631
110 | 2023-01-05 14:00 | 122.3783 | 65.03 | 10 | 0 | 0 | 19.5 | 1874.0833
111 | 2023-01-05 15:00 | 120.7464 | 65.03 | 10 | 0 | 0 | 19.5 | 1857.7644
112 | 2023-01-05 16:00 | 114.8167 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1893.1236
113 | 2023-01-05 17:00 | 125.0991 | 66.4 | 10 | 0 | 0 | 20 | 1914.9907
114 | 2023-01-05 18:00 | 134.4452 | 66.4 | 0 | 0 | 10 | 10 | 0
115 | 2023-01-05 19:00 | 130.2265 | 65.03 | 0 | 0 | 10 | 0 | 0
116 | 2023-01-05 20:00 | 115.7057 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1902.4813
117 | 2023-01-05 21:00 | 114.0627 | 65.03 | 20 | 10 | 0 | 10 | 3581.8547
118 | 2023-01-05 22:00 | 129.3217 | 65.03 | 0 | 0 | 10 | 0 | 0
119 | 2023-01-05 23:00 | 107.1661 | 53.53 | 10 | 0 | 0 | 0 | 1606.9608
120 | 2023-01-06 00:00 | 102.2887 | 53.53 | 10 | 0 | 0 | 0 | 1558.1867
121 | 2023-01-06 01:00 | 110.2797 | 53.53 | 10 | 0 | 0 | 0 | 1638.0969
122 | 2023-01-06 02:00 | 90.6039 | 53.53 | 20 | 10 | 0 | 9.5 | 2882.6789
123 | 2023-01-06 03:00 | 101.4843 | 53.53 | 10 | 0 | 0 | 9.5 | 1550.1432
124 | 2023-01-06 04:00 | 96.0161 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1652.8776
125 | 2023-01-06 05:00 | 91.7234 | 53.53 | 20 | 10 | 0 | 20 | 2905.0674
126 | 2023-01-06 06:00 | 102.6768 | 53.53 | 10 | 0 | 0 | 20 | 1562.0683
127 | 2023-01-06 07:00 | 101.3991 | 53.53 | 10 | 0 | 0 | 20 | 1549.2911
128 | 2023-01-06 08:00 | 114.5325 | 65.03 | 10 | 0 | 0 | 20 | 1795.6252
129 | 2023-01-06 09:00 | 112.8312 | 65.03 | 10 | 0 | 0 | 20 | 1778.6124
130 | 2023-01-06 10:00 | 116.1392 | 65.03 | 10 | 0 | 0 | 20 | 1811.692
131 | 2023-01-06 11:00 | 110.4398 | 65.03 | 10 | 0 | 0 | 20 | 1754.6977
132 | 2023-01-06 12:00 | 124.146 | 65.03 | 0 | 0 | 10 | 10 | 0
133 | 2023-01-06 13:00 | 117.286 | 65.03 | 10 | 0 | 0 | 10 | 1823.1598
134 | 2023-01-06 14:00 | 109.9792 | 65.03 | 20 | 10 | 0 | 19.5 | 3500.1847
135 | 2023-01-06 15:00 | 112.3324 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1866.9727
136 | 2023-01-06 16:00 | 121.3638 | 65.03 | 10 | 0 | 0 | 20 | 1863.9379
137 | 2023-01-06 17:00 | 141.0451 | 66.4 | 10 | 0 | 0 | 20 | 2074.4513
138 | 2023-01-06 18:00 | 154.4066 | 66.4 | 0 | 0 | 10 | 10 | 0
139 | 2023-01-06 19:00 | 168.8198 | 65.03 | 0 | 0 | 10 | 0 | 0
140 | 2023-01-06 20:00 | 117.2078 | 65.03 | 10 | 0 | 0 | 0 | 1822.3784
141 | 2023-01-06 21:00 | 107.477 | 65.03 | 10 | 0 | 0 | 0 | 1725.0698
142 | 2023-01-06 22:00 | 102.0857 | 65.03 | 10 | 0 | 0 | 0 | 1671.1571
143 | 2023-01-06 23:00 | 110.989 | 53.53 | 10 | 0 | 0 | 0 | 1645.1897
144 | 2023-01-07 00:00 | 95.4878 | 53.53 | 10 | 0 | 0 | 0 | 1490.178
145 | 2023-01-07 01:00 | 97.9694 | 53.53 | 10 | 0 | 0 | 0 | 1514.994
146 | 2023-01-07 02:00 | 76.7044 | 53.53 | 20 | 10 | 0 | 9.5 | 2604.6884
147 | 2023-01-07 03:00 | 79.8644 | 53.53 | 20 | 10 | 0 | 19 | 2667.8873
148 | 2023-01-07 04:00 | 90.3194 | 53.53 | 0 | 0 | 10 | 9 | 0
149 | 2023-01-07 05:00 | 82.1044 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1570.5031
150 | 2023-01-07 06:00 | 79.7364 | 53.53 | 20 | 10 | 0 | 20 | 2665.3282
151 | 2023-01-07 07:00 | 94.2217 | 53.53 | 10 | 0 | 0 | 20 | 1477.5172
152 | 2023-01-07 08:00 | 101.0252 | 53.53 | 10 | 0 | 0 | 20 | 1545.5515
153 | 2023-01-07 09:00 | 107.5046 | 53.53 | 10 | 0 | 0 | 20 | 1610.3457
154 | 2023-01-07 10:00 | 110.4982 | 53.53 | 10 | 0 | 0 | 20 | 1640.2817
155 | 2023-01-07 11:00 | 128.3877 | 53.53 | 0 | 0 | 10 | 10 | 0
156 | 2023-01-07 12:00 | 111.8947 | 53.53 | 10 | 0 | 0 | 10 | 1654.2471
157 | 2023-01-07 13:00 | 119.4705 | 53.53 | 0 | 0 | 10 | 0 | 0
158 | 2023-01-07 14:00 | 107.4206 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1778.9272
159 | 2023-01-07 15:00 | 103.4192 | 53.53 | 20 | 10 | 0 | 10.5 | 3138.9835
160 | 2023-01-07 16:00 | 104.6136 | 53.53 | 20 | 10 | 0 | 20 | 3162.8719
161 | 2023-01-07 17:00 | 121.0101 | 53.53 | 0 | 0 | 10 | 10 | 0
162 | 2023-01-07 18:00 | 148.2412 | 53.53 | 0 | 0 | 10 | 0 | 0
163 | 2023-01-07 19:00 | 120.4382 | 53.53 | 10 | 0 | 0 | 0 | 1739.6823
164 | 2023-01-07 20:00 | 113.0486 | 53.53 | 10 | 0 | 0 | 0 | 1665.7863
165 | 2023-01-07 21:00 | 99.966 | 53.53 | 20 | 10 | 0 | 9.5 | 3069.9208
166 | 2023-01-07 22:00 | 113.9591 | 53.53 | 0.5 | 0 | 9.5 | 0 | 83.7445
167 | 2023-01-07 23:00 | 103.9588 | 53.53 | 10 | 0 | 0 | 0 | 1574.8876
168 | 2023-01-08 00:00 | 99.7507 | 53.53 | 10 | 0 | 0 | 0 | 1532.807
169 | 2023-01-08 01:00 | 100.5944 | 53.53 | 10 | 0 | 0 | 0 | 1541.2445
170 | 2023-01-08 02:00 | 76.4396 | 53.53 | 20 | 10 | 0 | 9.5 | 2599.393
171 | 2023-01-08 03:00 | 84.478 | 53.53 | 1.5 | 0 | 8.5 | 1 | 207.012
172 | 2023-01-08 04:00 | 77.7086 | 53.53 | 10 | 0 | 0 | 1 | 1312.3857
173 | 2023-01-08 05:00 | 73.2067 | 53.53 | 20 | 10 | 0 | 10.5 | 2534.7349
174 | 2023-01-08 06:00 | 72.9371 | 53.53 | 20 | 10 | 0 | 20 | 2529.3426
175 | 2023-01-08 07:00 | 102.2268 | 53.53 | 10 | 0 | 0 | 20 | 1557.5681
176 | 2023-01-08 08:00 | 126.0475 | 53.53 | 0 | 0 | 10 | 10 | 0
177 | 2023-01-08 09:00 | 112.1275 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1743.7632
178 | 2023-01-08 10:00 | 110.0242 | 53.53 | 20 | 10 | 0 | 20 | 3271.0833
179 | 2023-01-08 11:00 | 113.1366 | 53.53 | 10 | 0 | 0 | 20 | 1666.666
180 | 2023-01-08 12:00 | 122.8894 | 53.53 | 0 | 0 | 10 | 10 | 0
181 | 2023-01-08 13:00 | 112.599 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1748.7266
182 | 2023-01-08 14:00 | 107.9987 | 53.53 | 20 | 10 | 0 | 20 | 3230.575
183 | 2023-01-08 15:00 | 120.7382 | 53.53 | 10 | 0 | 0 | 20 | 1742.6818
184 | 2023-01-08 16:00 | 114.33 | 53.53 | 10 | 0 | 0 | 20 | 1678.5995
185 | 2023-01-08 17:00 | 140.5289 | 53.53 | 0 | 0 | 10 | 10 | 0
186 | 2023-01-08 18:00 | 127.311 | 53.53 | 0 | 0 | 10 | 0 | 0
187 | 2023-01-08 19:00 | 118.2126 | 53.53 | 10 | 0 | 0 | 0 | 1717.4265
188 | 2023-01-08 20:00 | 97.4821 | 53.53 | 20 | 10 | 0 | 9.5 | 3020.2427
189 | 2023-01-08 21:00 | 121.9222 | 53.53 | 10 | 0 | 0 | 9.5 | 1754.5218
190 | 2023-01-08 22:00 | 122.8272 | 53.53 | 0.5 | 0 | 9.5 | 0 | 88.1786
191 | 2023-01-08 23:00 | 99.5875 | 53.53 | 20 | 10 | 0 | 9.5 | 3062.3505
192 | 2023-01-09 00:00 | 106.1834 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1681.1941
193 | 2023-01-09 01:00 | 122.6552 | 53.53 | 0 | 0 | 10 | 0 | 0
194 | 2023-01-09 02:00 | 81.8334 | 53.53 | 20 | 10 | 0 | 9.5 | 2707.269
195 | 2023-01-09 03:00 | 83.013 | 53.53 | 20 | 10 | 0 | 19 | 2730.8601
196 | 2023-01-09 04:00 | 94.2203 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 221.6255
197 | 2023-01-09 05:00 | 86.1072 | 53.53 | 20 | 10 | 0 | 20 | 2792.7446
198 | 2023-01-09 06:00 | 88.8599 | 53.53 | 10 | 0 | 0 | 20 | 1423.8992
199 | 2023-01-09 07:00 | 107.7021 | 53.53 | 10 | 0 | 0 | 20 | 1612.3205
200 | 2023-01-09 08:00 | 121.5628 | 65.03 | 10 | 0 | 0 | 20 | 1865.9276
201 | 2023-01-09 09:00 | 132.0328 | 65.03 | 0 | 0 | 10 | 10 | 0
202 | 2023-01-09 10:00 | 119.587 | 65.03 | 10 | 0 | 0 | 10 | 1846.1701
203 | 2023-01-09 11:00 | 124.2259 | 65.03 | 0 | 0 | 10 | 0 | 0
204 | 2023-01-09 12:00 | 107.4136 | 65.03 | 20 | 10 | 0 | 9.5 | 3448.8726
205 | 2023-01-09 13:00 | 118.5356 | 65.03 | 10 | 0 | 0 | 9.5 | 1835.6558
206 | 2023-01-09 14:00 | 113.3106 | 65.03 | 10 | 0 | 0 | 9.5 | 1783.406
207 | 2023-01-09 15:00 | 111.2421 | 65.03 | 20 | 10 | 0 | 19 | 3525.441
208 | 2023-01-09 16:00 | 113.1083 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1968.8969
209 | 2023-01-09 17:00 | 131.5139 | 66.4 | 0 | 0 | 10 | 10 | 0
210 | 2023-01-09 18:00 | 141.804 | 66.4 | 0 | 0 | 10 | 0 | 0
211 | 2023-01-09 19:00 | 125.6912 | 65.03 | 10 | 0 | 0 | 0 | 1907.2124
212 | 2023-01-09 20:00 | 114.1291 | 65.03 | 10 | 0 | 0 | 0 | 1791.591
213 | 2023-01-09 21:00 | 110.5184 | 65.03 | 10 | 0 | 0 | 0 | 1755.4844
214 | 2023-01-09 22:00 | 111.5577 | 65.03 | 10 | 0 | 0 | 0 | 1765.8769
215 | 2023-01-09 23:00 | 117.6727 | 53.53 | 10 | 0 | 0 | 0 | 1712.0271
216 | 2023-01-10 00:00 | 113.2782 | 53.53 | 10 | 0 | 0 | 0 | 1668.082
217 | 2023-01-10 01:00 | 121.2394 | 53.53 | 10 | 0 | 0 | 0 | 1747.6943
218 | 2023-01-10 02:00 | 87.766 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1561.6922
219 | 2023-01-10 03:00 | 84.1876 | 53.53 | 20 | 10 | 0 | 10.5 | 2754.3519
220 | 2023-01-10 04:00 | 87.2745 | 53.53 | 20 | 10 | 0 | 20 | 2816.09
221 | 2023-01-10 05:00 | 90.7848 | 53.53 | 10 | 0 | 0 | 20 | 1443.1482
222 | 2023-01-10 06:00 | 90.2583 | 53.53 | 10 | 0 | 0 | 20 | 1437.8831
223 | 2023-01-10 07:00 | 101.9558 | 53.53 | 10 | 0 | 0 | 20 | 1554.8578
224 | 2023-01-10 08:00 | 119.5863 | 65.03 | 10 | 0 | 0 | 20 | 1846.1628
225 | 2023-01-10 09:00 | 120.67 | 65.03 | 10 | 0 | 0 | 20 | 1856.9998
226 | 2023-01-10 10:00 | 147.1015 | 65.03 | 0 | 0 | 10 | 10 | 0
227 | 2023-01-10 11:00 | 137.799 | 65.03 | 0 | 0 | 10 | 0 | 0
228 | 2023-01-10 12:00 | 113.2524 | 65.03 | 20 | 10 | 0 | 9.5 | 3565.6476
229 | 2023-01-10 13:00 | 116.8332 | 65.03 | 10 | 0 | 0 | 9.5 | 1818.6323
230 | 2023-01-10 14:00 | 110.0148 | 65.03 | 20 | 10 | 0 | 19 | 3500.896
231 | 2023-01-10 15:00 | 114.8384 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1988.0187
232 | 2023-01-10 16:00 | 121.381 | 65.03 | 10 | 0 | 0 | 20 | 1864.1102
233 | 2023-01-10 17:00 | 144.7945 | 66.4 | 0 | 0 | 10 | 10 | 0
234 | 2023-01-10 18:00 | 128.9869 | 66.4 | 0 | 0 | 10 | 0 | 0
235 | 2023-01-10 19:00 | 129.4436 | 65.03 | 10 | 0 | 0 | 0 | 1944.736
236 | 2023-01-10 20:00 | 102.0255 | 65.03 | 20 | 10 | 0 | 9.5 | 3341.1108
237 | 2023-01-10 21:00 | 112.7076 | 65.03 | 0.5 | 0 | 9.5 | 0 | 88.8688
238 | 2023-01-10 22:00 | 107.0752 | 65.03 | 10 | 0 | 0 | 0 | 1721.0521
239 | 2023-01-10 23:00 | 105.2268 | 53.53 | 10 | 0 | 0 | 0 | 1587.568
240 | 2023-01-11 00:00 | 103.1157 | 53.53 | 10 | 0 | 0 | 0 | 1566.4573
241 | 2023-01-11 01:00 | 108.2012 | 53.53 | 10 | 0 | 0 | 0 | 1617.3124
242 | 2023-01-11 02:00 | 78.6529 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1460.9694
243 | 2023-01-11 03:00 | 79.9974 | 53.53 | 10 | 0 | 0 | 1 | 1335.2739
244 | 2023-01-11 04:00 | -21.6336 | 53.53 | 20 | 10 | 0 | 10.5 | 637.928
245 | 2023-01-11 05:00 | -56.277 | 53.53 | 20 | 10 | 0 | 20 | -54.9397
246 | 2023-01-11 06:00 | 81.8887 | 53.53 | 10 | 0 | 0 | 20 | 1354.1874
247 | 2023-01-11 07:00 | 127.2762 | 53.53 | 10 | 0 | 0 | 20 | 1808.062
248 | 2023-01-11 08:00 | 153.6619 | 65.03 | 0 | 0 | 10 | 10 | 0
249 | 2023-01-11 09:00 | 111.4896 | 65.03 | 20 | 10 | 0 | 19.5 | 3530.3926
250 | 2023-01-11 10:00 | 116.2835 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1908.5635
251 | 2023-01-11 11:00 | 121.5958 | 65.03 | 10 | 0 | 0 | 20 | 1866.2582
252 | 2023-01-11 12:00 | 135.8906 | 65.03 | 0 | 0 | 10 | 10 | 0
253 | 2023-01-11 13:00 | 112.4919 | 65.03 | 20 | 10 | 0 | 19.5 | 3550.4386
254 | 2023-01-11 14:00 | 117.1248 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1917.4187
255 | 2023-01-11 15:00 | 125.4642 | 65.03 | 10 | 0 | 0 | 20 | 1904.942
256 | 2023-01-11 16:00 | 122.3813 | 65.03 | 10 | 0 | 0 | 20 | 1874.1126
257 | 2023-01-11 17:00 | 131.2305 | 66.4 | 0 | 0 | 10 | 10 | 0
258 | 2023-01-11 18:00 | 132.9145 | 66.4 | 0 | 0 | 10 | 0 | 0
259 | 2023-01-11 19:00 | 125.4487 | 65.03 | 10 | 0 | 0 | 0 | 1904.7865
260 | 2023-01-11 20:00 | 112.1743 | 65.03 | 10 | 0 | 0 | 0 | 1772.0433
261 | 2023-01-11 21:00 | 111.9781 | 65.03 | 10 | 0 | 0 | 0 | 1770.0815
262 | 2023-01-11 22:00 | 115.7017 | 65.03 | 10 | 0 | 0 | 0 | 1807.3165
263 | 2023-01-11 23:00 | 105.0618 | 53.53 | 20 | 10 | 0 | 9.5 | 3171.836
264 | 2023-01-12 00:00 | 112.6972 | 53.53 | 10 | 0 | 0 | 9.5 | 1662.2721
265 | 2023-01-12 01:00 | 117.7738 | 53.53 | 0.5 | 0 | 9.5 | 0 | 85.6519
266 | 2023-01-12 02:00 | 90.0916 | 53.53 | 10 | 0 | 0 | 0 | 1436.2163
267 | 2023-01-12 03:00 | 91.6807 | 53.53 | 10 | 0 | 0 | 0 | 1452.1071
268 | 2023-01-12 04:00 | 89.3002 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1578.6492
269 | 2023-01-12 05:00 | 88.8989 | 53.53 | 20 | 10 | 0 | 10.5 | 2848.5788
270 | 2023-01-12 06:00 | 84.0323 | 53.53 | 20 | 10 | 0 | 20 | 2751.2455
271 | 2023-01-12 07:00 | 111.3884 | 53.53 | 10 | 0 | 0 | 20 | 1649.1836
272 | 2023-01-12 08:00 | 118.1792 | 65.03 | 10 | 0 | 0 | 20 | 1832.092
273 | 2023-01-12 09:00 | 140.7425 | 65.03 | 0 | 0 | 10 | 10 | 0
274 | 2023-01-12 10:00 | 133.9785 | 65.03 | 0 | 0 | 10 | 0 | 0
275 | 2023-01-12 11:00 | 121.9663 | 65.03 | 10 | 0 | 0 | 0 | 1869.963
276 | 2023-01-12 12:00 | 113.7832 | 65.03 | 20 | 10 | 0 | 9.5 | 3576.2633
277 | 2023-01-12 13:00 | 111.8046 | 65.03 | 20 | 10 | 0 | 19 | 3536.692
278 | 2023-01-12 14:00 | 129.6365 | 65.03 | 10 | 0 | 0 | 19 | 1946.6645
279 | 2023-01-12 15:00 | 120.9487 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 2055.5538
280 | 2023-01-12 16:00 | 122.7717 | 65.03 | 10 | 0 | 0 | 20 | 1878.0165
281 | 2023-01-12 17:00 | 123.7112 | 66.4 | 10 | 0 | 0 | 20 | 1901.1123
282 | 2023-01-12 18:00 | 141.9181 | 66.4 | 0 | 0 | 10 | 10 | 0
283 | 2023-01-12 19:00 | 137.5497 | 65.03 | 0 | 0 | 10 | 0 | 0
284 | 2023-01-12 20:00 | 106.8152 | 65.03 | 20 | 10 | 0 | 9.5 | 3436.9049
285 | 2023-01-12 21:00 | 110.6006 | 65.03 | 10 | 0 | 0 | 9.5 | 1756.3061
286 | 2023-01-12 22:00 | 115.9565 | 65.03 | 0.5 | 0 | 9.5 | 0 | 90.4933
287 | 2023-01-12 23:00 | 109.2949 | 53.53 | 10 | 0 | 0 | 0 | 1628.2492
288 | 2023-01-13 00:00 | 106.8003 | 53.53 | 10 | 0 | 0 | 0 | 1603.3031
289 | 2023-01-13 01:00 | 108.1341 | 53.53 | 10 | 0 | 0 | 0 | 1616.6407
290 | 2023-01-13 02:00 | 87.0781 | 53.53 | 20 | 10 | 0 | 9.5 | 2812.1628
291 | 2023-01-13 03:00 | 90.0691 | 53.53 | 11.5789 | 1.5789 | 0 | 11 | 1662.7266
292 | 2023-01-13 04:00 | 102.7722 | 53.53 | 0 | 0 | 10 | 1 | 0
293 | 2023-01-13 05:00 | 75.4737 | 53.53 | 20 | 10 | 0 | 10.5 | 2580.0732
294 | 2023-01-13 06:00 | 87.1836 | 53.53 | 20 | 10 | 0 | 20 | 2814.2714
295 | 2023-01-13 07:00 | 110.2578 | 53.53 | 10 | 0 | 0 | 20 | 1637.8783
296 | 2023-01-13 08:00 | 121.2198 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 93.1249
297 | 2023-01-13 09:00 | 116.2589 | 65.03 | 10 | 0 | 0 | 10.5 | 1812.8893
298 | 2023-01-13 10:00 | 108.6574 | 65.03 | 20 | 10 | 0 | 20 | 3473.748
299 | 2023-01-13 11:00 | 121.4834 | 65.03 | 10 | 0 | 0 | 20 | 1865.1337
300 | 2023-01-13 12:00 | 135.8736 | 65.03 | 0 | 0 | 10 | 10 | 0
301 | 2023-01-13 13:00 | 109.6779 | 65.03 | 20 | 10 | 0 | 19.5 | 3494.1579
302 | 2023-01-13 14:00 | 126.294 | 65.03 | 1 | 0 | 9 | 10.5 | 191.324
303 | 2023-01-13 15:00 | 116.5519 | 65.03 | 20 | 10 | 0 | 20 | 3631.6379
304 | 2023-01-13 16:00 | 118.4426 | 65.03 | 10 | 0 | 0 | 20 | 1834.7258
305 | 2023-01-13 17:00 | 127.1272 | 66.4 | 10 | 0 | 0 | 20 | 1935.2717
306 | 2023-01-13 18:00 | 131.5116 | 66.4 | 0 | 0 | 10 | 10 | 0
307 | 2023-01-13 19:00 | 145.8233 | 65.03 | 0 | 0 | 10 | 0 | 0
308 | 2023-01-13 20:00 | 118.6734 | 65.03 | 20 | 10 | 0 | 9.5 | 3674.0681
309 | 2023-01-13 21:00 | 130.9361 | 65.03 | 0.5 | 0 | 9.5 | 0 | 97.9831
310 | 2023-01-13 22:00 | 124.4895 | 65.03 | 10 | 0 | 0 | 0 | 1895.1954
311 | 2023-01-13 23:00 | 112.4182 | 53.53 | 10 | 0 | 0 | 0 | 1659.482
312 | 2023-01-14 00:00 | 118.0829 | 53.53 | 10 | 0 | 0 | 0 | 1716.1295
313 | 2023-01-14 01:00 | 104.4174 | 53.53 | 10 | 0 | 0 | 0 | 1579.474
314 | 2023-01-14 02:00 | 87.9475 | 53.53 | 10 | 0 | 0 | 0 | 1414.7751
315 | 2023-01-14 03:00 | 78.7701 | 53.53 | 20 | 10 | 0 | 9.5 | 2646.002
316 | 2023-01-14 04:00 | 81.4024 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1491.3583
317 | 2023-01-14 05:00 | 76.1786 | 53.53 | 20 | 10 | 0 | 20 | 2594.1716
318 | 2023-01-14 06:00 | 89.5395 | 53.53 | 10 | 0 | 0 | 20 | 1430.6949
319 | 2023-01-14 07:00 | 93.4541 | 53.53 | 10 | 0 | 0 | 20 | 1469.8411
320 | 2023-01-14 08:00 | 117.5117 | 53.53 | 10 | 0 | 0 | 20 | 1710.417
321 | 2023-01-14 09:00 | 109.5085 | 53.53 | 10 | 0 | 0 | 20 | 1630.3855
322 | 2023-01-14 10:00 | 121.4238 | 53.53 | 0 | 0 | 10 | 10 | 0
323 | 2023-01-14 11:00 | 117.2145 | 53.53 | 10 | 0 | 0 | 10 | 1707.4454
324 | 2023-01-14 12:00 | 129.065 | 53.53 | 0 | 0 | 10 | 0 | 0
325 | 2023-01-14 13:00 | 117.0263 | 53.53 | 10 | 0 | 0 | 0 | 1705.5632
326 | 2023-01-14 14:00 | 101.4982 | 53.53 | 20 | 10 | 0 | 9.5 | 3100.5639
327 | 2023-01-14 15:00 | 110.4012 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1811.8708
328 | 2023-01-14 16:00 | 103.4873 | 53.53 | 20 | 10 | 0 | 20 | 3140.3461
329 | 2023-01-14 17:00 | 122.2983 | 53.53 | 10 | 0 | 0 | 20 | 1758.2833
330 | 2023-01-14 18:00 | 140.2384 | 53.53 | 0 | 0 | 10 | 10 | 0
331 | 2023-01-14 19:00 | 131.1677 | 53.53 | 0 | 0 | 10 | 0 | 0
332 | 2023-01-14 20:00 | 101.1694 | 53.53 | 10 | 0 | 0 | 0 | 1546.9942
333 | 2023-01-14 21:00 | 99.3427 | 53.53 | 10 | 0 | 0 | 0 | 1528.727
334 | 2023-01-14 22:00 | -67.7957 | 53.53 | 20 | 10 | 0 | 9.5 | -285.314
335 | 2023-01-14 23:00 | 93.2538 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1545.0924
336 | 2023-01-15 00:00 | 96.3391 | 53.53 | 10 | 0 | 0 | 10 | 1498.6912
337 | 2023-01-15 01:00 | 103.3514 | 53.53 | 0 | 0 | 10 | 0 | 0
338 | 2023-01-15 02:00 | 91.2544 | 53.53 | 10 | 0 | 0 | 0 | 1447.8435
339 | 2023-01-15 03:00 | 85.9075 | 53.53 | 10 | 0 | 0 | 0 | 1394.3751
340 | 2023-01-15 04:00 | 68.4705 | 53.53 | 20 | 10 | 0 | 9.5 | 2440.0104
341 | 2023-01-15 05:00 | 83.2885 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1512.2047
342 | 2023-01-15 06:00 | 81.4444 | 53.53 | 20 | 10 | 0 | 20 | 2699.4888
343 | 2023-01-15 07:00 | 104.2034 | 53.53 | 10 | 0 | 0 | 20 | 1577.3343
344 | 2023-01-15 08:00 | 126.4971 | 53.53 | 0 | 0 | 10 | 10 | 0
345 | 2023-01-15 09:00 | 99.3608 | 53.53 | 20 | 10 | 0 | 19.5 | 3057.8151
346 | 2023-01-15 10:00 | 106.8359 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1688.0618
347 | 2023-01-15 11:00 | 115.7472 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 84.6386
348 | 2023-01-15 12:00 | 101.4535 | 53.53 | 20 | 10 | 0 | 20 | 3099.6709
349 | 2023-01-15 13:00 | 124.8242 | 53.53 | 0 | 0 | 10 | 10 | 0
350 | 2023-01-15 14:00 | 113.8194 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1761.5727
351 | 2023-01-15 15:00 | 118.1268 | 53.53 | 10 | 0 | 0 | 10.5 | 1716.568
352 | 2023-01-15 16:00 | 106.9629 | 53.53 | 20 | 10 | 0 | 20 | 3209.8576
353 | 2023-01-15 17:00 | 132.811 | 53.53 | 0 | 0 | 10 | 10 | 0
354 | 2023-01-15 18:00 | 135.3451 | 53.53 | 0 | 0 | 10 | 0 | 0
355 | 2023-01-15 19:00 | 127.7073 | 53.53 | 10 | 0 | 0 | 0 | 1812.3735
356 | 2023-01-15 20:00 | 107.7196 | 53.53 | 10 | 0 | 0 | 0 | 1612.496
357 | 2023-01-15 21:00 | 108.0104 | 53.53 | 10 | 0 | 0 | 0 | 1615.4037
358 | 2023-01-15 22:00 | 100.1938 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1618.1454
359 | 2023-01-15 23:00 | 99.816 | 53.53 | 20 | 10 | 0 | 10 | 3066.9194
360 | 2023-01-16 00:00 | 107.7802 | 53.53 | 10 | 0 | 0 | 10 | 1613.1016
361 | 2023-01-16 01:00 | 111.9457 | 53.53 | 0 | 0 | 10 | 0 | 0
362 | 2023-01-16 02:00 | 97.643 | 53.53 | 10 | 0 | 0 | 0 | 1511.73
363 | 2023-01-16 03:00 | 82.0964 | 53.53 | 20 | 10 | 0 | 9.5 | 2712.5273
364 | 2023-01-16 04:00 | 87.9781 | 53.53 | 20 | 10 | 0 | 19 | 2830.162
365 | 2023-01-16 05:00 | 102.8886 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 234.6279
366 | 2023-01-16 06:00 | 83.8996 | 53.53 | 20 | 10 | 0 | 20 | 2748.593
367 | 2023-01-16 07:00 | 103.4332 | 53.53 | 10 | 0 | 0 | 20 | 1569.6317
368 | 2023-01-16 08:00 | 120.4626 | 65.03 | 1 | 0 | 9 | 11 | 185.4926
369 | 2023-01-16 09:00 | 126.1055 | 65.03 | 0 | 0 | 10 | 1 | 0
370 | 2023-01-16 10:00 | 118.9841 | 65.03 | 10 | 0 | 0 | 1 | 1840.1415
371 | 2023-01-16 11:00 | -10.0214 | 65.03 | 20 | 10 | 0 | 10.5 | 1100.1718
372 | 2023-01-16 12:00 | -49.9042 | 65.03 | 20 | 10 | 0 | 20 | 302.517
373 | 2023-01-16 13:00 | 126.0808 | 65.03 | 10 | 0 | 0 | 20 | 1911.1077
374 | 2023-01-16 14:00 | 123.4196 | 65.03 | 10 | 0 | 0 | 20 | 1884.4957
375 | 2023-01-16 15:00 | 144.1564 | 65.03 | 0 | 0 | 10 | 10 | 0
376 | 2023-01-16 16:00 | 117.406 | 65.03 | 20 | 10 | 0 | 19.5 | 3648.7198
377 | 2023-01-16 17:00 | 122.6041 | 66.4 | 10 | 0 | 0 | 19.5 | 1890.0411
378 | 2023-01-16 18:00 | 149.3518 | 66.4 | 0 | 0 | 10 | 9.5 | 0
379 | 2023-01-16 19:00 | 130.6908 | 65.03 | 0.5 | 0 | 9.5 | 0 | 97.8604
380 | 2023-01-16 20:00 | 114.7206 | 65.03 | 20 | 10 | 0 | 9.5 | 3595.0129
381 | 2023-01-16 21:00 | 125.9288 | 65.03 | 0.5 | 0 | 9.5 | 0 | 95.4794
382 | 2023-01-16 22:00 | 104.3574 | 65.03 | 10 | 0 | 0 | 0 | 1693.8741
383 | 2023-01-16 23:00 | 101.072 | 53.53 | 10 | 0 | 0 | 0 | 1546.0205
384 | 2023-01-17 00:00 | 99.362 | 53.53 | 10 | 0 | 0 | 0 | 1528.9196
385 | 2023-01-17 01:00 | 103.5986 | 53.53 | 10 | 0 | 0 | 0 | 1571.2863
386 | 2023-01-17 02:00 | 92.4229 | 53.53 | 10 | 0 | 0 | 0 | 1459.529
387 | 2023-01-17 03:00 | 93.1557 | 53.53 | 10 | 0 | 0 | 0 | 1466.857
388 | 2023-01-17 04:00 | 91.0587 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1598.0851
389 | 2023-01-17 05:00 | 80.2617 | 53.53 | 20 | 10 | 0 | 10.5 | 2675.8338
390 | 2023-01-17 06:00 | 76.3998 | 53.53 | 20 | 10 | 0 | 20 | 2598.5952
391 | 2023-01-17 07:00 | 109.3093 | 53.53 | 10 | 0 | 0 | 20 | 1628.393
392 | 2023-01-17 08:00 | 115.599 | 65.03 | 10 | 0 | 0 | 20 | 1806.2897
393 | 2023-01-17 09:00 | 122.5924 | 65.03 | 10 | 0 | 0 | 20 | 1876.2241
394 | 2023-01-17 10:00 | 124.7583 | 65.03 | 10 | 0 | 0 | 20 | 1897.8834
395 | 2023-01-17 11:00 | 119.9569 | 65.03 | 10 | 0 | 0 | 20 | 1849.8692
396 | 2023-01-17 12:00 | 125.3017 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 95.1658
397 | 2023-01-17 13:00 | 120.6779 | 65.03 | 10 | 0 | 0 | 10.5 | 1857.0787
398 | 2023-01-17 14:00 | 123.2073 | 65.03 | 10 | 0 | 0 | 10.5 | 1882.3732
399 | 2023-01-17 15:00 | 114.1345 | 65.03 | 20 | 10 | 0 | 20 | 3583.2904
400 | 2023-01-17 16:00 | 117.5869 | 65.03 | 10 | 0 | 0 | 20 | 1826.1687
401 | 2023-01-17 17:00 | 135.4186 | 66.4 | 0 | 0 | 10 | 10 | 0
402 | 2023-01-17 18:00 | 140.8759 | 66.4 | 0 | 0 | 10 | 0 | 0
403 | 2023-01-17 19:00 | 131.113 | 65.03 | 10 | 0 | 0 | 0 | 1961.4299
404 | 2023-01-17 20:00 | 118.1292 | 65.03 | 10 | 0 | 0 | 0 | 1831.592
405 | 2023-01-17 21:00 | 111.9819 | 65.03 | 10 | 0 | 0 | 0 | 1770.1195
406 | 2023-01-17 22:00 | 113.0321 | 65.03 | 10 | 0 | 0 | 0 | 1780.621
407 | 2023-01-17 23:00 | 115.9622 | 53.53 | 10 | 0 | 0 | 0 | 1694.9223
408 | 2023-01-18 00:00 | 97.6472 | 53.53 | 10 | 0 | 0 | 0 | 1511.7719
409 | 2023-01-18 01:00 | 100.8427 | 53.53 | 10 | 0 | 0 | 0 | 1543.7265
410 | 2023-01-18 02:00 | 79.9244 | 53.53 | 20 | 10 | 0 | 9.5 | 2669.0886
411 | 2023-01-18 03:00 | 76.3119 | 53.53 | 20 | 10 | 0 | 19 | 2596.8377
412 | 2023-01-18 04:00 | 84.2955 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1523.3343
413 | 2023-01-18 05:00 | 95.2011 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 74.3655
414 | 2023-01-18 06:00 | 86.8504 | 53.53 | 20 | 10 | 0 | 20 | 2807.6087
415 | 2023-01-18 07:00 | 110.4266 | 53.53 | 10 | 0 | 0 | 20 | 1639.5663
416 | 2023-01-18 08:00 | 128.5602 | 65.03 | 0 | 0 | 10 | 10 | 0
417 | 2023-01-18 09:00 | 131.1308 | 65.03 | 0 | 0 | 10 | 0 | 0
418 | 2023-01-18 10:00 | 118.3851 | 65.03 | 10 | 0 | 0 | 0 | 1834.1511
419 | 2023-01-18 11:00 | -5.7055 | 65.03 | 20 | 10 | 0 | 9.5 | 1186.4891
420 | 2023-01-18 12:00 | -7.9971 | 65.03 | 20 | 10 | 0 | 19 | 1140.6571
421 | 2023-01-18 13:00 | 113.3446 | 65.03 | 10 | 0 | 0 | 19 | 1783.746
422 | 2023-01-18 14:00 | 114.8152 | 65.03 | 10 | 0 | 0 | 19 | 1798.4517
423 | 2023-01-18 15:00 | 109.9324 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1933.7945
424 | 2023-01-18 16:00 | 113.0509 | 65.03 | 10 | 0 | 0 | 20 | 1780.8085
425 | 2023-01-18 17:00 | 131.3524 | 66.4 | 10 | 0 | 0 | 20 | 1977.5235
426 | 2023-01-18 18:00 | 140.7137 | 66.4 | 0 | 0 | 10 | 10 | 0
427 | 2023-01-18 19:00 | 150.7908 | 65.03 | 0 | 0 | 10 | 0 | 0
428 | 2023-01-18 20:00 | 105.4125 | 65.03 | 20 | 10 | 0 | 9.5 | 3408.8504
429 | 2023-01-18 21:00 | 117.0251 | 65.03 | 0.5 | 0 | 9.5 | 0 | 91.0276
430 | 2023-01-18 22:00 | 107.1949 | 65.03 | 10 | 0 | 0 | 0 | 1722.2486
431 | 2023-01-18 23:00 | 112.7245 | 53.53 | 10 | 0 | 0 | 0 | 1662.5451
432 | 2023-01-19 00:00 | 107.9342 | 53.53 | 10 | 0 | 0 | 0 | 1614.6424
433 | 2023-01-19 01:00 | 98.3326 | 53.53 | 10 | 0 | 0 | 0 | 1518.6256
434 | 2023-01-19 02:00 | 96.9266 | 53.53 | 10 | 0 | 0 | 0 | 1504.5661
435 | 2023-01-19 03:00 | 84.7488 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1528.3442
436 | 2023-01-19 04:00 | 85.1983 | 53.53 | 10 | 0 | 0 | 1 | 1387.2828
437 | 2023-01-19 05:00 | 82.0352 | 53.53 | 20 | 10 | 0 | 10.5 | 2711.3047
438 | 2023-01-19 06:00 | 84.4428 | 53.53 | 20 | 10 | 0 | 20 | 2759.4551
439 | 2023-01-19 07:00 | 112.3226 | 53.53 | 10 | 0 | 0 | 20 | 1658.5256
440 | 2023-01-19 08:00 | 117.5185 | 65.03 | 10 | 0 | 0 | 20 | 1825.4851
441 | 2023-01-19 09:00 | 121.4889 | 65.03 | 10 | 0 | 0 | 20 | 1865.1889
442 | 2023-01-19 10:00 | 121.7656 | 65.03 | 10 | 0 | 0 | 20 | 1867.9556
443 | 2023-01-19 11:00 | 131.0524 | 65.03 | 0 | 0 | 10 | 10 | 0
444 | 2023-01-19 12:00 | 116.4552 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1910.3703
445 | 2023-01-19 13:00 | 109.9501 | 65.03 | 20 | 10 | 0 | 20 | 3499.6013
446 | 2023-01-19 14:00 | 128.3322 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 96.6811
447 | 2023-01-19 15:00 | 116.5318 | 65.03 | 20 | 10 | 0 | 20 | 3631.2353
448 | 2023-01-19 16:00 | 128.8251 | 65.03 | 10 | 0 | 0 | 20 | 1938.5508
449 | 2023-01-19 17:00 | 136.9455 | 66.4 | 0 | 0 | 10 | 10 | 0
450 | 2023-01-19 18:00 | 132.9339 | 66.4 | 10 | 0 | 0 | 10 | 1993.3387
451 | 2023-01-19 19:00 | 136.6559 | 65.03 | 0 | 0 | 10 | 0 | 0
452 | 2023-01-19 20:00 | 133.7867 | 65.03 | 10 | 0 | 0 | 0 | 1988.1671
453 | 2023-01-19 21:00 | 135.5155 | 65.03 | 10 | 0 | 0 | 0 | 2005.4553
454 | 2023-01-19 22:00 | 114.4241 | 65.03 | 10 | 0 | 0 | 0 | 1794.5412
455 | 2023-01-19 23:00 | 110.1291 | 53.53 | 10 | 0 | 0 | 0 | 1636.5907
456 | 2023-01-20 00:00 | 118.4255 | 53.53 | 10 | 0 | 0 | 0 | 1719.5552
457 | 2023-01-20 01:00 | 103.2965 | 53.53 | 10 | 0 | 0 | 0 | 1568.2645
458 | 2023-01-20 02:00 | 91.5254 | 53.53 | 10 | 0 | 0 | 0 | 1450.554
459 | 2023-01-20 03:00 | 88.7051 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1572.072
460 | 2023-01-20 04:00 | 91.367 | 53.53 | 10 | 0 | 0 | 1 | 1448.9704
461 | 2023-01-20 05:00 | 83.3681 | 53.53 | 20 | 10 | 0 | 10.5 | 2737.9624
462 | 2023-01-20 06:00 | 79.4164 | 53.53 | 20 | 10 | 0 | 20 | 2658.9277
463 | 2023-01-20 07:00 | 97.3215 | 53.53 | 10 | 0 | 0 | 20 | 1508.5146
464 | 2023-01-20 08:00 | 111.7779 | 65.03 | 10 | 0 | 0 | 20 | 1768.0791
465 | 2023-01-20 09:00 | 115.6844 | 65.03 | 10 | 0 | 0 | 20 | 1807.1443
466 | 2023-01-20 10:00 | 116.7933 | 65.03 | 10 | 0 | 0 | 20 | 1818.233
467 | 2023-01-20 11:00 | 138.6015 | 65.03 | 0 | 0 | 10 | 10 | 0
468 | 2023-01-20 12:00 | 128.7351 | 65.03 | 0 | 0 | 10 | 0 | 0
469 | 2023-01-20 13:00 | 112.6306 | 65.03 | 20 | 10 | 0 | 9.5 | 3553.2118
470 | 2023-01-20 14:00 | 121.647 | 65.03 | 10 | 0 | 0 | 9.5 | 1866.7699
471 | 2023-01-20 15:00 | 116.0243 | 65.03 | 20 | 10 | 0 | 19 | 3621.0857
472 | 2023-01-20 16:00 | 116.854 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 2010.297
473 | 2023-01-20 17:00 | 135.3276 | 66.4 | 0 | 0 | 10 | 10 | 0
474 | 2023-01-20 18:00 | 139.0014 | 66.4 | 0 | 0 | 10 | 0 | 0
475 | 2023-01-20 19:00 | 131.4791 | 65.03 | 10 | 0 | 0 | 0 | 1965.0907
476 | 2023-01-20 20:00 | 123.2974 | 65.03 | 10 | 0 | 0 | 0 | 1883.2744
477 | 2023-01-20 21:00 | 106.6467 | 65.03 | 20 | 10 | 0 | 9.5 | 3433.5338
478 | 2023-01-20 22:00 | 113.9459 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1883.9568
479 | 2023-01-20 23:00 | 138.3971 | 53.53 | 0 | 0 | 10 | 0 | 0
480 | 2023-01-21 00:00 | 102.6287 | 53.53 | 20 | 10 | 0 | 9.5 | 3123.1732
481 | 2023-01-21 01:00 | 114.3284 | 53.53 | 0.5 | 0 | 9.5 | 0 | 83.9292
482 | 2023-01-21 02:00 | 81.5942 | 53.53 | 10 | 0 | 0 | 0 | 1351.2422
483 | 2023-01-21 03:00 | 85.6566 | 53.53 | 10 | 0 | 0 | 0 | 1391.8663
484 | 2023-01-21 04:00 | 80.476 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1481.1194
485 | 2023-01-21 05:00 | 79.6524 | 53.53 | 20 | 10 | 0 | 10.5 | 2663.6474
486 | 2023-01-21 06:00 | 75.6854 | 53.53 | 20 | 10 | 0 | 20 | 2584.3085
487 | 2023-01-21 07:00 | 104.3431 | 53.53 | 10 | 0 | 0 | 20 | 1578.7313
488 | 2023-01-21 08:00 | 105.2623 | 53.53 | 10 | 0 | 0 | 20 | 1587.9229
489 | 2023-01-21 09:00 | 116.4235 | 53.53 | 10 | 0 | 0 | 20 | 1699.5347
490 | 2023-01-21 10:00 | 120.5194 | 53.53 | 0 | 0 | 10 | 10 | 0
491 | 2023-01-21 11:00 | 113.8041 | 53.53 | 10 | 0 | 0 | 10 | 1673.3413
492 | 2023-01-21 12:00 | 108.841 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1709.1688
493 | 2023-01-21 13:00 | 114.5458 | 53.53 | 10 | 0 | 0 | 10.5 | 1680.7579
494 | 2023-01-21 14:00 | 108.6872 | 53.53 | 20 | 10 | 0 | 20 | 3244.3443
495 | 2023-01-21 15:00 | 118.9985 | 53.53 | 0 | 0 | 10 | 10 | 0
496 | 2023-01-21 16:00 | 100.3304 | 53.53 | 20 | 10 | 0 | 19.5 | 3077.2079
497 | 2023-01-21 17:00 | 123.5038 | 53.53 | 0 | 0 | 10 | 9.5 | 0
498 | 2023-01-21 18:00 | 114.6565 | 53.53 | 10 | 0 | 0 | 9.5 | 1681.8647
499 | 2023-01-21 19:00 | 116.8626 | 53.53 | 10 | 0 | 0 | 9.5 | 1703.9265
500 | 2023-01-21 20:00 | 118.5371 | 53.53 | 0.5 | 0 | 9.5 | 0 | 86.0335
501 | 2023-01-21 21:00 | 113.6001 | 53.53 | 10 | 0 | 0 | 0 | 1671.3015
502 | 2023-01-21 22:00 | 101.0448 | 53.53 | 10 | 0 | 0 | 0 | 1545.7483
503 | 2023-01-21 23:00 | 91.827 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1530.0741
504 | 2023-01-22 00:00 | 86.1713 | 53.53 | 20 | 10 | 0 | 10 | 2794.0257
505 | 2023-01-22 01:00 | 97.1371 | 53.53 | 10 | 0 | 0 | 10 | 1506.6705
506 | 2023-01-22 02:00 | 107.5747 | 53.53 | 0 | 0 | 10 | 0 | 0
507 | 2023-01-22 03:00 | 84.3823 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1524.2935
508 | 2023-01-22 04:00 | 77.0349 | 53.53 | 20 | 10 | 0 | 10.5 | 2611.2973
509 | 2023-01-22 05:00 | 84.6415 | 53.53 | 10 | 0 | 0 | 10.5 | 1381.7147
510 | 2023-01-22 06:00 | 71.5501 | 53.53 | 20 | 10 | 0 | 20 | 2501.6029
511 | 2023-01-22 07:00 | 98.7649 | 53.53 | 10 | 0 | 0 | 20 | 1522.9494
512 | 2023-01-22 08:00 | 111.6556 | 53.53 | 10 | 0 | 0 | 20 | 1651.8563
513 | 2023-01-22 09:00 | 110.2608 | 53.53 | 10 | 0 | 0 | 20 | 1637.9082
514 | 2023-01-22 10:00 | 117.592 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 85.561
515 | 2023-01-22 11:00 | 113.6215 | 53.53 | 10 | 0 | 0 | 10.5 | 1671.515
516 | 2023-01-22 12:00 | 116.4486 | 53.53 | 10 | 0 | 0 | 10.5 | 1699.7858
517 | 2023-01-22 13:00 | 106.2337 | 53.53 | 20 | 10 | 0 | 20 | 3195.2745
518 | 2023-01-22 14:00 | 118.626 | 53.53 | 10 | 0 | 0 | 20 | 1721.5596
519 | 2023-01-22 15:00 | 126.6524 | 53.53 | 0 | 0 | 10 | 10 | 0
520 | 2023-01-22 16:00 | 104.5854 | 53.53 | 20 | 10 | 0 | 19.5 | 3162.3072
521 | 2023-01-22 17:00 | 120.0534 | 53.53 | 10 | 0 | 0 | 19.5 | 1735.8337
522 | 2023-01-22 18:00 | 138.2214 | 53.53 | 0 | 0 | 10 | 9.5 | 0
523 | 2023-01-22 19:00 | 124.5036 | 53.53 | 0.5 | 0 | 9.5 | 0 | 89.0168
524 | 2023-01-22 20:00 | 118.991 | 53.53 | 10 | 0 | 0 | 0 | 1725.2099
525 | 2023-01-22 21:00 | 102.7902 | 53.53 | 20 | 10 | 0 | 9.5 | 3126.4034
526 | 2023-01-22 22:00 | 119.5809 | 53.53 | 0.5 | 0 | 9.5 | 0 | 86.5554
527 | 2023-01-22 23:00 | 101.9042 | 53.53 | 20 | 10 | 0 | 9.5 | 3108.6832
528 | 2023-01-23 00:00 | 110.912 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1730.9686
529 | 2023-01-23 01:00 | 123.8748 | 53.53 | 0 | 0 | 10 | 0 | 0
530 | 2023-01-23 02:00 | 86.3271 | 53.53 | 10 | 0 | 0 | 0 | 1398.5708
531 | 2023-01-23 03:00 | 82.7488 | 53.53 | 20 | 10 | 0 | 9.5 | 2725.576
532 | 2023-01-23 04:00 | 85.7506 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1539.4173
533 | 2023-01-23 05:00 | 92.5318 | 53.53 | 10 | 0 | 0 | 10.5 | 1460.6177
534 | 2023-01-23 06:00 | 79.5276 | 53.53 | 20 | 10 | 0 | 20 | 2661.1524
535 | 2023-01-23 07:00 | 114.1671 | 53.53 | 10 | 0 | 0 | 20 | 1676.9709
536 | 2023-01-23 08:00 | 115.1672 | 65.03 | 10 | 0 | 0 | 20 | 1801.9717
537 | 2023-01-23 09:00 | 129.1749 | 65.03 | 0 | 0 | 10 | 10 | 0
538 | 2023-01-23 10:00 | 106.0881 | 65.03 | 20 | 10 | 0 | 19.5 | 3422.3617
539 | 2023-01-23 11:00 | 113.6434 | 65.03 | 10 | 0 | 0 | 19.5 | 1786.7342
540 | 2023-01-23 12:00 | 108.9718 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1831.5975
541 | 2023-01-23 13:00 | 113.4099 | 65.03 | 10 | 0 | 0 | 20 | 1784.3986
542 | 2023-01-23 14:00 | 120.8265 | 65.03 | 10 | 0 | 0 | 20 | 1858.5655
543 | 2023-01-23 15:00 | 117.5896 | 65.03 | 10 | 0 | 0 | 20 | 1826.196
544 | 2023-01-23 16:00 | 117.0684 | 65.03 | 10 | 0 | 0 | 20 | 1820.984
545 | 2023-01-23 17:00 | 132.7325 | 66.4 | 0 | 0 | 10 | 10 | 0
546 | 2023-01-23 18:00 | 135.4712 | 66.4 | 0 | 0 | 10 | 0 | 0
547 | 2023-01-23 19:00 | 127.3714 | 65.03 | 10 | 0 | 0 | 0 | 1924.0139
548 | 2023-01-23 20:00 | 119.8037 | 65.03 | 10 | 0 | 0 | 0 | 1848.337
549 | 2023-01-23 21:00 | 119.3967 | 65.03 | 10 | 0 | 0 | 0 | 1844.2675
550 | 2023-01-23 22:00 | 116.9595 | 65.03 | 10 | 0 | 0 | 0 | 1819.8949
551 | 2023-01-23 23:00 | 113.441 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1757.5893
552 | 2023-01-24 00:00 | 111.2233 | 53.53 | 20 | 10 | 0 | 10 | 3295.0657
553 | 2023-01-24 01:00 | 129.9331 | 53.53 | 0 | 0 | 10 | 0 | 0
554 | 2023-01-24 02:00 | 88.2536 | 53.53 | 10 | 0 | 0 | 0 | 1417.8356
555 | 2023-01-24 03:00 | 86.6981 | 53.53 | 10 | 0 | 0 | 0 | 1402.2809
556 | 2023-01-24 04:00 | 83.8401 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1518.3011
557 | 2023-01-24 05:00 | 82.2404 | 53.53 | 20 | 10 | 0 | 10.5 | 2715.4074
558 | 2023-01-24 06:00 | 81.1091 | 53.53 | 20 | 10 | 0 | 20 | 2692.7812
559 | 2023-01-24 07:00 | 103.047 | 53.53 | 10 | 0 | 0 | 20 | 1565.7704
560 | 2023-01-24 08:00 | 118.3738 | 65.03 | 10 | 0 | 0 | 20 | 1834.0378
561 | 2023-01-24 09:00 | 121.5356 | 65.03 | 10 | 0 | 0 | 20 | 1865.6555
562 | 2023-01-24 10:00 | 119.2848 | 65.03 | 10 | 0 | 0 | 20 | 1843.1483
563 | 2023-01-24 11:00 | 113.7684 | 65.03 | 10 | 0 | 0 | 20 | 1787.9839
564 | 2023-01-24 12:00 | 126.6492 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 95.8396
565 | 2023-01-24 13:00 | 125.1071 | 65.03 | 10 | 0 | 0 | 10.5 | 1901.3709
566 | 2023-01-24 14:00 | 117.7292 | 65.03 | 10 | 0 | 0 | 10.5 | 1827.5916
567 | 2023-01-24 15:00 | 114.4512 | 65.03 | 20 | 10 | 0 | 20 | 3589.6237
568 | 2023-01-24 16:00 | 123.3692 | 65.03 | 10 | 0 | 0 | 20 | 1883.9923
569 | 2023-01-24 17:00 | 135.3486 | 66.4 | 0 | 0 | 10 | 10 | 0
570 | 2023-01-24 18:00 | 125.089 | 66.4 | 10 | 0 | 0 | 10 | 1914.8902
571 | 2023-01-24 19:00 | 133.3936 | 65.03 | 0 | 0 | 10 | 0 | 0
572 | 2023-01-24 20:00 | 115.9429 | 65.03 | 10 | 0 | 0 | 0 | 1809.7288
573 | 2023-01-24 21:00 | 107.9845 | 65.03 | 10 | 0 | 0 | 0 | 1730.1454
574 | 2023-01-24 22:00 | 115.3635 | 65.03 | 10 | 0 | 0 | 0 | 1803.9346
575 | 2023-01-24 23:00 | 100.0565 | 53.53 | 20 | 10 | 0 | 9.5 | 3071.7306
576 | 2023-01-25 00:00 | 121.2259 | 53.53 | 0.5 | 0 | 9.5 | 0 | 87.3779
577 | 2023-01-25 01:00 | 120.2507 | 53.53 | 10 | 0 | 0 | 0 | 1737.8073
578 | 2023-01-25 02:00 | 87.0744 | 53.53 | 10 | 0 | 0 | 0 | 1406.0438
579 | 2023-01-25 03:00 | 91.7784 | 53.53 | 10 | 0 | 0 | 0 | 1453.0838
580 | 2023-01-25 04:00 | 76.0309 | 53.53 | 20 | 10 | 0 | 9.5 | 2591.2189
581 | 2023-01-25 05:00 | 81.5701 | 53.53 | 20 | 10 | 0 | 19 | 2702.0026
582 | 2023-01-25 06:00 | 86.7893 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1550.8972
583 | 2023-01-25 07:00 | 102.0223 | 53.53 | 10 | 0 | 0 | 20 | 1555.5229
584 | 2023-01-25 08:00 | 124.8738 | 65.03 | 1 | 0 | 9 | 11 | 189.9038
585 | 2023-01-25 09:00 | 139.4143 | 65.03 | 0 | 0 | 10 | 1 | 0
586 | 2023-01-25 10:00 | 111.463 | 65.03 | 20 | 10 | 0 | 10.5 | 3529.8602
587 | 2023-01-25 11:00 | 113.3442 | 65.03 | 20 | 10 | 0 | 20 | 3567.4843
588 | 2023-01-25 12:00 | 120.728 | 65.03 | 10 | 0 | 0 | 20 | 1857.5803
589 | 2023-01-25 13:00 | 134.4351 | 65.03 | 0 | 0 | 10 | 10 | 0
590 | 2023-01-25 14:00 | 111.2235 | 65.03 | 20 | 10 | 0 | 19.5 | 3525.0706
591 | 2023-01-25 15:00 | 120.8376 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1956.5013
592 | 2023-01-25 16:00 | 137.0735 | 65.03 | 0 | 0 | 10 | 10 | 0
593 | 2023-01-25 17:00 | 124.1295 | 66.4 | 10 | 0 | 0 | 10 | 1905.2954
594 | 2023-01-25 18:00 | 125.9211 | 66.4 | 10 | 0 | 0 | 10 | 1923.2113
595 | 2023-01-25 19:00 | 130.9148 | 65.03 | 0 | 0 | 10 | 0 | 0
596 | 2023-01-25 20:00 | 110.2835 | 65.03 | 20 | 10 | 0 | 9.5 | 3506.2702
597 | 2023-01-25 21:00 | 120.7999 | 65.03 | 0.5 | 0 | 9.5 | 0 | 92.915
598 | 2023-01-25 22:00 | 115.7781 | 65.03 | 10 | 0 | 0 | 0 | 1808.0807
599 | 2023-01-25 23:00 | 98.5769 | 53.53 | 20 | 10 | 0 | 9.5 | 3042.1371
600 | 2023-01-26 00:00 | 113.0788 | 53.53 | 0.5 | 0 | 9.5 | 0 | 83.3044
601 | 2023-01-26 01:00 | 104.9212 | 53.53 | 10 | 0 | 0 | 0 | 1584.5124
602 | 2023-01-26 02:00 | 100.5409 | 53.53 | 10 | 0 | 0 | 0 | 1540.7085
603 | 2023-01-26 03:00 | 84.608 | 53.53 | 20 | 10 | 0 | 9.5 | 2762.759
604 | 2023-01-26 04:00 | 84.5519 | 53.53 | 20 | 10 | 0 | 19 | 2761.6388
605 | 2023-01-26 05:00 | 93.3048 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1622.9109
606 | 2023-01-26 06:00 | 95.328 | 53.53 | 10 | 0 | 0 | 20 | 1488.5802
607 | 2023-01-26 07:00 | 112.4954 | 53.53 | 10 | 0 | 0 | 20 | 1660.2542
608 | 2023-01-26 08:00 | 108.9757 | 65.03 | 10 | 0 | 0 | 20 | 1740.057
609 | 2023-01-26 09:00 | 123.2775 | 65.03 | 0 | 0 | 10 | 10 | 0
610 | 2023-01-26 10:00 | 112.2291 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1865.8855
611 | 2023-01-26 11:00 | 120.7266 | 65.03 | 10 | 0 | 0 | 10.5 | 1857.5664
612 | 2023-01-26 12:00 | 110.2079 | 65.03 | 20 | 10 | 0 | 20 | 3504.7586
613 | 2023-01-26 13:00 | 122.4802 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 93.7551
614 | 2023-01-26 14:00 | 113.5251 | 65.03 | 10 | 0 | 0 | 10.5 | 1785.5511
615 | 2023-01-26 15:00 | 110.9131 | 65.03 | 20 | 10 | 0 | 20 | 3518.8628
616 | 2023-01-26 16:00 | 124.8684 | 65.03 | 10 | 0 | 0 | 20 | 1898.9839
617 | 2023-01-26 17:00 | 135.7779 | 66.4 | 0 | 0 | 10 | 10 | 0
618 | 2023-01-26 18:00 | 129.6927 | 66.4 | 10 | 0 | 0 | 10 | 1960.9269
619 | 2023-01-26 19:00 | 147.536 | 65.03 | 0 | 0 | 10 | 0 | 0
620 | 2023-01-26 20:00 | 110.8025 | 65.03 | 10 | 0 | 0 | 0 | 1758.3254
621 | 2023-01-26 21:00 | 114.1403 | 65.03 | 10 | 0 | 0 | 0 | 1791.7028
622 | 2023-01-26 22:00 | 115.9987 | 65.03 | 10 | 0 | 0 | 0 | 1810.2874
623 | 2023-01-26 23:00 | 104.6572 | 53.53 | 10 | 0 | 0 | 0 | 1581.8723
624 | 2023-01-27 00:00 | 112.6937 | 53.53 | 10 | 0 | 0 | 0 | 1662.2374
625 | 2023-01-27 01:00 | 105.2011 | 53.53 | 10 | 0 | 0 | 0 | 1587.3114
626 | 2023-01-27 02:00 | 85.994 | 53.53 | 20 | 10 | 0 | 9.5 | 2790.4807
627 | 2023-01-27 03:00 | 101.5233 | 53.53 | 1.5 | 0 | 8.5 | 1 | 232.58
628 | 2023-01-27 04:00 | 82.1946 | 53.53 | 20 | 10 | 0 | 10.5 | 2714.4925
629 | 2023-01-27 05:00 | 76.0205 | 53.53 | 20 | 10 | 0 | 20 | 2591.0109
630 | 2023-01-27 06:00 | 104.4329 | 53.53 | 10 | 0 | 0 | 20 | 1579.6295
631 | 2023-01-27 07:00 | 137.6123 | 53.53 | 0 | 0 | 10 | 10 | 0
632 | 2023-01-27 08:00 | 116.0363 | 65.03 | 10 | 0 | 0 | 10 | 1810.6629
633 | 2023-01-27 09:00 | 107.8811 | 65.03 | 20 | 10 | 0 | 19.5 | 3458.2211
634 | 2023-01-27 10:00 | 116.6748 | 65.03 | 10 | 0 | 0 | 19.5 | 1817.0484
635 | 2023-01-27 11:00 | 116.8412 | 65.03 | 10 | 0 | 0 | 19.5 | 1818.7122
636 | 2023-01-27 12:00 | 117.5137 | 65.03 | 10 | 0 | 0 | 19.5 | 1825.437
637 | 2023-01-27 13:00 | 111.7994 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1861.3617
638 | 2023-01-27 14:00 | 123.6458 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 94.3379
639 | 2023-01-27 15:00 | 123.1585 | 65.03 | 10 | 0 | 0 | 10.5 | 1881.885
640 | 2023-01-27 16:00 | 109.8658 | 65.03 | 20 | 10 | 0 | 20 | 3497.9157
641 | 2023-01-27 17:00 | 139.7328 | 66.4 | 0 | 0 | 10 | 10 | 0
642 | 2023-01-27 18:00 | 155.177 | 66.4 | 0 | 0 | 10 | 0 | 0
643 | 2023-01-27 19:00 | 135.2219 | 65.03 | 10 | 0 | 0 | 0 | 2002.5185
644 | 2023-01-27 20:00 | 111.4922 | 65.03 | 10 | 0 | 0 | 0 | 1765.2217
645 | 2023-01-27 21:00 | 112.8556 | 65.03 | 10 | 0 | 0 | 0 | 1778.8565
646 | 2023-01-27 22:00 | -70.8193 | 65.03 | 20 | 10 | 0 | 9.5 | -115.7853
647 | 2023-01-27 23:00 | 98.7732 | 53.53 | 10 | 0 | 0 | 9.5 | 1523.0319
648 | 2023-01-28 00:00 | 102.1621 | 53.53 | 0.5 | 0 | 9.5 | 0 | 77.8461
649 | 2023-01-28 01:00 | 98.1348 | 53.53 | 10 | 0 | 0 | 0 | 1516.6484
650 | 2023-01-28 02:00 | 99.4184 | 53.53 | 10 | 0 | 0 | 0 | 1529.4842
651 | 2023-01-28 03:00 | 79.6256 | 53.53 | 20 | 10 | 0 | 9.5 | 2663.111
652 | 2023-01-28 04:00 | 97.1314 | 53.53 | 1.5 | 0 | 8.5 | 1 | 225.9922
653 | 2023-01-28 05:00 | 73.8512 | 53.53 | 20 | 10 | 0 | 10.5 | 2547.6248
654 | 2023-01-28 06:00 | 85.7146 | 53.53 | 20 | 10 | 0 | 20 | 2784.8911
655 | 2023-01-28 07:00 | 103.4123 | 53.53 | 10 | 0 | 0 | 20 | 1569.4233
656 | 2023-01-28 08:00 | 105.1608 | 53.53 | 10 | 0 | 0 | 20 | 1586.9083
657 | 2023-01-28 09:00 | 112.2648 | 53.53 | 10 | 0 | 0 | 20 | 1657.9482
658 | 2023-01-28 10:00 | 121.8664 | 53.53 | 0 | 0 | 10 | 10 | 0
659 | 2023-01-28 11:00 | 108.5841 | 53.53 | 10 | 0 | 0 | 10 | 1621.1409
660 | 2023-01-28 12:00 | 100.9469 | 53.53 | 20 | 10 | 0 | 19.5 | 3089.5387
661 | 2023-01-28 13:00 | 110.7669 | 53.53 | 10 | 0 | 0 | 19.5 | 1642.9693
662 | 2023-01-28 14:00 | 104.9689 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1668.4097
663 | 2023-01-28 15:00 | 108.4582 | 53.53 | 10 | 0 | 0 | 20 | 1619.882
664 | 2023-01-28 16:00 | 110.2938 | 53.53 | 10 | 0 | 0 | 20 | 1638.2383
665 | 2023-01-28 17:00 | 115.8853 | 53.53 | 10 | 0 | 0 | 20 | 1694.1526
666 | 2023-01-28 18:00 | 116.2954 | 53.53 | 0 | 0 | 10 | 10 | 0
667 | 2023-01-28 19:00 | 129.7883 | 53.53 | 0 | 0 | 10 | 0 | 0
668 | 2023-01-28 20:00 | 102.2698 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1639.9984
669 | 2023-01-28 21:00 | 92.4803 | 53.53 | 20 | 10 | 0 | 10 | 2920.2062
670 | 2023-01-28 22:00 | 112.5354 | 53.53 | 0 | 0 | 10 | 0 | 0
671 | 2023-01-28 23:00 | 103.0269 | 53.53 | 10 | 0 | 0 | 0 | 1565.5686
672 | 2023-01-29 00:00 | 96.0787 | 53.53 | 10 | 0 | 0 | 0 | 1496.0874
673 | 2023-01-29 01:00 | 92.7395 | 53.53 | 10 | 0 | 0 | 0 | 1462.6948
674 | 2023-01-29 02:00 | 88.0228 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1639.0322
675 | 2023-01-29 03:00 | 83.6607 | 53.53 | 20 | 10 | 0 | 11 | 2743.8132
676 | 2023-01-29 04:00 | 106.9918 | 53.53 | 0 | 0 | 10 | 1 | 0
677 | 2023-01-29 05:00 | 84.257 | 53.53 | 20 | 10 | 0 | 10.5 | 2755.7393
678 | 2023-01-29 06:00 | 83.9819 | 53.53 | 20 | 10 | 0 | 20 | 2750.2387
679 | 2023-01-29 07:00 | 99.6772 | 53.53 | 10 | 0 | 0 | 20 | 1532.0718
680 | 2023-01-29 08:00 | 117.8399 | 53.53 | 0 | 0 | 10 | 10 | 0
681 | 2023-01-29 09:00 | 116.0548 | 53.53 | 10 | 0 | 0 | 10 | 1695.8483
682 | 2023-01-29 10:00 | 122.2919 | 53.53 | 0 | 0 | 10 | 0 | 0
683 | 2023-01-29 11:00 | 107.2788 | 53.53 | 20 | 10 | 0 | 9.5 | 3216.176
684 | 2023-01-29 12:00 | 107.837 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1783.5304
685 | 2023-01-29 13:00 | 107.5513 | 53.53 | 20 | 10 | 0 | 20 | 3221.6265
686 | 2023-01-29 14:00 | 117.592 | 53.53 | 10 | 0 | 0 | 20 | 1711.2196
687 | 2023-01-29 15:00 | 125.087 | 53.53 | 0 | 0 | 10 | 10 | 0
688 | 2023-01-29 16:00 | 107.6833 | 53.53 | 20 | 10 | 0 | 19.5 | 3224.267
689 | 2023-01-29 17:00 | 122.9071 | 53.53 | 10 | 0 | 0 | 19.5 | 1764.3714
690 | 2023-01-29 18:00 | 128.3684 | 53.53 | 0 | 0 | 10 | 9.5 | 0
691 | 2023-01-29 19:00 | 124.1214 | 53.53 | 0.5 | 0 | 9.5 | 0 | 88.8257
692 | 2023-01-29 20:00 | 114.1628 | 53.53 | 10 | 0 | 0 | 0 | 1676.9284
693 | 2023-01-29 21:00 | 93.6204 | 53.53 | 20 | 10 | 0 | 9.5 | 2943.0086
694 | 2023-01-29 22:00 | 100.4071 | 53.53 | 10 | 0 | 0 | 9.5 | 1539.3708
695 | 2023-01-29 23:00 | 95.668 | 53.53 | 10 | 0 | 0 | 9.5 | 1491.9802
696 | 2023-01-30 00:00 | 96.3614 | 53.53 | 10 | 0 | 0 | 9.5 | 1498.9137
697 | 2023-01-30 01:00 | 102.6219 | 53.53 | 0.5 | 0 | 9.5 | 0 | 78.0759
698 | 2023-01-30 02:00 | 82.8962 | 53.53 | 20 | 10 | 0 | 9.5 | 2728.5243
699 | 2023-01-30 03:00 | 87.4346 | 53.53 | 11.5789 | 1.5789 | 0 | 11 | 1632.2219
700 | 2023-01-30 04:00 | 98.808 | 53.53 | 0 | 0 | 10 | 1 | 0
701 | 2023-01-30 05:00 | 87.1263 | 53.53 | 20 | 10 | 0 | 10.5 | 2813.1257
702 | 2023-01-30 06:00 | 82.2483 | 53.53 | 20 | 10 | 0 | 20 | 2715.5669
703 | 2023-01-30 07:00 | 108.4748 | 53.53 | 10 | 0 | 0 | 20 | 1620.0478
704 | 2023-01-30 08:00 | 128.1463 | 65.03 | 0 | 0 | 10 | 10 | 0
705 | 2023-01-30 09:00 | 112.5528 | 65.03 | 20 | 10 | 0 | 19.5 | 3551.6564
706 | 2023-01-30 10:00 | 112.9223 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1873.1826
707 | 2023-01-30 11:00 | 123.4589 | 65.03 | 10 | 0 | 0 | 20 | 1884.8885
708 | 2023-01-30 12:00 | 117.2908 | 65.03 | 10 | 0 | 0 | 20 | 1823.208
709 | 2023-01-30 13:00 | 124.2582 | 65.03 | 10 | 0 | 0 | 20 | 1892.8816
710 | 2023-01-30 14:00 | 118.7962 | 65.03 | 10 | 0 | 0 | 20 | 1838.2616
711 | 2023-01-30 15:00 | 124.7557 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 94.8928
712 | 2023-01-30 16:00 | 112.2249 | 65.03 | 20 | 10 | 0 | 20 | 3545.0977
713 | 2023-01-30 17:00 | 133.8078 | 66.4 | 0 | 0 | 10 | 10 | 0
714 | 2023-01-30 18:00 | 132.367 | 66.4 | 0 | 0 | 10 | 0 | 0
715 | 2023-01-30 19:00 | -28.7746 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 400.718
716 | 2023-01-30 20:00 | -36.9907 | 65.03 | 20 | 10 | 0 | 10.5 | 560.7854
717 | 2023-01-30 21:00 | -41.8621 | 65.03 | 20 | 10 | 0 | 20 | 463.3575
718 | 2023-01-30 22:00 | 111.4 | 65.03 | 0 | 0 | 10 | 10 | 0
719 | 2023-01-30 23:00 | 102.2954 | 53.53 | 10 | 0 | 0 | 10 | 1558.2538
720 | 2023-01-31 00:00 | 108.1873 | 53.53 | 10 | 0 | 0 | 10 | 1617.1727
721 | 2023-01-31 01:00 | 118.966 | 53.53 | 0 | 0 | 10 | 0 | 0
722 | 2023-01-31 02:00 | 76.5104 | 53.53 | 20 | 10 | 0 | 9.5 | 2600.8076
723 | 2023-01-31 03:00 | 79.8551 | 53.53 | 20 | 10 | 0 | 19 | 2667.7018
724 | 2023-01-31 04:00 | 82.8522 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1507.3823
725 | 2023-01-31 05:00 | 102.6521 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 78.0911
726 | 2023-01-31 06:00 | 91.1101 | 53.53 | 20 | 10 | 0 | 20 | 2892.8028
727 | 2023-01-31 07:00 | 115.3694 | 53.53 | 10 | 0 | 0 | 20 | 1688.9945
728 | 2023-01-31 08:00 | 111.6562 | 65.03 | 10 | 0 | 0 | 20 | 1766.8615
729 | 2023-01-31 09:00 | 111.7664 | 65.03 | 10 | 0 | 0 | 20 | 1767.9637
730 | 2023-01-31 10:00 | 122.493 | 65.03 | 10 | 0 | 0 | 20 | 1875.2296
731 | 2023-01-31 11:00 | 119.3392 | 65.03 | 10 | 0 | 0 | 20 | 1843.6921
732 | 2023-01-31 12:00 | 123.372 | 65.03 | 10 | 0 | 0 | 20 | 1884.0198
733 | 2023-01-31 13:00 | 117.5297 | 65.03 | 10 | 0 | 0 | 20 | 1825.5966
734 | 2023-01-31 14:00 | 121.0739 | 65.03 | 10 | 0 | 0 | 20 | 1861.0389
735 | 2023-01-31 15:00 | 120.1128 | 65.03 | 10 | 0 | 0 | 20 | 1851.4278
736 | 2023-01-31 16:00 | 125.4683 | 65.03 | 10 | 0 | 0 | 20 | 1904.9827
737 | 2023-01-31 17:00 | 140.7464 | 66.4 | 0 | 0 | 10 | 10 | 0
738 | 2023-01-31 18:00 | 124.2759 | 66.4 | 0 | 0 | 10 | 0 | 0
739 | 2023-01-31 19:00 | 121.6377 | 65.03 | 10 | 0 | 0 | 0 | 1866.6765
740 | 2023-01-31 20:00 | 122.6625 | 65.03 | 10 | 0 | 0 | 0 | 1876.9245
741 | 2023-01-31 21:00 | 124.5998 | 65.03 | 10 | 0 | 0 | 0 | 1896.2983
742 | 2023-01-31 22:00 | 107.3045 | 65.03 | 10 | 0 | 0 | 0 | 1723.3453
743 | 2023-01-31 23:00 | 98.2078 | 53.53 | 20 | 10 | 0 | 9.5 | 3034.7566
744 | 2023-02-01 00:00 | -45.0506 | 53.53 | 20 | 10 | 0 | 19 | 169.588
745 | 2023-02-01 01:00 | 116.9518 | 53.53 | 0 | 0 | 10 | 9 | 0
746 | 2023-02-01 02:00 | 106.7675 | 53.53 | 1 | 0 | 9 | 0 | 160.2975
747 | 2023-02-01 03:00 | 93.0865 | 53.53 | 10 | 0 | 0 | 0 | 1466.1652
748 | 2023-02-01 04:00 | 86.2603 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1545.0502
749 | 2023-02-01 05:00 | -39.4141 | 53.53 | 20 | 10 | 0 | 10.5 | 282.3188
750 | 2023-02-01 06:00 | -5.9863 | 53.53 | 20 | 10 | 0 | 20 | 950.8745
751 | 2023-02-01 07:00 | 106.7516 | 53.53 | 10 | 0 | 0 | 20 | 1602.8163
752 | 2023-02-01 08:00 | 112.3352 | 65.03 | 10 | 0 | 0 | 20 | 1773.6523
753 | 2023-02-01 09:00 | 140.1225 | 65.03 | 0 | 0 | 10 | 10 | 0
754 | 2023-02-01 10:00 | 136.608 | 65.03 | 0 | 0 | 10 | 0 | 0
755 | 2023-02-01 11:00 | 129.0506 | 65.03 | 10 | 0 | 0 | 0 | 1940.8062
756 | 2023-02-01 12:00 | 112.8638 | 65.03 | 20 | 10 | 0 | 9.5 | 3557.8758
757 | 2023-02-01 13:00 | 126.2085 | 65.03 | 10 | 0 | 0 | 9.5 | 1912.3846
758 | 2023-02-01 14:00 | 124.1867 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 2091.3422
759 | 2023-02-01 15:00 | 122.4478 | 65.03 | 20 | 10 | 0 | 20 | 3749.5562
760 | 2023-02-01 16:00 | 130.2694 | 65.03 | 10 | 0 | 0 | 20 | 1952.9944
761 | 2023-02-01 17:00 | 139.148 | 66.4 | 0 | 0 | 10 | 10 | 0
762 | 2023-02-01 18:00 | 140.1127 | 66.4 | 0 | 0 | 10 | 0 | 0
763 | 2023-02-01 19:00 | 139.162 | 65.03 | 10 | 0 | 0 | 0 | 2041.9197
764 | 2023-02-01 20:00 | 116.5895 | 65.03 | 10 | 0 | 0 | 0 | 1816.1947
765 | 2023-02-01 21:00 | 103.5388 | 65.03 | 20 | 10 | 0 | 9.5 | 3371.3764
766 | 2023-02-01 22:00 | 114.5334 | 65.03 | 0.5 | 0 | 9.5 | 0 | 89.7817
767 | 2023-02-01 23:00 | 105.0563 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1669.3296
768 | 2023-02-02 00:00 | 100.9274 | 53.53 | 20 | 10 | 0 | 10 | 3089.1481
769 | 2023-02-02 01:00 | 125.3041 | 53.53 | 0 | 0 | 10 | 0 | 0
770 | 2023-02-02 02:00 | 105.8943 | 53.53 | 10 | 0 | 0 | 0 | 1594.2431
771 | 2023-02-02 03:00 | 101.4847 | 53.53 | 10 | 0 | 0 | 0 | 1550.147
772 | 2023-02-02 04:00 | 90.8876 | 53.53 | 20 | 10 | 0 | 9.5 | 2888.3518
773 | 2023-02-02 05:00 | 101.3879 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1712.2505
774 | 2023-02-02 06:00 | 88.9889 | 53.53 | 20 | 10 | 0 | 20 | 2850.3774
775 | 2023-02-02 07:00 | 110.4665 | 53.53 | 10 | 0 | 0 | 20 | 1639.9651
776 | 2023-02-02 08:00 | 111.9066 | 65.03 | 10 | 0 | 0 | 20 | 1769.3664
777 | 2023-02-02 09:00 | 122.0603 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 93.5451
778 | 2023-02-02 10:00 | 119.3553 | 65.03 | 10 | 0 | 0 | 10.5 | 1843.8533
779 | 2023-02-02 11:00 | 110.8113 | 65.03 | 20 | 10 | 0 | 20 | 3516.8253
780 | 2023-02-02 12:00 | 118.5173 | 65.03 | 10 | 0 | 0 | 20 | 1835.4726
781 | 2023-02-02 13:00 | 118.3074 | 65.03 | 10 | 0 | 0 | 20 | 1833.3743
782 | 2023-02-02 14:00 | 136.7671 | 65.03 | 0 | 0 | 10 | 10 | 0
783 | 2023-02-02 15:00 | 126.5906 | 65.03 | 10 | 0 | 0 | 10 | 1916.2061
784 | 2023-02-02 16:00 | 118.9843 | 65.03 | 20 | 10 | 0 | 19.5 | 3680.2859
785 | 2023-02-02 17:00 | 135.8356 | 66.4 | 0 | 0 | 10 | 9.5 | 0
786 | 2023-02-02 18:00 | 134.2321 | 66.4 | 0.5 | 0 | 9.5 | 0 | 100.3161
787 | 2023-02-02 19:00 | 132.4218 | 65.03 | 10 | 0 | 0 | 0 | 1974.5185
788 | 2023-02-02 20:00 | 106.9664 | 65.03 | 10 | 0 | 0 | 0 | 1719.964
789 | 2023-02-02 21:00 | 112.7907 | 65.03 | 10 | 0 | 0 | 0 | 1778.207
790 | 2023-02-02 22:00 | 108.8846 | 65.03 | 10 | 0 | 0 | 0 | 1739.1459
791 | 2023-02-02 23:00 | 101.0789 | 53.53 | 20 | 10 | 0 | 9.5 | 3092.1782
792 | 2023-02-03 00:00 | 113.0421 | 53.53 | 0.5 | 0 | 9.5 | 0 | 83.2861
793 | 2023-02-03 01:00 | 112.012 | 53.53 | 10 | 0 | 0 | 0 | 1655.4196
794 | 2023-02-03 02:00 | 78.5252 | 53.53 | 20 | 10 | 0 | 9.5 | 2641.1045
795 | 2023-02-03 03:00 | 87.9949 | 53.53 | 20 | 10 | 0 | 19 | 2830.498
796 | 2023-02-03 04:00 | 97.6013 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1670.3984
797 | 2023-02-03 05:00 | 98.2497 | 53.53 | 10 | 0 | 0 | 20 | 1517.7971
798 | 2023-02-03 06:00 | 97.9074 | 53.53 | 10 | 0 | 0 | 20 | 1514.3736
799 | 2023-02-03 07:00 | 109.1919 | 53.53 | 10 | 0 | 0 | 20 | 1627.2187
800 | 2023-02-03 08:00 | 113.3 | 65.03 | 10 | 0 | 0 | 20 | 1783.3004
801 | 2023-02-03 09:00 | 111.9595 | 65.03 | 10 | 0 | 0 | 20 | 1769.8951
802 | 2023-02-03 10:00 | 121.6212 | 65.03 | 10 | 0 | 0 | 20 | 1866.5116
803 | 2023-02-03 11:00 | 121.9111 | 65.03 | 10 | 0 | 0 | 20 | 1869.4106
804 | 2023-02-03 12:00 | 130.6828 | 65.03 | 0 | 0 | 10 | 10 | 0
805 | 2023-02-03 13:00 | 128.6723 | 65.03 | 0 | 0 | 10 | 0 | 0
806 | 2023-02-03 14:00 | 117.926 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 2022.1453
807 | 2023-02-03 15:00 | 111.1104 | 65.03 | 20 | 10 | 0 | 10.5 | 3522.8086
808 | 2023-02-03 16:00 | 116.616 | 65.03 | 20 | 10 | 0 | 20 | 3632.9199
809 | 2023-02-03 17:00 | 135.5818 | 66.4 | 0 | 0 | 10 | 10 | 0
810 | 2023-02-03 18:00 | 132.4277 | 66.4 | 0 | 0 | 10 | 0 | 0
811 | 2023-02-03 19:00 | 129.919 | 65.03 | 10 | 0 | 0 | 0 | 1949.49
812 | 2023-02-03 20:00 | 115.8687 | 65.03 | 10 | 0 | 0 | 0 | 1808.9874
813 | 2023-02-03 21:00 | 110.3905 | 65.03 | 10 | 0 | 0 | 0 | 1754.2047
814 | 2023-02-03 22:00 | 109.605 | 65.03 | 10 | 0 | 0 | 0 | 1746.3498
815 | 2023-02-03 23:00 | 111.3468 | 53.53 | 10 | 0 | 0 | 0 | 1648.7681
816 | 2023-02-04 00:00 | 98.0581 | 53.53 | 10 | 0 | 0 | 0 | 1515.8807
817 | 2023-02-04 01:00 | 102.7978 | 53.53 | 10 | 0 | 0 | 0 | 1563.2779
818 | 2023-02-04 02:00 | 83.0336 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1509.3877
819 | 2023-02-04 03:00 | 73.6601 | 53.53 | 20 | 10 | 0 | 10.5 | 2543.8011
820 | 2023-02-04 04:00 | 77.5374 | 53.53 | 20 | 10 | 0 | 20 | 2621.3488
821 | 2023-02-04 05:00 | 94.381 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 73.9555
822 | 2023-02-04 06:00 | -66.5319 | 53.53 | 20 | 10 | 0 | 20 | -260.038
823 | 2023-02-04 07:00 | 89.1467 | 53.53 | 10 | 0 | 0 | 20 | 1426.7674
824 | 2023-02-04 08:00 | 100.1992 | 53.53 | 10 | 0 | 0 | 20 | 1537.292
825 | 2023-02-04 09:00 | 111.1176 | 53.53 | 10 | 0 | 0 | 20 | 1646.4759
826 | 2023-02-04 10:00 | 111.1313 | 53.53 | 10 | 0 | 0 | 20 | 1646.6126
827 | 2023-02-04 11:00 | 110.0316 | 53.53 | 10 | 0 | 0 | 20 | 1635.616
828 | 2023-02-04 12:00 | 121.8844 | 53.53 | 0 | 0 | 10 | 10 | 0
829 | 2023-02-04 13:00 | 97.1108 | 53.53 | 20 | 10 | 0 | 19.5 | 3012.8153
830 | 2023-02-04 14:00 | 114.0514 | 53.53 | 10 | 0 | 0 | 19.5 | 1675.8136
831 | 2023-02-04 15:00 | 125.8355 | 53.53 | 0 | 0 | 10 | 9.5 | 0
832 | 2023-02-04 16:00 | 103.7222 | 53.53 | 20 | 10 | 0 | 19 | 3145.0446
833 | 2023-02-04 17:00 | 123.206 | 53.53 | 0 | 0 | 10 | 9 | 0
834 | 2023-02-04 18:00 | 120.8439 | 53.53 | 1.5 | 0 | 8.5 | 0.5 | 261.5608
835 | 2023-02-04 19:00 | 120.0152 | 53.53 | 10 | 0 | 0 | 0.5 | 1735.4519
836 | 2023-02-04 20:00 | 103.5673 | 53.53 | 20 | 10 | 0 | 10 | 3141.9456
837 | 2023-02-04 21:00 | 119.2624 | 53.53 | 10 | 0 | 0 | 10 | 1727.9238
838 | 2023-02-04 22:00 | 124.2824 | 53.53 | 0 | 0 | 10 | 0 | 0
839 | 2023-02-04 23:00 | 98.5016 | 53.53 | 20 | 10 | 0 | 9.5 | 3040.6313
840 | 2023-02-05 00:00 | 120.1721 | 53.53 | 0.5 | 0 | 9.5 | 0 | 86.8511
841 | 2023-02-05 01:00 | 101.1666 | 53.53 | 10 | 0 | 0 | 0 | 1546.9656
842 | 2023-02-05 02:00 | 98.2066 | 53.53 | 10 | 0 | 0 | 0 | 1517.366
843 | 2023-02-05 03:00 | 80.2083 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1478.1598
844 | 2023-02-05 04:00 | 81.9008 | 53.53 | 10 | 0 | 0 | 1 | 1354.3082
845 | 2023-02-05 05:00 | 83.7953 | 53.53 | 10 | 0 | 0 | 1 | 1373.2528
846 | 2023-02-05 06:00 | -25.7359 | 53.53 | 20 | 10 | 0 | 10.5 | 555.8813
847 | 2023-02-05 07:00 | -67.504 | 53.53 | 20 | 10 | 0 | 20 | -279.4809
848 | 2023-02-05 08:00 | 106.1188 | 53.53 | 10 | 0 | 0 | 20 | 1596.488
849 | 2023-02-05 09:00 | 119.3324 | 53.53 | 0 | 0 | 10 | 10 | 0
850 | 2023-02-05 10:00 | 108.3267 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1703.7543
851 | 2023-02-05 11:00 | 107.4823 | 53.53 | 20 | 10 | 0 | 20 | 3220.2455
852 | 2023-02-05 12:00 | 118.732 | 53.53 | 10 | 0 | 0 | 20 | 1722.6203
853 | 2023-02-05 13:00 | 111.1325 | 53.53 | 10 | 0 | 0 | 20 | 1646.6254
854 | 2023-02-05 14:00 | 113.0774 | 53.53 | 10 | 0 | 0 | 20 | 1666.0741
855 | 2023-02-05 15:00 | 111.0034 | 53.53 | 10 | 0 | 0 | 20 | 1645.3342
856 | 2023-02-05 16:00 | 113.5545 | 53.53 | 10 | 0 | 0 | 20 | 1670.8453
857 | 2023-02-05 17:00 | 129.2976 | 53.53 | 0 | 0 | 10 | 10 | 0
858 | 2023-02-05 18:00 | 114.8805 | 53.53 | 10 | 0 | 0 | 10 | 1684.1052
859 | 2023-02-05 19:00 | 131.4325 | 53.53 | 0 | 0 | 10 | 0 | 0
860 | 2023-02-05 20:00 | 99.5189 | 53.53 | 10 | 0 | 0 | 0 | 1530.4893
861 | 2023-02-05 21:00 | 97.1173 | 53.53 | 20 | 10 | 0 | 9.5 | 3012.947
862 | 2023-02-05 22:00 | 105.464 | 53.53 | 0.5 | 0 | 9.5 | 0 | 79.497
863 | 2023-02-05 23:00 | 101.5362 | 53.53 | 10 | 0 | 0 | 0 | 1550.6617
864 | 2023-02-06 00:00 | 104.2024 | 53.53 | 10 | 0 | 0 | 0 | 1577.3243
865 | 2023-02-06 01:00 | -13.6025 | 53.53 | 20 | 10 | 0 | 9.5 | 798.55
866 | 2023-02-06 02:00 | 80.6119 | 53.53 | 20 | 10 | 0 | 19 | 2682.8383
867 | 2023-02-06 03:00 | 86.0252 | 53.53 | 10 | 0 | 0 | 19 | 1395.5518
868 | 2023-02-06 04:00 | 84.875 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1529.7398
869 | 2023-02-06 05:00 | 88.5513 | 53.53 | 10 | 0 | 0 | 20 | 1420.8133
870 | 2023-02-06 06:00 | 91.0798 | 53.53 | 10 | 0 | 0 | 20 | 1446.0977
871 | 2023-02-06 07:00 | 102.375 | 53.53 | 10 | 0 | 0 | 20 | 1559.0496
872 | 2023-02-06 08:00 | 124.9658 | 65.03 | 0 | 0 | 10 | 10 | 0
873 | 2023-02-06 09:00 | 119.3753 | 65.03 | 1 | 0 | 9 | 1 | 184.4053
874 | 2023-02-06 10:00 | 108.0706 | 65.03 | 20 | 10 | 0 | 10.5 | 3462.0129
875 | 2023-02-06 11:00 | 107.7901 | 65.03 | 20 | 10 | 0 | 20 | 3456.402
876 | 2023-02-06 12:00 | 118.8061 | 65.03 | 10 | 0 | 0 | 20 | 1838.3608
877 | 2023-02-06 13:00 | 117.2948 | 65.03 | 10 | 0 | 0 | 20 | 1823.2479
878 | 2023-02-06 14:00 | 118.1346 | 65.03 | 10 | 0 | 0 | 20 | 1831.6456
879 | 2023-02-06 15:00 | 118.6893 | 65.03 | 10 | 0 | 0 | 20 | 1837.1932
880 | 2023-02-06 16:00 | 120.6486 | 65.03 | 10 | 0 | 0 | 20 | 1856.7855
881 | 2023-02-06 17:00 | 142.1189 | 66.4 | 0 | 0 | 10 | 10 | 0
882 | 2023-02-06 18:00 | 126.8116 | 66.4 | 0 | 0 | 10 | 0 | 0
883 | 2023-02-06 19:00 | 126.4875 | 65.03 | 10 | 0 | 0 | 0 | 1915.1749
884 | 2023-02-06 20:00 | 106.9074 | 65.03 | 20 | 10 | 0 | 9.5 | 3438.7487
885 | 2023-02-06 21:00 | 116.1619 | 65.03 | 10 | 0 | 0 | 9.5 | 1811.9186
886 | 2023-02-06 22:00 | 125.218 | 65.03 | 0.5 | 0 | 9.5 | 0 | 95.124
887 | 2023-02-06 23:00 | 105.8638 | 53.53 | 10 | 0 | 0 | 0 | 1593.9383
888 | 2023-02-07 00:00 | 95.7014 | 53.53 | 10 | 0 | 0 | 0 | 1492.3145
889 | 2023-02-07 01:00 | 98.8927 | 53.53 | 10 | 0 | 0 | 0 | 1524.2272
890 | 2023-02-07 02:00 | 83.3701 | 53.53 | 20 | 10 | 0 | 9.5 | 2738.0012
891 | 2023-02-07 03:00 | 85.0466 | 53.53 | 20 | 10 | 0 | 19 | 2771.5311
892 | 2023-02-07 04:00 | 86.0156 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1542.346
893 | 2023-02-07 05:00 | 89.1893 | 53.53 | 10 | 0 | 0 | 20 | 1427.1935
894 | 2023-02-07 06:00 | 86.6662 | 53.53 | 10 | 0 | 0 | 20 | 1401.9621
895 | 2023-02-07 07:00 | 118.148 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 85.839
896 | 2023-02-07 08:00 | -45.9519 | 65.03 | 20 | 10 | 0 | 20 | 381.5619
897 | 2023-02-07 09:00 | 113.1998 | 65.03 | 10 | 0 | 0 | 20 | 1782.2976
898 | 2023-02-07 10:00 | 122.7607 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 93.8953
899 | 2023-02-07 11:00 | 109.6695 | 65.03 | 20 | 10 | 0 | 20 | 3493.9894
900 | 2023-02-07 12:00 | 121.9987 | 65.03 | 10 | 0 | 0 | 20 | 1870.2869
901 | 2023-02-07 13:00 | 119.6794 | 65.03 | 10 | 0 | 0 | 20 | 1847.0941
902 | 2023-02-07 14:00 | 117.8166 | 65.03 | 10 | 0 | 0 | 20 | 1828.4659
903 | 2023-02-07 15:00 | 134.1583 | 65.03 | 0 | 0 | 10 | 10 | 0
904 | 2023-02-07 16:00 | 114.6414 | 65.03 | 20 | 10 | 0 | 19.5 | 3593.4281
905 | 2023-02-07 17:00 | 155.2828 | 66.4 | 0 | 0 | 10 | 9.5 | 0
906 | 2023-02-07 18:00 | 132.2635 | 66.4 | 0.5 | 0 | 9.5 | 0 | 99.3317
907 | 2023-02-07 19:00 | 125.9418 | 65.03 | 10 | 0 | 0 | 0 | 1909.7184
908 | 2023-02-07 20:00 | 114.4282 | 65.03 | 10 | 0 | 0 | 0 | 1794.5824
909 | 2023-02-07 21:00 | 106.9999 | 65.03 | 10 | 0 | 0 | 0 | 1720.2994
910 | 2023-02-07 22:00 | 108.8507 | 65.03 | 10 | 0 | 0 | 0 | 1738.807
911 | 2023-02-07 23:00 | 112.0607 | 53.53 | 10 | 0 | 0 | 0 | 1655.9065
912 | 2023-02-08 00:00 | 113.4326 | 53.53 | 10 | 0 | 0 | 0 | 1669.6255
913 | 2023-02-08 01:00 | 104.6417 | 53.53 | 10 | 0 | 0 | 0 | 1581.7165
914 | 2023-02-08 02:00 | 97.5175 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1669.4724
915 | 2023-02-08 03:00 | 99.2777 | 53.53 | 10 | 0 | 0 | 1 | 1528.0765
916 | 2023-02-08 04:00 | 102.364 | 53.53 | 10 | 0 | 0 | 1 | 1558.9398
917 | 2023-02-08 05:00 | 93.2016 | 53.53 | 20 | 10 | 0 | 10.5 | 2934.632
918 | 2023-02-08 06:00 | -32.3849 | 53.53 | 20 | 10 | 0 | 20 | 422.9021
919 | 2023-02-08 07:00 | 98.1181 | 53.53 | 10 | 0 | 0 | 20 | 1516.4812
920 | 2023-02-08 08:00 | 116.6242 | 65.03 | 0 | 0 | 10 | 10 | 0
921 | 2023-02-08 09:00 | 113.1726 | 65.03 | 1 | 0 | 9 | 1 | 178.2026
922 | 2023-02-08 10:00 | -10.8657 | 65.03 | 20 | 10 | 0 | 10.5 | 1083.2867
923 | 2023-02-08 11:00 | -62.7832 | 65.03 | 20 | 10 | 0 | 20 | 44.9364
924 | 2023-02-08 12:00 | 117.6827 | 65.03 | 10 | 0 | 0 | 20 | 1827.1267
925 | 2023-02-08 13:00 | 137.8692 | 65.03 | 0 | 0 | 10 | 10 | 0
926 | 2023-02-08 14:00 | 117.6573 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1923.0239
927 | 2023-02-08 15:00 | 122.2026 | 65.03 | 10 | 0 | 0 | 10.5 | 1872.326
928 | 2023-02-08 16:00 | 117.2156 | 65.03 | 20 | 10 | 0 | 20 | 3644.9119
929 | 2023-02-08 17:00 | 134.4727 | 66.4 | 0 | 0 | 10 | 10 | 0
930 | 2023-02-08 18:00 | 133.9435 | 66.4 | 10 | 0 | 0 | 10 | 2003.4347
931 | 2023-02-08 19:00 | 137.4973 | 65.03 | 0 | 0 | 10 | 0 | 0
932 | 2023-02-08 20:00 | 124.3605 | 65.03 | 10 | 0 | 0 | 0 | 1893.9053
933 | 2023-02-08 21:00 | 129.8787 | 65.03 | 10 | 0 | 0 | 0 | 1949.0871
934 | 2023-02-08 22:00 | 116.3317 | 65.03 | 10 | 0 | 0 | 0 | 1813.6172
935 | 2023-02-08 23:00 | 113.735 | 53.53 | 10 | 0 | 0 | 0 | 1672.6503
936 | 2023-02-09 00:00 | 101.5992 | 53.53 | 10 | 0 | 0 | 0 | 1551.2922
937 | 2023-02-09 01:00 | 108.2478 | 53.53 | 10 | 0 | 0 | 0 | 1617.7784
938 | 2023-02-09 02:00 | 97.0457 | 53.53 | 10 | 0 | 0 | 0 | 1505.7565
939 | 2023-02-09 03:00 | 96.3148 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1656.179
940 | 2023-02-09 04:00 | 90.5368 | 53.53 | 20 | 10 | 0 | 10.5 | 2881.3368
941 | 2023-02-09 05:00 | 96.514 | 53.53 | 10 | 0 | 0 | 10.5 | 1500.4401
942 | 2023-02-09 06:00 | 92.8638 | 53.53 | 20 | 10 | 0 | 20 | 2927.8763
943 | 2023-02-09 07:00 | 119.7348 | 53.53 | 10 | 0 | 0 | 20 | 1732.6483
944 | 2023-02-09 08:00 | 121.1655 | 65.03 | 1.5 | 0 | 8.5 | 11.5 | 279.2932
945 | 2023-02-09 09:00 | 116.368 | 65.03 | 10 | 0 | 0 | 11.5 | 1813.9797
946 | 2023-02-09 10:00 | 121.5484 | 65.03 | 0 | 0 | 10 | 1.5 | 0
947 | 2023-02-09 11:00 | 104.2764 | 65.03 | 20 | 10 | 0 | 11 | 3386.1281
948 | 2023-02-09 12:00 | 121.9414 | 65.03 | 0 | 0 | 10 | 1 | 0
949 | 2023-02-09 13:00 | 102.2658 | 65.03 | 20 | 10 | 0 | 10.5 | 3345.9156
950 | 2023-02-09 14:00 | 108.8054 | 65.03 | 20 | 10 | 0 | 20 | 3476.7079
951 | 2023-02-09 15:00 | 122.5269 | 65.03 | 10 | 0 | 0 | 20 | 1875.5691
952 | 2023-02-09 16:00 | 122.749 | 65.03 | 10 | 0 | 0 | 20 | 1877.7902
953 | 2023-02-09 17:00 | 126.5379 | 66.4 | 10 | 0 | 0 | 20 | 1929.3792
954 | 2023-02-09 18:00 | 129.0895 | 66.4 | 0.5 | 0 | 9.5 | 10.5 | 97.7447
955 | 2023-02-09 19:00 | 146.6126 | 65.03 | 0 | 0 | 10 | 0.5 | 0
956 | 2023-02-09 20:00 | 110.5193 | 65.03 | 20 | 10 | 0 | 10 | 3510.9869
957 | 2023-02-09 21:00 | 137.895 | 65.03 | 0 | 0 | 10 | 0 | 0
958 | 2023-02-09 22:00 | 113.8839 | 65.03 | 10 | 0 | 0 | 0 | 1789.1391
959 | 2023-02-09 23:00 | 112.1538 | 53.53 | 20 | 10 | 0 | 9.5 | 3313.6753
960 | 2023-02-10 00:00 | 124.5052 | 53.53 | 0.5 | 0 | 9.5 | 0 | 89.0176
961 | 2023-02-10 01:00 | 109.9006 | 53.53 | 10 | 0 | 0 | 0 | 1634.3058
962 | 2023-02-10 02:00 | 82.4057 | 53.53 | 20 | 10 | 0 | 9.5 | 2718.7149
963 | 2023-02-10 03:00 | 88.0887 | 53.53 | 10 | 0 | 0 | 9.5 | 1416.1875
964 | 2023-02-10 04:00 | 88.6326 | 53.53 | 10 | 0 | 0 | 9.5 | 1421.6265
965 | 2023-02-10 05:00 | 80.4991 | 53.53 | 20 | 10 | 0 | 19 | 2680.5829
966 | 2023-02-10 06:00 | 87.0513 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1553.7939
967 | 2023-02-10 07:00 | 103.908 | 53.53 | 10 | 0 | 0 | 20 | 1574.3803
968 | 2023-02-10 08:00 | 126.8876 | 65.03 | 0 | 0 | 10 | 10 | 0
969 | 2023-02-10 09:00 | 119.1592 | 65.03 | 10 | 0 | 0 | 10 | 1841.8925
970 | 2023-02-10 10:00 | 116.8648 | 65.03 | 10 | 0 | 0 | 10 | 1818.9482
971 | 2023-02-10 11:00 | 118.1145 | 65.03 | 10 | 0 | 0 | 10 | 1831.4449
972 | 2023-02-10 12:00 | 120.629 | 65.03 | 10 | 0 | 0 | 10 | 1856.59
973 | 2023-02-10 13:00 | 123.9801 | 65.03 | 1 | 0 | 9 | 1 | 189.0101
974 | 2023-02-10 14:00 | 112.4204 | 65.03 | 20 | 10 | 0 | 10.5 | 3549.0072
975 | 2023-02-10 15:00 | 112.1891 | 65.03 | 20 | 10 | 0 | 20 | 3544.3826
976 | 2023-02-10 16:00 | 128.7214 | 65.03 | 10 | 0 | 0 | 20 | 1937.5136
977 | 2023-02-10 17:00 | 130.9894 | 66.4 | 0 | 0 | 10 | 10 | 0
978 | 2023-02-10 18:00 | 125.2417 | 66.4 | 10 | 0 | 0 | 10 | 1916.4169
979 | 2023-02-10 19:00 | 137.4587 | 65.03 | 0 | 0 | 10 | 0 | 0
980 | 2023-02-10 20:00 | -24.6545 | 65.03 | 20 | 10 | 0 | 9.5 | 807.5093
981 | 2023-02-10 21:00 | -50.1547 | 65.03 | 20 | 10 | 0 | 19 | 297.5054
982 | 2023-02-10 22:00 | 115.68 | 65.03 | 0 | 0 | 10 | 9 | 0
983 | 2023-02-10 23:00 | 115.0713 | 53.53 | 1 | 0 | 9 | 0 | 168.6013
984 | 2023-02-11 00:00 | 103.87 | 53.53 | 10 | 0 | 0 | 0 | 1573.9996
985 | 2023-02-11 01:00 | 106.1173 | 53.53 | 10 | 0 | 0 | 0 | 1596.4729
986 | 2023-02-11 02:00 | 72.3035 | 53.53 | 20 | 10 | 0 | 9.5 | 2516.6691
987 | 2023-02-11 03:00 | 83.5086 | 53.53 | 10 | 0 | 0 | 9.5 | 1370.3858
988 | 2023-02-11 04:00 | 78.7286 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1461.806
989 | 2023-02-11 05:00 | 77.5274 | 53.53 | 20 | 10 | 0 | 20 | 2621.1478
990 | 2023-02-11 06:00 | 88.3594 | 53.53 | 10 | 0 | 0 | 20 | 1418.8941
991 | 2023-02-11 07:00 | 114.8631 | 53.53 | 10 | 0 | 0 | 20 | 1683.9309
992 | 2023-02-11 08:00 | 128.7261 | 53.53 | 0 | 0 | 10 | 10 | 0
993 | 2023-02-11 09:00 | 122.9872 | 53.53 | 0 | 0 | 10 | 0 | 0
994 | 2023-02-11 10:00 | 110.0887 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1808.4172
995 | 2023-02-11 11:00 | -39.4364 | 53.53 | 20 | 10 | 0 | 10.5 | 281.8718
996 | 2023-02-11 12:00 | 117.3648 | 53.53 | 10 | 0 | 0 | 10.5 | 1708.9478
997 | 2023-02-11 13:00 | -23.0087 | 53.53 | 20 | 10 | 0 | 20 | 610.4253
998 | 2023-02-11 14:00 | 111.8985 | 53.53 | 10 | 0 | 0 | 20 | 1654.2853
999 | 2023-02-11 15:00 | 117.9068 | 53.53 | 10 | 0 | 0 | 20 | 1714.3681
1000 | 2023-02-11 16:00 | 110.4576 | 53.53 | 10 | 0 | 0 | 20 | 1639.8762
1001 | 2023-02-11 17:00 | 120.9856 | 53.53 | 10 | 0 | 0 | 20 | 1745.1565
1002 | 2023-02-11 18:00 | 122.9753 | 53.53 | 0 | 0 | 10 | 10 | 0
1003 | 2023-02-11 19:00 | 131.1348 | 53.53 | 0 | 0 | 10 | 0 | 0
1004 | 2023-02-11 20:00 | 105.9208 | 53.53 | 10 | 0 | 0 | 0 | 1594.5077
1005 | 2023-02-11 21:00 | 108.5846 | 53.53 | 10 | 0 | 0 | 0 | 1621.1464
1006 | 2023-02-11 22:00 | 111.4647 | 53.53 | 10 | 0 | 0 | 0 | 1649.9465
1007 | 2023-02-11 23:00 | 98.2393 | 53.53 | 20 | 10 | 0 | 9.5 | 3035.386
1008 | 2023-02-12 00:00 | 107.2651 | 53.53 | 0.5 | 0 | 9.5 | 0 | 80.3976
1009 | 2023-02-12 01:00 | 103.9074 | 53.53 | 10 | 0 | 0 | 0 | 1574.3738
1010 | 2023-02-12 02:00 | 73.159 | 53.53 | 10 | 0 | 0 | 0 | 1266.89
1011 | 2023-02-12 03:00 | -49.7992 | 53.53 | 20 | 10 | 0 | 9.5 | 74.6165
1012 | 2023-02-12 04:00 | -26.5175 | 53.53 | 20 | 10 | 0 | 19 | 540.2509
1013 | 2023-02-12 05:00 | -7.4975 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 508.7808
1014 | 2023-02-12 06:00 | 74.1702 | 53.53 | 10 | 0 | 0 | 20 | 1277.0018
1015 | 2023-02-12 07:00 | 94.3022 | 53.53 | 10 | 0 | 0 | 20 | 1478.322
1016 | 2023-02-12 08:00 | 111.2927 | 53.53 | 10 | 0 | 0 | 20 | 1648.2268
1017 | 2023-02-12 09:00 | 108.9265 | 53.53 | 10 | 0 | 0 | 20 | 1624.5653
1018 | 2023-02-12 10:00 | 108.4955 | 53.53 | 10 | 0 | 0 | 20 | 1620.2551
1019 | 2023-02-12 11:00 | 116.0062 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 84.7681
1020 | 2023-02-12 12:00 | 113.5819 | 53.53 | 10 | 0 | 0 | 10.5 | 1671.1186
1021 | 2023-02-12 13:00 | 113.3847 | 53.53 | 10 | 0 | 0 | 10.5 | 1669.1467
1022 | 2023-02-12 14:00 | 114.169 | 53.53 | 10 | 0 | 0 | 10.5 | 1676.9896
1023 | 2023-02-12 15:00 | 115.974 | 53.53 | 10 | 0 | 0 | 10.5 | 1695.0397
1024 | 2023-02-12 16:00 | 99.1814 | 53.53 | 20 | 10 | 0 | 20 | 3054.2274
1025 | 2023-02-12 17:00 | 123.3091 | 53.53 | 0 | 0 | 10 | 10 | 0
1026 | 2023-02-12 18:00 | 113.8965 | 53.53 | 10 | 0 | 0 | 10 | 1674.2653
1027 | 2023-02-12 19:00 | 126.1702 | 53.53 | 0 | 0 | 10 | 0 | 0
1028 | 2023-02-12 20:00 | 105.8636 | 53.53 | 20 | 10 | 0 | 9.5 | 3187.8717
1029 | 2023-02-12 21:00 | 115.1089 | 53.53 | 10 | 0 | 0 | 9.5 | 1686.389
1030 | 2023-02-12 22:00 | 116.5989 | 53.53 | 0.5 | 0 | 9.5 | 0 | 85.0644
1031 | 2023-02-12 23:00 | 102.4663 | 53.53 | 10 | 0 | 0 | 0 | 1559.9633
1032 | 2023-02-13 00:00 | 105.4137 | 53.53 | 10 | 0 | 0 | 0 | 1589.4367
1033 | 2023-02-13 01:00 | -45.3399 | 53.53 | 20 | 10 | 0 | 9.5 | 163.8027
1034 | 2023-02-13 02:00 | 85.2365 | 53.53 | 20 | 10 | 0 | 19 | 2775.3308
1035 | 2023-02-13 03:00 | 88.8879 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1574.0922
1036 | 2023-02-13 04:00 | 97.5047 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 75.5174
1037 | 2023-02-13 05:00 | 85.0463 | 53.53 | 20 | 10 | 0 | 20 | 2771.5257
1038 | 2023-02-13 06:00 | 95.7337 | 53.53 | 10 | 0 | 0 | 20 | 1492.6372
1039 | 2023-02-13 07:00 | 114.5319 | 53.53 | 10 | 0 | 0 | 20 | 1680.6187
1040 | 2023-02-13 08:00 | 112.6717 | 65.03 | 10 | 0 | 0 | 20 | 1777.0166
1041 | 2023-02-13 09:00 | 127.3815 | 65.03 | 0 | 0 | 10 | 10 | 0
1042 | 2023-02-13 10:00 | 124.727 | 65.03 | 0 | 0 | 10 | 0 | 0
1043 | 2023-02-13 11:00 | 119.6746 | 65.03 | 10 | 0 | 0 | 0 | 1847.0456
1044 | 2023-02-13 12:00 | 113.7875 | 65.03 | 20 | 10 | 0 | 9.5 | 3576.3509
1045 | 2023-02-13 13:00 | 113.2178 | 65.03 | 20 | 10 | 0 | 19 | 3564.9558
1046 | 2023-02-13 14:00 | 115.1743 | 65.03 | 10 | 0 | 0 | 19 | 1802.0425
1047 | 2023-02-13 15:00 | 123.3177 | 65.03 | 1.5 | 0 | 8.5 | 10.5 | 282.5216
1048 | 2023-02-13 16:00 | 112.667 | 65.03 | 20 | 10 | 0 | 20 | 3553.9393
1049 | 2023-02-13 17:00 | 137.4047 | 66.4 | 0 | 0 | 10 | 10 | 0
1050 | 2023-02-13 18:00 | 126.1231 | 66.4 | 10 | 0 | 0 | 10 | 1925.2309
1051 | 2023-02-13 19:00 | 132.4137 | 65.03 | 0.5 | 0 | 9.5 | 0.5 | 98.7218
1052 | 2023-02-13 20:00 | 114.7343 | 65.03 | 20 | 10 | 0 | 10 | 3595.2868
1053 | 2023-02-13 21:00 | 140.9592 | 65.03 | 0 | 0 | 10 | 0 | 0
1054 | 2023-02-13 22:00 | 105.4366 | 65.03 | 10 | 0 | 0 | 0 | 1704.6664
1055 | 2023-02-13 23:00 | 122.7783 | 53.53 | 10 | 0 | 0 | 0 | 1763.0831
1056 | 2023-02-14 00:00 | 110.0478 | 53.53 | 10 | 0 | 0 | 0 | 1635.7777
1057 | 2023-02-14 01:00 | 112.1804 | 53.53 | 10 | 0 | 0 | 0 | 1657.1036
1058 | 2023-02-14 02:00 | 89.8019 | 53.53 | 20 | 10 | 0 | 9.5 | 2866.6372
1059 | 2023-02-14 03:00 | 92.4665 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1613.6455
1060 | 2023-02-14 04:00 | 87.7718 | 53.53 | 20 | 10 | 0 | 20 | 2826.0367
1061 | 2023-02-14 05:00 | 102.5693 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 78.0497
1062 | 2023-02-14 06:00 | 85.6988 | 53.53 | 20 | 10 | 0 | 20 | 2784.5768
1063 | 2023-02-14 07:00 | 119.0104 | 53.53 | 10 | 0 | 0 | 20 | 1725.4042
1064 | 2023-02-14 08:00 | 114.504 | 65.03 | 10 | 0 | 0 | 20 | 1795.3396
1065 | 2023-02-14 09:00 | 118.4505 | 65.03 | 10 | 0 | 0 | 20 | 1834.8048
1066 | 2023-02-14 10:00 | 112.0232 | 65.03 | 10 | 0 | 0 | 20 | 1770.5321
1067 | 2023-02-14 11:00 | 122.5549 | 65.03 | 1 | 0 | 9 | 11 | 187.5849
1068 | 2023-02-14 12:00 | 132.4659 | 65.03 | 0 | 0 | 10 | 1 | 0
1069 | 2023-02-14 13:00 | 118.3248 | 65.03 | 10 | 0 | 0 | 1 | 1833.5481
1070 | 2023-02-14 14:00 | -54.3745 | 65.03 | 20 | 10 | 0 | 10.5 | 213.1096
1071 | 2023-02-14 15:00 | 111.7928 | 65.03 | 20 | 10 | 0 | 20 | 3536.4552
1072 | 2023-02-14 16:00 | 117.2364 | 65.03 | 10 | 0 | 0 | 20 | 1822.6642
1073 | 2023-02-14 17:00 | 124.4014 | 66.4 | 10 | 0 | 0 | 20 | 1908.0137
1074 | 2023-02-14 18:00 | 127.9092 | 66.4 | 10 | 0 | 0 | 20 | 1943.092
1075 | 2023-02-14 19:00 | 135.6584 | 65.03 | 0 | 0 | 10 | 10 | 0
1076 | 2023-02-14 20:00 | 126.034 | 65.03 | 10 | 0 | 0 | 10 | 1910.6404
1077 | 2023-02-14 21:00 | 146.9677 | 65.03 | 0 | 0 | 10 | 0 | 0
1078 | 2023-02-14 22:00 | 109.8643 | 65.03 | 10 | 0 | 0 | 0 | 1748.9427
1079 | 2023-02-14 23:00 | 122.3524 | 53.53 | 10 | 0 | 0 | 0 | 1758.8243
1080 | 2023-02-15 00:00 | -9.0362 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 491.7734
1081 | 2023-02-15 01:00 | -61.0357 | 53.53 | 20 | 10 | 0 | 10.5 | -150.1132
1082 | 2023-02-15 02:00 | -30.9275 | 53.53 | 20 | 10 | 0 | 20 | 452.0505
1083 | 2023-02-15 03:00 | 89.367 | 53.53 | 1 | 0 | 9 | 11 | 142.897
1084 | 2023-02-15 04:00 | 89.7401 | 53.53 | 0 | 0 | 10 | 1 | 0
1085 | 2023-02-15 05:00 | 86.016 | 53.53 | 10 | 0 | 0 | 1 | 1395.4595
1086 | 2023-02-15 06:00 | -49.299 | 53.53 | 20 | 10 | 0 | 10.5 | 84.6194
1087 | 2023-02-15 07:00 | -56.5179 | 53.53 | 20 | 10 | 0 | 20 | -59.7575
1088 | 2023-02-15 08:00 | 124.3107 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 94.6703
1089 | 2023-02-15 09:00 | 116.9069 | 65.03 | 10 | 0 | 0 | 10.5 | 1819.3685
1090 | 2023-02-15 10:00 | 114.8046 | 65.03 | 20 | 10 | 0 | 20 | 3596.6915
1091 | 2023-02-15 11:00 | 118.9622 | 65.03 | 10 | 0 | 0 | 20 | 1839.9218
1092 | 2023-02-15 12:00 | 125.6313 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 95.3306
1093 | 2023-02-15 13:00 | 120.2883 | 65.03 | 10 | 0 | 0 | 10.5 | 1853.183
1094 | 2023-02-15 14:00 | 114.4318 | 65.03 | 20 | 10 | 0 | 20 | 3589.2368
1095 | 2023-02-15 15:00 | 130.0153 | 65.03 | 10 | 0 | 0 | 20 | 1950.4531
1096 | 2023-02-15 16:00 | 134.0487 | 65.03 | 10 | 0 | 0 | 20 | 1990.7867
1097 | 2023-02-15 17:00 | 137.8968 | 66.4 | 10 | 0 | 0 | 20 | 2042.9677
1098 | 2023-02-15 18:00 | 142.3792 | 66.4 | 0 | 0 | 10 | 10 | 0
1099 | 2023-02-15 19:00 | 145.1855 | 65.03 | 0 | 0 | 10 | 0 | 0
1100 | 2023-02-15 20:00 | 123.9879 | 65.03 | 10 | 0 | 0 | 0 | 1890.1794
1101 | 2023-02-15 21:00 | 118.9556 | 65.03 | 10 | 0 | 0 | 0 | 1839.8561
1102 | 2023-02-15 22:00 | 118.8139 | 65.03 | 10 | 0 | 0 | 0 | 1838.439
1103 | 2023-02-15 23:00 | 113.116 | 53.53 | 10 | 0 | 0 | 0 | 1666.4599
1104 | 2023-02-16 00:00 | 101.8858 | 53.53 | 20 | 10 | 0 | 9.5 | 3108.3152
1105 | 2023-02-16 01:00 | 114.7469 | 53.53 | 0.5 | 0 | 9.5 | 0 | 84.1385
1106 | 2023-02-16 02:00 | 80.5437 | 53.53 | 20 | 10 | 0 | 9.5 | 2681.4734
1107 | 2023-02-16 03:00 | 83.5959 | 53.53 | 20 | 10 | 0 | 19 | 2742.5178
1108 | 2023-02-16 04:00 | 100.8623 | 53.53 | 10 | 0 | 0 | 19 | 1543.9234
1109 | 2023-02-16 05:00 | 96.0653 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1653.4221
1110 | 2023-02-16 06:00 | 102.9582 | 53.53 | 10 | 0 | 0 | 20 | 1564.8816
1111 | 2023-02-16 07:00 | 106.9416 | 53.53 | 10 | 0 | 0 | 20 | 1604.7157
1112 | 2023-02-16 08:00 | 111.5919 | 65.03 | 10 | 0 | 0 | 20 | 1766.2187
1113 | 2023-02-16 09:00 | 117.1585 | 65.03 | 10 | 0 | 0 | 20 | 1821.8853
1114 | 2023-02-16 10:00 | 119.6754 | 65.03 | 10 | 0 | 0 | 20 | 1847.0537
1115 | 2023-02-16 11:00 | 119.4978 | 65.03 | 10 | 0 | 0 | 20 | 1845.278
1116 | 2023-02-16 12:00 | 129.0257 | 65.03 | 0 | 0 | 10 | 10 | 0
1117 | 2023-02-16 13:00 | 116.3304 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1909.0573
1118 | 2023-02-16 14:00 | 121.683 | 65.03 | 10 | 0 | 0 | 10.5 | 1867.1302
1119 | 2023-02-16 15:00 | 112.4821 | 65.03 | 20 | 10 | 0 | 20 | 3550.2412
1120 | 2023-02-16 16:00 | 122.5144 | 65.03 | 10 | 0 | 0 | 20 | 1875.4445
1121 | 2023-02-16 17:00 | 133.9216 | 66.4 | 0 | 0 | 10 | 10 | 0
1122 | 2023-02-16 18:00 | 128.8623 | 66.4 | 10 | 0 | 0 | 10 | 1952.6233
1123 | 2023-02-16 19:00 | 132.1907 | 65.03 | 0 | 0 | 10 | 0 | 0
1124 | 2023-02-16 20:00 | 112.5545 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1869.3101
1125 | 2023-02-16 21:00 | 111.9521 | 65.03 | 20 | 10 | 0 | 10 | 3539.6415
1126 | 2023-02-16 22:00 | 131.4312 | 65.03 | 0 | 0 | 10 | 0 | 0
1127 | 2023-02-16 23:00 | 108.1708 | 53.53 | 10 | 0 | 0 | 0 | 1617.0076
1128 | 2023-02-17 00:00 | 107.1344 | 53.53 | 10 | 0 | 0 | 0 | 1606.644
1129 | 2023-02-17 01:00 | 97.2233 | 53.53 | 10 | 0 | 0 | 0 | 1507.5329
1130 | 2023-02-17 02:00 | 83.016 | 53.53 | 20 | 10 | 0 | 9.5 | 2730.9197
1131 | 2023-02-17 03:00 | 87.0011 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1553.2385
1132 | 2023-02-17 04:00 | 84.2491 | 53.53 | 20 | 10 | 0 | 20 | 2755.582
1133 | 2023-02-17 05:00 | 101.7391 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 77.6346
1134 | 2023-02-17 06:00 | 87.6914 | 53.53 | 20 | 10 | 0 | 20 | 2824.4276
1135 | 2023-02-17 07:00 | 120.695 | 53.53 | 10 | 0 | 0 | 20 | 1742.2504
1136 | 2023-02-17 08:00 | 119.3654 | 65.03 | 0 | 0 | 10 | 10 | 0
1137 | 2023-02-17 09:00 | 119.1791 | 65.03 | 10 | 0 | 0 | 10 | 1842.0908
1138 | 2023-02-17 10:00 | 118.2411 | 65.03 | 10 | 0 | 0 | 10 | 1832.7112
1139 | 2023-02-17 11:00 | 118.9268 | 65.03 | 10 | 0 | 0 | 10 | 1839.5679
1140 | 2023-02-17 12:00 | 135.766 | 65.03 | 0 | 0 | 10 | 0 | 0
1141 | 2023-02-17 13:00 | 106.3642 | 65.03 | 10 | 0 | 0 | 0 | 1713.9415
1142 | 2023-02-17 14:00 | 107.6122 | 65.03 | 10 | 0 | 0 | 0 | 1726.4224
1143 | 2023-02-17 15:00 | 115.1391 | 65.03 | 10 | 0 | 0 | 0 | 1801.6912
1144 | 2023-02-17 16:00 | -21.6332 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 479.6488
1145 | 2023-02-17 17:00 | -50.1761 | 66.4 | 20 | 10 | 0 | 10.5 | 324.478
1146 | 2023-02-17 18:00 | -73.2715 | 66.4 | 20 | 10 | 0 | 20 | -137.4306
1147 | 2023-02-17 19:00 | 131.1764 | 65.03 | 0 | 0 | 10 | 10 | 0
1148 | 2023-02-17 20:00 | 122.8381 | 65.03 | 10 | 0 | 0 | 10 | 1878.6813
1149 | 2023-02-17 21:00 | 122.9519 | 65.03 | 0 | 0 | 10 | 0 | 0
1150 | 2023-02-17 22:00 | 115.3176 | 65.03 | 10 | 0 | 0 | 0 | 1803.4756
1151 | 2023-02-17 23:00 | 117.2688 | 53.53 | 10 | 0 | 0 | 0 | 1707.9883
1152 | 2023-02-18 00:00 | 103.0291 | 53.53 | 10 | 0 | 0 | 0 | 1565.591
1153 | 2023-02-18 01:00 | 97.0228 | 53.53 | 10 | 0 | 0 | 0 | 1505.5275
1154 | 2023-02-18 02:00 | 86.7201 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1550.1323
1155 | 2023-02-18 03:00 | 81.7418 | 53.53 | 20 | 10 | 0 | 10.5 | 2705.4365
1156 | 2023-02-18 04:00 | -52.6744 | 53.53 | 20 | 10 | 0 | 20 | 17.1125
1157 | 2023-02-18 05:00 | 94.7893 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 74.1596
1158 | 2023-02-18 06:00 | 67.8828 | 53.53 | 20 | 10 | 0 | 20 | 2428.2561
1159 | 2023-02-18 07:00 | 92.2376 | 53.53 | 10 | 0 | 0 | 20 | 1457.6756
1160 | 2023-02-18 08:00 | 103.408 | 53.53 | 10 | 0 | 0 | 20 | 1569.38
1161 | 2023-02-18 09:00 | 108.3171 | 53.53 | 10 | 0 | 0 | 20 | 1618.4706
1162 | 2023-02-18 10:00 | 109.0599 | 53.53 | 10 | 0 | 0 | 20 | 1625.8985
1163 | 2023-02-18 11:00 | 101.804 | 53.53 | 10 | 0 | 0 | 20 | 1553.3402
1164 | 2023-02-18 12:00 | 104.5014 | 53.53 | 10 | 0 | 0 | 20 | 1580.3141
1165 | 2023-02-18 13:00 | 105.2083 | 53.53 | 10 | 0 | 0 | 20 | 1587.3831
1166 | 2023-02-18 14:00 | 138.1516 | 53.53 | 0 | 0 | 10 | 10 | 0
1167 | 2023-02-18 15:00 | 128.8209 | 53.53 | 0 | 0 | 10 | 0 | 0
1168 | 2023-02-18 16:00 | 107.9933 | 53.53 | 20 | 10 | 0 | 9.5 | 3230.466
1169 | 2023-02-18 17:00 | 123.3149 | 53.53 | 0.5 | 0 | 9.5 | 0 | 88.4224
1170 | 2023-02-18 18:00 | -13.5042 | 53.53 | 20 | 10 | 0 | 9.5 | 800.5163
1171 | 2023-02-18 19:00 | 115.002 | 53.53 | 0.5 | 0 | 9.5 | 0 | 84.266
1172 | 2023-02-18 20:00 | -10.721 | 53.53 | 20 | 10 | 0 | 9.5 | 856.1804
1173 | 2023-02-18 21:00 | 99.4307 | 53.53 | 10 | 0 | 0 | 9.5 | 1529.607
1174 | 2023-02-18 22:00 | 105.27 | 53.53 | 0.5 | 0 | 9.5 | 0 | 79.4
1175 | 2023-02-18 23:00 | 91.3669 | 53.53 | 10 | 0 | 0 | 0 | 1448.9694
1176 | 2023-02-19 00:00 | -61.7696 | 53.53 | 20 | 10 | 0 | 9.5 | -164.791
1177 | 2023-02-19 01:00 | -70.3499 | 53.53 | 20 | 10 | 0 | 19 | -336.398
1178 | 2023-02-19 02:00 | 83.8014 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 205.9971
1179 | 2023-02-19 03:00 | 84.2339 | 53.53 | 0 | 0 | 10 | 0.5 | 0
1180 | 2023-02-19 04:00 | 72.721 | 53.53 | 20 | 10 | 0 | 10 | 2525.0201
1181 | 2023-02-19 05:00 | 88.2052 | 53.53 | 0 | 0 | 10 | 0 | 0
1182 | 2023-02-19 06:00 | -77.6491 | 53.53 | 20 | 10 | 0 | 9.5 | -482.3827
1183 | 2023-02-19 07:00 | -39.0722 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 159.7965
1184 | 2023-02-19 08:00 | -49.8954 | 53.53 | 20 | 10 | 0 | 20 | 72.6927
1185 | 2023-02-19 09:00 | 102.4412 | 53.53 | 10 | 0 | 0 | 20 | 1559.7125
1186 | 2023-02-19 10:00 | 108.6358 | 53.53 | 10 | 0 | 0 | 20 | 1621.6583
1187 | 2023-02-19 11:00 | 113.7944 | 53.53 | 10 | 0 | 0 | 20 | 1673.2435
1188 | 2023-02-19 12:00 | 115.9454 | 53.53 | 10 | 0 | 0 | 20 | 1694.7538
1189 | 2023-02-19 13:00 | 109.8629 | 53.53 | 10 | 0 | 0 | 20 | 1633.9295
1190 | 2023-02-19 14:00 | 125.4817 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 89.5058
1191 | 2023-02-19 15:00 | 119.7209 | 53.53 | 10 | 0 | 0 | 10.5 | 1732.509
1192 | 2023-02-19 16:00 | 109.0456 | 53.53 | 20 | 10 | 0 | 20 | 3251.5128
1193 | 2023-02-19 17:00 | 132.2075 | 53.53 | 10 | 0 | 0 | 20 | 1857.3752
1194 | 2023-02-19 18:00 | 145.5554 | 53.53 | 0 | 0 | 10 | 10 | 0
1195 | 2023-02-19 19:00 | 145.9145 | 53.53 | 0 | 0 | 10 | 0 | 0
1196 | 2023-02-19 20:00 | 98.1943 | 53.53 | 20 | 10 | 0 | 9.5 | 3034.4863
1197 | 2023-02-19 21:00 | 99.8315 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1614.3314
1198 | 2023-02-19 22:00 | 119.9291 | 53.53 | 0 | 0 | 10 | 0 | 0
1199 | 2023-02-19 23:00 | 94.0978 | 53.53 | 20 | 10 | 0 | 9.5 | 2952.5552
1200 | 2023-02-20 00:00 | 100.7107 | 53.53 | 10 | 0 | 0 | 9.5 | 1542.4065
1201 | 2023-02-20 01:00 | 105.5053 | 53.53 | 0.5 | 0 | 9.5 | 0 | 79.5177
1202 | 2023-02-20 02:00 | 92.2573 | 53.53 | 10 | 0 | 0 | 0 | 1457.8729
1203 | 2023-02-20 03:00 | 88.142 | 53.53 | 10 | 0 | 0 | 0 | 1416.7201
1204 | 2023-02-20 04:00 | 84.4657 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1525.2156
1205 | 2023-02-20 05:00 | 84.3203 | 53.53 | 20 | 10 | 0 | 10.5 | 2757.0058
1206 | 2023-02-20 06:00 | 84.088 | 53.53 | 20 | 10 | 0 | 20 | 2752.361
1207 | 2023-02-20 07:00 | 103.1005 | 53.53 | 10 | 0 | 0 | 20 | 1566.3047
1208 | 2023-02-20 08:00 | 143.4673 | 65.03 | 0 | 0 | 10 | 10 | 0
1209 | 2023-02-20 09:00 | 121.2322 | 65.03 | 10 | 0 | 0 | 10 | 1862.6225
1210 | 2023-02-20 10:00 | 126.5176 | 65.03 | 0 | 0 | 10 | 0 | 0
1211 | 2023-02-20 11:00 | 115.4866 | 65.03 | 10 | 0 | 0 | 0 | 1805.1663
1212 | 2023-02-20 12:00 | 117.5418 | 65.03 | 10 | 0 | 0 | 0 | 1825.7182
1213 | 2023-02-20 13:00 | 114.0807 | 65.03 | 10 | 0 | 0 | 0 | 1791.1068
1214 | 2023-02-20 14:00 | 105.1821 | 65.03 | 20 | 10 | 0 | 9.5 | 3404.241
1215 | 2023-02-20 15:00 | 110.4332 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1939.3301
1216 | 2023-02-20 16:00 | 108.4207 | 65.03 | 20 | 10 | 0 | 20 | 3469.0135
1217 | 2023-02-20 17:00 | 121.628 | 66.4 | 10 | 0 | 0 | 20 | 1880.2804
1218 | 2023-02-20 18:00 | 126.3645 | 66.4 | 0 | 0 | 10 | 10 | 0
1219 | 2023-02-20 19:00 | 146.1003 | 65.03 | 0 | 0 | 10 | 0 | 0
1220 | 2023-02-20 20:00 | 113.5672 | 65.03 | 20 | 10 | 0 | 9.5 | 3571.9449
1221 | 2023-02-20 21:00 | 125.7184 | 65.03 | 0.5 | 0 | 9.5 | 0 | 95.3742
1222 | 2023-02-20 22:00 | 117.1788 | 65.03 | 10 | 0 | 0 | 0 | 1822.0875
1223 | 2023-02-20 23:00 | 115.5137 | 53.53 | 10 | 0 | 0 | 0 | 1690.4368
1224 | 2023-02-21 00:00 | -32.8437 | 53.53 | 20 | 10 | 0 | 9.5 | 413.7267
1225 | 2023-02-21 01:00 | -69.9332 | 53.53 | 20 | 10 | 0 | 19 | -328.0646
1226 | 2023-02-21 02:00 | 95.0071 | 53.53 | 0 | 0 | 10 | 9 | 0
1227 | 2023-02-21 03:00 | 84.9269 | 53.53 | 20 | 10 | 0 | 18.5 | 2769.1374
1228 | 2023-02-21 04:00 | 93.4676 | 53.53 | 10 | 0 | 0 | 18.5 | 1469.9764
1229 | 2023-02-21 05:00 | 93.5267 | 53.53 | 2 | 0 | 8 | 10.5 | 294.1133
1230 | 2023-02-21 06:00 | 85.0985 | 53.53 | 20 | 10 | 0 | 20 | 2772.5699
1231 | 2023-02-21 07:00 | 101.7491 | 53.53 | 10 | 0 | 0 | 20 | 1552.7905
1232 | 2023-02-21 08:00 | 111.4235 | 65.03 | 10 | 0 | 0 | 20 | 1764.5346
1233 | 2023-02-21 09:00 | 119.5556 | 65.03 | 10 | 0 | 0 | 20 | 1845.8559
1234 | 2023-02-21 10:00 | 121.4752 | 65.03 | 10 | 0 | 0 | 20 | 1865.0521
1235 | 2023-02-21 11:00 | 113.6081 | 65.03 | 10 | 0 | 0 | 20 | 1786.3815
1236 | 2023-02-21 12:00 | 119.0985 | 65.03 | 10 | 0 | 0 | 20 | 1841.2849
1237 | 2023-02-21 13:00 | 123.5654 | 65.03 | 10 | 0 | 0 | 20 | 1885.9535
1238 | 2023-02-21 14:00 | 123.9925 | 65.03 | 1 | 0 | 9 | 11 | 189.0225
1239 | 2023-02-21 15:00 | 133.7211 | 65.03 | 0 | 0 | 10 | 1 | 0
1240 | 2023-02-21 16:00 | -41.881 | 65.03 | 20 | 10 | 0 | 10.5 | 462.9802
1241 | 2023-02-21 17:00 | 127.4116 | 66.4 | 0 | 0 | 10 | 0.5 | 0
1242 | 2023-02-21 18:00 | -10.0206 | 66.4 | 20 | 10 | 0 | 10 | 1127.5871
1243 | 2023-02-21 19:00 | 130.217 | 65.03 | 0 | 0 | 10 | 0 | 0
1244 | 2023-02-21 20:00 | -58.0256 | 65.03 | 20 | 10 | 0 | 9.5 | 140.0884
1245 | 2023-02-21 21:00 | 114.4134 | 65.03 | 0.5 | 0 | 9.5 | 0 | 89.7217
1246 | 2023-02-21 22:00 | 110.9906 | 65.03 | 10 | 0 | 0 | 0 | 1760.2065
1247 | 2023-02-21 23:00 | -48.2651 | 53.53 | 20 | 10 | 0 | 9.5 | 105.2985
1248 | 2023-02-22 00:00 | 107.6441 | 53.53 | 0.5 | 0 | 9.5 | 0 | 80.5871
1249 | 2023-02-22 01:00 | -32.4823 | 53.53 | 20 | 10 | 0 | 9.5 | 420.9535
1250 | 2023-02-22 02:00 | 97.3153 | 53.53 | 10 | 0 | 0 | 9.5 | 1508.4533
1251 | 2023-02-22 03:00 | 103.3041 | 53.53 | 0.5 | 0 | 9.5 | 0 | 78.4171
1252 | 2023-02-22 04:00 | 83.5822 | 53.53 | 20 | 10 | 0 | 9.5 | 2742.2447
1253 | 2023-02-22 05:00 | 91.2688 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1600.4082
1254 | 2023-02-22 06:00 | 84.0091 | 53.53 | 20 | 10 | 0 | 20 | 2750.7827
1255 | 2023-02-22 07:00 | 104.6024 | 53.53 | 10 | 0 | 0 | 20 | 1581.3238
1256 | 2023-02-22 08:00 | 125.4373 | 65.03 | 10 | 0 | 0 | 20 | 1904.6729
1257 | 2023-02-22 09:00 | 118.6109 | 65.03 | 10 | 0 | 0 | 20 | 1836.4093
1258 | 2023-02-22 10:00 | 136.0287 | 65.03 | 0 | 0 | 10 | 10 | 0
1259 | 2023-02-22 11:00 | 115.531 | 65.03 | 20 | 10 | 0 | 19.5 | 3611.2201
1260 | 2023-02-22 12:00 | 127.6381 | 65.03 | 1 | 0 | 9 | 10.5 | 192.6681
1261 | 2023-02-22 13:00 | 119.6397 | 65.03 | 10 | 0 | 0 | 10.5 | 1846.6969
1262 | 2023-02-22 14:00 | 125.6393 | 65.03 | 10 | 0 | 0 | 10.5 | 1906.6931
1263 | 2023-02-22 15:00 | 115.7598 | 65.03 | 20 | 10 | 0 | 20 | 3615.7967
1264 | 2023-02-22 16:00 | 118.5294 | 65.03 | 10 | 0 | 0 | 20 | 1835.5936
1265 | 2023-02-22 17:00 | 133.0469 | 66.4 | 0 | 0 | 10 | 10 | 0
1266 | 2023-02-22 18:00 | 128.3524 | 66.4 | 10 | 0 | 0 | 10 | 1947.5242
1267 | 2023-02-22 19:00 | 139.3914 | 65.03 | 0 | 0 | 10 | 0 | 0
1268 | 2023-02-22 20:00 | 119.2834 | 65.03 | 10 | 0 | 0 | 0 | 1843.1335
1269 | 2023-02-22 21:00 | 118.7709 | 65.03 | 20 | 10 | 0 | 9.5 | 3676.0185
1270 | 2023-02-22 22:00 | 128.5433 | 65.03 | 0.5 | 0 | 9.5 | 0 | 96.7867
1271 | 2023-02-22 23:00 | -69.8307 | 53.53 | 20 | 10 | 0 | 9.5 | -326.0146
1272 | 2023-02-23 00:00 | 106.2386 | 53.53 | 10 | 0 | 0 | 9.5 | 1597.6861
1273 | 2023-02-23 01:00 | 111.8588 | 53.53 | 0.5 | 0 | 9.5 | 0 | 82.6944
1274 | 2023-02-23 02:00 | 84.6327 | 53.53 | 20 | 10 | 0 | 9.5 | 2763.2547
1275 | 2023-02-23 03:00 | 89.0741 | 53.53 | 10 | 0 | 0 | 9.5 | 1426.0409
1276 | 2023-02-23 04:00 | 84.7816 | 53.53 | 11.5789 | 1.5789 | 0 | 11 | 1601.5031
1277 | 2023-02-23 05:00 | 104.5442 | 53.53 | 0 | 0 | 10 | 1 | 0
1278 | 2023-02-23 06:00 | -55.2691 | 53.53 | 20 | 10 | 0 | 10.5 | -34.7817
1279 | 2023-02-23 07:00 | -77.6561 | 53.53 | 20 | 10 | 0 | 20 | -482.5228
1280 | 2023-02-23 08:00 | 129.663 | 65.03 | 0 | 0 | 10 | 10 | 0
1281 | 2023-02-23 09:00 | 106.934 | 65.03 | 20 | 10 | 0 | 19.5 | 3439.28
1282 | 2023-02-23 10:00 | 107.5607 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1816.7439
1283 | 2023-02-23 11:00 | 125.6399 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 95.3349
1284 | 2023-02-23 12:00 | 119.356 | 65.03 | 10 | 0 | 0 | 10.5 | 1843.8596
1285 | 2023-02-23 13:00 | 120.849 | 65.03 | 10 | 0 | 0 | 10.5 | 1858.7902
1286 | 2023-02-23 14:00 | 110.6912 | 65.03 | 20 | 10 | 0 | 20 | 3514.4244
1287 | 2023-02-23 15:00 | 118.7247 | 65.03 | 10 | 0 | 0 | 20 | 1837.5466
1288 | 2023-02-23 16:00 | 139.4993 | 65.03 | 0 | 0 | 10 | 10 | 0
1289 | 2023-02-23 17:00 | 140.9111 | 66.4 | 0 | 0 | 10 | 0 | 0
1290 | 2023-02-23 18:00 | 135.2041 | 66.4 | 10 | 0 | 0 | 0 | 2016.0406
1291 | 2023-02-23 19:00 | 130.8131 | 65.03 | 10 | 0 | 0 | 0 | 1958.4305
1292 | 2023-02-23 20:00 | 111.1074 | 65.03 | 10 | 0 | 0 | 0 | 1761.3745
1293 | 2023-02-23 21:00 | 102.097 | 65.03 | 20 | 10 | 0 | 9.5 | 3342.5396
1294 | 2023-02-23 22:00 | 115.9072 | 65.03 | 0.5 | 0 | 9.5 | 0 | 90.4686
1295 | 2023-02-23 23:00 | 116.1162 | 53.53 | 10 | 0 | 0 | 0 | 1696.4616
1296 | 2023-02-24 00:00 | 99.4815 | 53.53 | 10 | 0 | 0 | 0 | 1530.1145
1297 | 2023-02-24 01:00 | 104.3988 | 53.53 | 10 | 0 | 0 | 0 | 1579.2884
1298 | 2023-02-24 02:00 | 81.5642 | 53.53 | 20 | 10 | 0 | 9.5 | 2701.8842
1299 | 2023-02-24 03:00 | 82.6123 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1504.7305
1300 | 2023-02-24 04:00 | 89.3027 | 53.53 | 10 | 0 | 0 | 10.5 | 1428.3265
1301 | 2023-02-24 05:00 | 77.2756 | 53.53 | 20 | 10 | 0 | 20 | 2616.111
1302 | 2023-02-24 06:00 | 93.9572 | 53.53 | 10 | 0 | 0 | 20 | 1474.8715
1303 | 2023-02-24 07:00 | 115.2426 | 53.53 | 10 | 0 | 0 | 20 | 1687.726
1304 | 2023-02-24 08:00 | 117.0842 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 91.0571
1305 | 2023-02-24 09:00 | 105.776 | 65.03 | 20 | 10 | 0 | 20 | 3416.1203
1306 | 2023-02-24 10:00 | 112.4387 | 65.03 | 10 | 0 | 0 | 20 | 1774.6867
1307 | 2023-02-24 11:00 | 130.087 | 65.03 | 0 | 0 | 10 | 10 | 0
1308 | 2023-02-24 12:00 | 104.7626 | 65.03 | 20 | 10 | 0 | 19.5 | 3395.8511
1309 | 2023-02-24 13:00 | 116.4231 | 65.03 | 10 | 0 | 0 | 19.5 | 1814.5315
1310 | 2023-02-24 14:00 | 111.4452 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1857.6334
1311 | 2023-02-24 15:00 | 125.7231 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 95.3766
1312 | 2023-02-24 16:00 | 114.3148 | 65.03 | 20 | 10 | 0 | 20 | 3586.8954
1313 | 2023-02-24 17:00 | 137.1192 | 66.4 | 10 | 0 | 0 | 20 | 2035.1918
1314 | 2023-02-24 18:00 | 138.5202 | 66.4 | 0 | 0 | 10 | 10 | 0
1315 | 2023-02-24 19:00 | 152.2672 | 65.03 | 0 | 0 | 10 | 0 | 0
1316 | 2023-02-24 20:00 | 112.4216 | 65.03 | 10 | 0 | 0 | 0 | 1774.5165
1317 | 2023-02-24 21:00 | 116.8839 | 65.03 | 10 | 0 | 0 | 0 | 1819.1388
1318 | 2023-02-24 22:00 | 104.9106 | 65.03 | 10 | 0 | 0 | 0 | 1699.4064
1319 | 2023-02-24 23:00 | 119.6286 | 53.53 | 10 | 0 | 0 | 0 | 1731.5864
1320 | 2023-02-25 00:00 | 95.7984 | 53.53 | 10 | 0 | 0 | 0 | 1493.2837
1321 | 2023-02-25 01:00 | 97.0274 | 53.53 | 10 | 0 | 0 | 0 | 1505.5737
1322 | 2023-02-25 02:00 | 80.732 | 53.53 | 20 | 10 | 0 | 9.5 | 2685.2401
1323 | 2023-02-25 03:00 | 71.5411 | 53.53 | 20 | 10 | 0 | 19 | 2501.422
1324 | 2023-02-25 04:00 | 82.6743 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1505.4163
1325 | 2023-02-25 05:00 | 89.317 | 53.53 | 10 | 0 | 0 | 20 | 1428.4701
1326 | 2023-02-25 06:00 | 83.1947 | 53.53 | 10 | 0 | 0 | 20 | 1367.2474
1327 | 2023-02-25 07:00 | 91.4195 | 53.53 | 10 | 0 | 0 | 20 | 1449.495
1328 | 2023-02-25 08:00 | 109.9868 | 53.53 | 10 | 0 | 0 | 20 | 1635.1677
1329 | 2023-02-25 09:00 | 117.1316 | 53.53 | 0 | 0 | 10 | 10 | 0
1330 | 2023-02-25 10:00 | 100.1301 | 53.53 | 20 | 10 | 0 | 19.5 | 3073.2022
1331 | 2023-02-25 11:00 | 104.008 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1658.2945
1332 | 2023-02-25 12:00 | 118.4178 | 53.53 | 10 | 0 | 0 | 20 | 1719.4777
1333 | 2023-02-25 13:00 | 113.0084 | 53.53 | 10 | 0 | 0 | 20 | 1665.3835
1334 | 2023-02-25 14:00 | 114.1871 | 53.53 | 10 | 0 | 0 | 20 | 1677.1714
1335 | 2023-02-25 15:00 | 129.5711 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 91.5505
1336 | 2023-02-25 16:00 | 114.6714 | 53.53 | 20 | 10 | 0 | 20 | 3364.0285
1337 | 2023-02-25 17:00 | 131.3531 | 53.53 | 0 | 0 | 10 | 10 | 0
1338 | 2023-02-25 18:00 | 157.2775 | 53.53 | 0 | 0 | 10 | 0 | 0
1339 | 2023-02-25 19:00 | 124.3451 | 53.53 | 10 | 0 | 0 | 0 | 1778.7512
1340 | 2023-02-25 20:00 | 100.5765 | 53.53 | 20 | 10 | 0 | 9.5 | 3082.13
1341 | 2023-02-25 21:00 | 109.3218 | 53.53 | 10 | 0 | 0 | 9.5 | 1628.5176
1342 | 2023-02-25 22:00 | 109.4174 | 53.53 | 0.5 | 0 | 9.5 | 0 | 81.4737
1343 | 2023-02-25 23:00 | 97.2442 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1587.0972
1344 | 2023-02-26 00:00 | 94.2396 | 53.53 | 20 | 10 | 0 | 10 | 2955.3926
1345 | 2023-02-26 01:00 | 125.8886 | 53.53 | 0 | 0 | 10 | 0 | 0
1346 | 2023-02-26 02:00 | 83.4738 | 53.53 | 10 | 0 | 0 | 0 | 1370.0384
1347 | 2023-02-26 03:00 | 75.9676 | 53.53 | 20 | 10 | 0 | 9.5 | 2589.9517
1348 | 2023-02-26 04:00 | 88.8043 | 53.53 | 1.5 | 0 | 8.5 | 1 | 213.5015
1349 | 2023-02-26 05:00 | 80.093 | 53.53 | 20 | 10 | 0 | 10.5 | 2672.4595
1350 | 2023-02-26 06:00 | 79.0719 | 53.53 | 20 | 10 | 0 | 20 | 2652.0371
1351 | 2023-02-26 07:00 | 105.4919 | 53.53 | 10 | 0 | 0 | 20 | 1590.2189
1352 | 2023-02-26 08:00 | 102.866 | 53.53 | 10 | 0 | 0 | 20 | 1563.96
1353 | 2023-02-26 09:00 | 113.688 | 53.53 | 1 | 0 | 9 | 11 | 167.218
1354 | 2023-02-26 10:00 | 130.2771 | 53.53 | 0 | 0 | 10 | 1 | 0
1355 | 2023-02-26 11:00 | -50.5091 | 53.53 | 20 | 10 | 0 | 10.5 | 60.4177
1356 | 2023-02-26 12:00 | -7.5508 | 53.53 | 20 | 10 | 0 | 20 | 919.5843
1357 | 2023-02-26 13:00 | 107.3702 | 53.53 | 10 | 0 | 0 | 20 | 1609.0019
1358 | 2023-02-26 14:00 | 108.0026 | 53.53 | 10 | 0 | 0 | 20 | 1615.3264
1359 | 2023-02-26 15:00 | 109.0643 | 53.53 | 10 | 0 | 0 | 20 | 1625.9434
1360 | 2023-02-26 16:00 | 108.2194 | 53.53 | 10 | 0 | 0 | 20 | 1617.4944
1361 | 2023-02-26 17:00 | 133.8081 | 53.53 | 0 | 0 | 10 | 10 | 0
1362 | 2023-02-26 18:00 | 115.7619 | 53.53 | 0 | 0 | 10 | 0 | 0
1363 | 2023-02-26 19:00 | -36.2651 | 53.53 | 20 | 10 | 0 | 9.5 | 345.2977
1364 | 2023-02-26 20:00 | 103.2069 | 53.53 | 10 | 0 | 0 | 9.5 | 1567.3685
1365 | 2023-02-26 21:00 | -11.8178 | 53.53 | 20 | 10 | 0 | 19 | 834.2434
1366 | 2023-02-26 22:00 | 98.7265 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1682.8347
1367 | 2023-02-26 23:00 | 113.1413 | 53.53 | 10 | 0 | 0 | 20 | 1666.7135
1368 | 2023-02-27 00:00 | 120.2255 | 53.53 | 0 | 0 | 10 | 10 | 0
1369 | 2023-02-27 01:00 | 117.2381 | 53.53 | 0 | 0 | 10 | 0 | 0
1370 | 2023-02-27 02:00 | 79.7686 | 53.53 | 20 | 10 | 0 | 9.5 | 2665.9721
1371 | 2023-02-27 03:00 | 95.9584 | 53.53 | 1.5 | 0 | 8.5 | 1 | 224.2326
1372 | 2023-02-27 04:00 | -59.4125 | 53.53 | 20 | 10 | 0 | 10.5 | -117.6493
1373 | 2023-02-27 05:00 | -73.6549 | 53.53 | 20 | 10 | 0 | 20 | -402.4978
1374 | 2023-02-27 06:00 | 88.7167 | 53.53 | 10 | 0 | 0 | 20 | 1422.4674
1375 | 2023-02-27 07:00 | 111.7874 | 53.53 | 10 | 0 | 0 | 20 | 1653.1741
1376 | 2023-02-27 08:00 | 123.4369 | 65.03 | 10 | 0 | 0 | 20 | 1884.6692
1377 | 2023-02-27 09:00 | 120.2638 | 65.03 | 10 | 0 | 0 | 20 | 1852.9375
1378 | 2023-02-27 10:00 | 121.1808 | 65.03 | 10 | 0 | 0 | 20 | 1862.108
1379 | 2023-02-27 11:00 | 132.7969 | 65.03 | 0 | 0 | 10 | 10 | 0
1380 | 2023-02-27 12:00 | 130.0125 | 65.03 | 0 | 0 | 10 | 0 | 0
1381 | 2023-02-27 13:00 | 104.4761 | 65.03 | 20 | 10 | 0 | 9.5 | 3390.1225
1382 | 2023-02-27 14:00 | 116.6274 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 2007.7919
1383 | 2023-02-27 15:00 | 117.6934 | 65.03 | 10 | 0 | 0 | 10.5 | 1827.2343
1384 | 2023-02-27 16:00 | 108.6779 | 65.03 | 20 | 10 | 0 | 20 | 3474.1576
1385 | 2023-02-27 17:00 | 134.6148 | 66.4 | 0 | 0 | 10 | 10 | 0
1386 | 2023-02-27 18:00 | 145.2595 | 66.4 | 0 | 0 | 10 | 0 | 0
1387 | 2023-02-27 19:00 | 126.944 | 65.03 | 10 | 0 | 0 | 0 | 1919.7397
1388 | 2023-02-27 20:00 | 116.553 | 65.03 | 10 | 0 | 0 | 0 | 1815.8302
1389 | 2023-02-27 21:00 | 107.8924 | 65.03 | 10 | 0 | 0 | 0 | 1729.2241
1390 | 2023-02-27 22:00 | 109.3344 | 65.03 | 10 | 0 | 0 | 0 | 1743.6439
1391 | 2023-02-27 23:00 | 122.8411 | 53.53 | 10 | 0 | 0 | 0 | 1763.7111
1392 | 2023-02-28 00:00 | 105.143 | 53.53 | 10 | 0 | 0 | 0 | 1586.7303
1393 | 2023-02-28 01:00 | 112.6168 | 53.53 | 10 | 0 | 0 | 0 | 1661.4675
1394 | 2023-02-28 02:00 | 78.159 | 53.53 | 20 | 10 | 0 | 9.5 | 2633.7809
1395 | 2023-02-28 03:00 | 107.6081 | 53.53 | 0.5 | 0 | 9.5 | 0 | 80.569
1396 | 2023-02-28 04:00 | 93.8526 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1628.9652
1397 | 2023-02-28 05:00 | 87.5664 | 53.53 | 20 | 10 | 0 | 10.5 | 2821.927
1398 | 2023-02-28 06:00 | 93.61 | 53.53 | 20 | 10 | 0 | 20 | 2942.7994
1399 | 2023-02-28 07:00 | 100.2762 | 53.53 | 10 | 0 | 0 | 20 | 1538.0616
1400 | 2023-02-28 08:00 | 129.5442 | 65.03 | 0 | 0 | 10 | 10 | 0
1401 | 2023-02-28 09:00 | 116.5828 | 65.03 | 10 | 0 | 0 | 10 | 1816.1277
1402 | 2023-02-28 10:00 | 117.4137 | 65.03 | 10 | 0 | 0 | 10 | 1824.4369
1403 | 2023-02-28 11:00 | 115.4699 | 65.03 | 10 | 0 | 0 | 10 | 1804.9994
1404 | 2023-02-28 12:00 | 114.9016 | 65.03 | 20 | 10 | 0 | 19.5 | 3598.6325
1405 | 2023-02-28 13:00 | 124.691 | 65.03 | 1 | 0 | 9 | 10.5 | 189.721
1406 | 2023-02-28 14:00 | 120.8932 | 65.03 | 10 | 0 | 0 | 10.5 | 1859.232
1407 | 2023-02-28 15:00 | 124.297 | 65.03 | 10 | 0 | 0 | 10.5 | 1893.2702
1408 | 2023-02-28 16:00 | 118.8324 | 65.03 | 10 | 0 | 0 | 10.5 | 1838.6243
1409 | 2023-02-28 17:00 | -38.7265 | 66.4 | 20 | 10 | 0 | 20 | 553.47
1410 | 2023-02-28 18:00 | 130.9463 | 66.4 | 0 | 0 | 10 | 10 | 0
1411 | 2023-02-28 19:00 | 157.7015 | 65.03 | 0 | 0 | 10 | 0 | 0
1412 | 2023-02-28 20:00 | 104.5174 | 65.03 | 20 | 10 | 0 | 9.5 | 3390.9488
1413 | 2023-02-28 21:00 | 125.3926 | 65.03 | 10 | 0 | 0 | 9.5 | 1904.2264
1414 | 2023-02-28 22:00 | 126.5828 | 65.03 | 0.5 | 0 | 9.5 | 0 | 95.8064
1415 | 2023-02-28 23:00 | 103.2587 | 53.53 | 20 | 10 | 0 | 9.5 | 3135.7735
1416 | 2023-03-01 00:00 | 122.6948 | 53.53 | 0.5 | 0 | 9.5 | 0 | 88.1124
1417 | 2023-03-01 01:00 | 107.5992 | 53.53 | 10 | 0 | 0 | 0 | 1611.2915
1418 | 2023-03-01 02:00 | 87.3539 | 53.53 | 10 | 0 | 0 | 0 | 1408.8385
1419 | 2023-03-01 03:00 | 79.1094 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1466.014
1420 | 2023-03-01 04:00 | 77.3211 | 53.53 | 20 | 10 | 0 | 10.5 | 2617.0212
1421 | 2023-03-01 05:00 | 77.3761 | 53.53 | 20 | 10 | 0 | 20 | 2618.1211
1422 | 2023-03-01 06:00 | 82.0058 | 53.53 | 10 | 0 | 0 | 20 | 1355.3577
1423 | 2023-03-01 07:00 | 111.9609 | 53.53 | 10 | 0 | 0 | 20 | 1654.9089
1424 | 2023-03-01 08:00 | 110.2958 | 65.03 | 10 | 0 | 0 | 20 | 1753.2583
1425 | 2023-03-01 09:00 | 102.9174 | 65.03 | 10 | 0 | 0 | 20 | 1679.4739
1426 | 2023-03-01 10:00 | 115.9133 | 65.03 | 1 | 0 | 9 | 11 | 180.9433
1427 | 2023-03-01 11:00 | 116.8559 | 65.03 | 0 | 0 | 10 | 1 | 0
1428 | 2023-03-01 12:00 | 114.3236 | 65.03 | 10 | 0 | 0 | 1 | 1793.5358
1429 | 2023-03-01 13:00 | 115.1641 | 65.03 | 10 | 0 | 0 | 1 | 1801.9413
1430 | 2023-03-01 14:00 | 106.9467 | 65.03 | 10 | 0 | 0 | 1 | 1719.7673
1431 | 2023-03-01 15:00 | 102.8175 | 65.03 | 20 | 10 | 0 | 10.5 | 3356.9508
1432 | 2023-03-01 16:00 | 103.1658 | 65.03 | 20 | 10 | 0 | 20 | 3363.9154
1433 | 2023-03-01 17:00 | 114.2042 | 66.4 | 10 | 0 | 0 | 20 | 1806.0418
1434 | 2023-03-01 18:00 | 125.7401 | 66.4 | 0 | 0 | 10 | 10 | 0
1435 | 2023-03-01 19:00 | 123.2802 | 65.03 | 0 | 0 | 10 | 0 | 0
1436 | 2023-03-01 20:00 | 100.8069 | 65.03 | 10 | 0 | 0 | 0 | 1658.3691
1437 | 2023-03-01 21:00 | 89.1988 | 65.03 | 20 | 10 | 0 | 9.5 | 3084.5757
1438 | 2023-03-01 22:00 | 96.0944 | 65.03 | 10 | 0 | 0 | 9.5 | 1611.2437
1439 | 2023-03-01 23:00 | 108.8906 | 53.53 | 0.5 | 0 | 9.5 | 0 | 81.2103
1440 | 2023-03-02 00:00 | 94.3791 | 53.53 | 10 | 0 | 0 | 0 | 1479.0911
1441 | 2023-03-02 01:00 | -11.8966 | 53.53 | 20 | 10 | 0 | 9.5 | 832.6688
1442 | 2023-03-02 02:00 | -14.8735 | 53.53 | 20 | 10 | 0 | 19 | 773.1303
1443 | 2023-03-02 03:00 | 92.3917 | 53.53 | 0 | 0 | 10 | 9 | 0
1444 | 2023-03-02 04:00 | 77.8411 | 53.53 | 20 | 10 | 0 | 18.5 | 2627.4221
1445 | 2023-03-02 05:00 | 81.1711 | 53.53 | 11.5789 | 1.5789 | 0 | 20 | 1559.6964
1446 | 2023-03-02 06:00 | 104.1282 | 53.53 | 1 | 0 | 9 | 11 | 157.6582
1447 | 2023-03-02 07:00 | 113.3 | 53.53 | 0 | 0 | 10 | 1 | 0
1448 | 2023-03-02 08:00 | -48.2202 | 65.03 | 20 | 10 | 0 | 10.5 | 336.1955
1449 | 2023-03-02 09:00 | -55.3572 | 65.03 | 20 | 10 | 0 | 20 | 193.4568
1450 | 2023-03-02 10:00 | 106.5722 | 65.03 | 10 | 0 | 0 | 20 | 1716.0216
1451 | 2023-03-02 11:00 | 113.0305 | 65.03 | 10 | 0 | 0 | 20 | 1780.6054
1452 | 2023-03-02 12:00 | 108.1215 | 65.03 | 10 | 0 | 0 | 20 | 1731.5145
1453 | 2023-03-02 13:00 | 106.103 | 65.03 | 10 | 0 | 0 | 20 | 1711.3298
1454 | 2023-03-02 14:00 | 122.722 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 93.876
1455 | 2023-03-02 15:00 | 108.0562 | 65.03 | 20 | 10 | 0 | 20 | 3461.7248
1456 | 2023-03-02 16:00 | 133.7351 | 65.03 | 0 | 0 | 10 | 10 | 0
1457 | 2023-03-02 17:00 | 124.5882 | 66.4 | 10 | 0 | 0 | 10 | 1909.8822
1458 | 2023-03-02 18:00 | 141.6099 | 66.4 | 0 | 0 | 10 | 0 | 0
1459 | 2023-03-02 19:00 | 126.7271 | 65.03 | 10 | 0 | 0 | 0 | 1917.5711
1460 | 2023-03-02 20:00 | -31.1323 | 65.03 | 20 | 10 | 0 | 9.5 | 677.9542
1461 | 2023-03-02 21:00 | 99.0138 | 65.03 | 0.5 | 0 | 9.5 | 0 | 82.0219
1462 | 2023-03-02 22:00 | 98.2494 | 65.03 | 10 | 0 | 0 | 0 | 1632.7938
1463 | 2023-03-02 23:00 | 102.5952 | 53.53 | 10 | 0 | 0 | 0 | 1561.2516
1464 | 2023-03-03 00:00 | 107.5291 | 53.53 | 10 | 0 | 0 | 0 | 1610.5909
1465 | 2023-03-03 01:00 | 99.2021 | 53.53 | 10 | 0 | 0 | 0 | 1527.3206
1466 | 2023-03-03 02:00 | 70.894 | 53.53 | 10 | 0 | 0 | 0 | 1244.2396
1467 | 2023-03-03 03:00 | 70.5215 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1371.0954
1468 | 2023-03-03 04:00 | 70.1913 | 53.53 | 20 | 10 | 0 | 10.5 | 2474.4259
1469 | 2023-03-03 05:00 | 68.6092 | 53.53 | 20 | 10 | 0 | 20 | 2442.7843
1470 | 2023-03-03 06:00 | 79.7331 | 53.53 | 10 | 0 | 0 | 20 | 1332.6308
1471 | 2023-03-03 07:00 | 108.9348 | 53.53 | 10 | 0 | 0 | 20 | 1624.6476
1472 | 2023-03-03 08:00 | 108.7979 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 86.9139
1473 | 2023-03-03 09:00 | 96.5875 | 65.03 | 20 | 10 | 0 | 20 | 3232.3502
1474 | 2023-03-03 10:00 | 107.5078 | 65.03 | 10 | 0 | 0 | 20 | 1725.3777
1475 | 2023-03-03 11:00 | 107.7067 | 65.03 | 10 | 0 | 0 | 20 | 1727.3665
1476 | 2023-03-03 12:00 | 130.7823 | 65.03 | 0 | 0 | 10 | 10 | 0
1477 | 2023-03-03 13:00 | 100.0453 | 65.03 | 20 | 10 | 0 | 19.5 | 3301.5062
1478 | 2023-03-03 14:00 | 106.1334 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1801.7202
1479 | 2023-03-03 15:00 | 125.6037 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 95.3169
1480 | 2023-03-03 16:00 | 112.5115 | 65.03 | 20 | 10 | 0 | 20 | 3550.8308
1481 | 2023-03-03 17:00 | 128.5011 | 66.4 | 0 | 0 | 10 | 10 | 0
1482 | 2023-03-03 18:00 | 124.7726 | 66.4 | 10 | 0 | 0 | 10 | 1911.7263
1483 | 2023-03-03 19:00 | 126.4995 | 65.03 | 0 | 0 | 10 | 0 | 0
1484 | 2023-03-03 20:00 | 110.4668 | 65.03 | 10 | 0 | 0 | 0 | 1754.9677
1485 | 2023-03-03 21:00 | 98.5081 | 65.03 | 20 | 10 | 0 | 9.5 | 3270.7623
1486 | 2023-03-03 22:00 | 111.4326 | 65.03 | 0.5 | 0 | 9.5 | 0 | 88.2313
1487 | 2023-03-03 23:00 | 90.4581 | 53.53 | 10 | 0 | 0 | 0 | 1439.8805
1488 | 2023-03-04 00:00 | 93.4865 | 53.53 | 10 | 0 | 0 | 0 | 1470.1645
1489 | 2023-03-04 01:00 | 92.2755 | 53.53 | 10 | 0 | 0 | 0 | 1458.0546
1490 | 2023-03-04 02:00 | 66.6782 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1328.6174
1491 | 2023-03-04 03:00 | 70.7287 | 53.53 | 10 | 0 | 0 | 1 | 1242.5874
1492 | 2023-03-04 04:00 | -62.8326 | 53.53 | 20 | 10 | 0 | 10.5 | -186.0521
1493 | 2023-03-04 05:00 | 64.0246 | 53.53 | 20 | 10 | 0 | 20 | 2351.0927
1494 | 2023-03-04 06:00 | 68.382 | 53.53 | 10 | 0 | 0 | 20 | 1219.1202
1495 | 2023-03-04 07:00 | 83.8499 | 53.53 | 10 | 0 | 0 | 20 | 1373.7991
1496 | 2023-03-04 08:00 | 103.4404 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 78.4852
1497 | 2023-03-04 09:00 | 93.6034 | 53.53 | 20 | 10 | 0 | 20 | 2942.6672
1498 | 2023-03-04 10:00 | 106.8513 | 53.53 | 0 | 0 | 10 | 10 | 0
1499 | 2023-03-04 11:00 | 93.4374 | 53.53 | 20 | 10 | 0 | 19.5 | 2939.3479
1500 | 2023-03-04 12:00 | 96.9923 | 53.53 | 10 | 0 | 0 | 19.5 | 1505.2228
1501 | 2023-03-04 13:00 | 96.6265 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1580.5947
1502 | 2023-03-04 14:00 | 113.1024 | 53.53 | 0 | 0 | 10 | 10 | 0
1503 | 2023-03-04 15:00 | 103.5024 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1652.9723
1504 | 2023-03-04 16:00 | 99.3597 | 53.53 | 20 | 10 | 0 | 20 | 3057.7937
1505 | 2023-03-04 17:00 | 119.933 | 53.53 | 0 | 0 | 10 | 10 | 0
1506 | 2023-03-04 18:00 | 104.1844 | 53.53 | 20 | 10 | 0 | 19.5 | 3154.2881
1507 | 2023-03-04 19:00 | 115.5769 | 53.53 | 0.5 | 0 | 9.5 | 10 | 84.5534
1508 | 2023-03-04 20:00 | 116.4173 | 53.53 | 0 | 0 | 10 | 0 | 0
1509 | 2023-03-04 21:00 | 96.9109 | 53.53 | 10 | 0 | 0 | 0 | 1504.4087
1510 | 2023-03-04 22:00 | 96.4129 | 53.53 | 10 | 0 | 0 | 0 | 1499.4288
1511 | 2023-03-04 23:00 | 95.3666 | 53.53 | 10 | 0 | 0 | 0 | 1488.9658
1512 | 2023-03-05 00:00 | 98.6043 | 53.53 | 10 | 0 | 0 | 0 | 1521.3427
1513 | 2023-03-05 01:00 | 79.629 | 53.53 | 10 | 0 | 0 | 0 | 1331.5903
1514 | 2023-03-05 02:00 | 60.9905 | 53.53 | 20 | 10 | 0 | 9.5 | 2290.4101
1515 | 2023-03-05 03:00 | 72.5263 | 53.53 | 0.5 | 0 | 9.5 | 0 | 63.0282
1516 | 2023-03-05 04:00 | 66.0727 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1321.9243
1517 | 2023-03-05 05:00 | -19.9005 | 53.53 | 20 | 10 | 0 | 10.5 | 672.5906
1518 | 2023-03-05 06:00 | -74.9372 | 53.53 | 20 | 10 | 0 | 20 | -428.1433
1519 | 2023-03-05 07:00 | 79.8907 | 53.53 | 10 | 0 | 0 | 20 | 1334.2074
1520 | 2023-03-05 08:00 | 92.9879 | 53.53 | 10 | 0 | 0 | 20 | 1465.1793
1521 | 2023-03-05 09:00 | 86.8552 | 53.53 | 10 | 0 | 0 | 20 | 1403.8525
1522 | 2023-03-05 10:00 | 99.2026 | 53.53 | 10 | 0 | 0 | 20 | 1527.3261
1523 | 2023-03-05 11:00 | 99.5246 | 53.53 | 10 | 0 | 0 | 20 | 1530.5461
1524 | 2023-03-05 12:00 | 97.9092 | 53.53 | 10 | 0 | 0 | 20 | 1514.3919
1525 | 2023-03-05 13:00 | 110.4529 | 53.53 | 1 | 0 | 9 | 11 | 163.9829
1526 | 2023-03-05 14:00 | 111.7156 | 53.53 | 0 | 0 | 10 | 1 | 0
1527 | 2023-03-05 15:00 | 99.6525 | 53.53 | 20 | 10 | 0 | 10.5 | 3063.6501
1528 | 2023-03-05 16:00 | 89.0752 | 53.53 | 20 | 10 | 0 | 20 | 2852.1048
1529 | 2023-03-05 17:00 | 120.9843 | 53.53 | 0 | 0 | 10 | 10 | 0
1530 | 2023-03-05 18:00 | 120.4306 | 53.53 | 0 | 0 | 10 | 0 | 0
1531 | 2023-03-05 19:00 | 118.3298 | 53.53 | 10 | 0 | 0 | 0 | 1718.5984
1532 | 2023-03-05 20:00 | 104.4578 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1663.0295
1533 | 2023-03-05 21:00 | 88.5252 | 53.53 | 20 | 10 | 0 | 10 | 2841.1046
1534 | 2023-03-05 22:00 | 116.5711 | 53.53 | 0 | 0 | 10 | 0 | 0
1535 | 2023-03-05 23:00 | 84.6456 | 53.53 | 20 | 10 | 0 | 9.5 | 2763.5113
1536 | 2023-03-06 00:00 | 105.1991 | 53.53 | 0.5 | 0 | 9.5 | 0 | 79.3645
1537 | 2023-03-06 01:00 | -59.7747 | 53.53 | 20 | 10 | 0 | 9.5 | -124.8941
1538 | 2023-03-06 02:00 | -36.5148 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 188.0628
1539 | 2023-03-06 03:00 | -57.0415 | 53.53 | 20 | 10 | 0 | 20 | -70.2307
1540 | 2023-03-06 04:00 | 77.0162 | 53.53 | 10 | 0 | 0 | 20 | 1305.4618
1541 | 2023-03-06 05:00 | 86.0625 | 53.53 | 10 | 0 | 0 | 20 | 1395.9246
1542 | 2023-03-06 06:00 | 80.7402 | 53.53 | 10 | 0 | 0 | 20 | 1342.7016
1543 | 2023-03-06 07:00 | 98.1234 | 53.53 | 10 | 0 | 0 | 20 | 1516.5338
1544 | 2023-03-06 08:00 | 121.5369 | 65.03 | 0 | 0 | 10 | 10 | 0
1545 | 2023-03-06 09:00 | 107.1849 | 65.03 | 10 | 0 | 0 | 10 | 1722.1491
1546 | 2023-03-06 10:00 | 98.5514 | 65.03 | 20 | 10 | 0 | 19.5 | 3271.6288
1547 | 2023-03-06 11:00 | 103.5449 | 65.03 | 10 | 0 | 0 | 19.5 | 1685.749
1548 | 2023-03-06 12:00 | 113.3937 | 65.03 | 0 | 0 | 10 | 9.5 | 0
1549 | 2023-03-06 13:00 | 112.0478 | 65.03 | 0.5 | 0 | 9.5 | 0 | 88.5389
1550 | 2023-03-06 14:00 | 99.5215 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1818.7274
1551 | 2023-03-06 15:00 | 104.0155 | 65.03 | 10 | 0 | 0 | 1 | 1690.4546
1552 | 2023-03-06 16:00 | -57.4814 | 65.03 | 20 | 10 | 0 | 10.5 | 150.9712
1553 | 2023-03-06 17:00 | -19.3334 | 66.4 | 20 | 10 | 0 | 20 | 941.3312
1554 | 2023-03-06 18:00 | 115.4436 | 66.4 | 0 | 0 | 10 | 10 | 0
1555 | 2023-03-06 19:00 | 119.6031 | 65.03 | 0 | 0 | 10 | 0 | 0
1556 | 2023-03-06 20:00 | 98.9897 | 65.03 | 20 | 10 | 0 | 9.5 | 3280.3944
1557 | 2023-03-06 21:00 | 110.4093 | 65.03 | 10 | 0 | 0 | 9.5 | 1754.3928
1558 | 2023-03-06 22:00 | 110.7666 | 65.03 | 0.5 | 0 | 9.5 | 0 | 87.8983
1559 | 2023-03-06 23:00 | 97.8283 | 53.53 | 10 | 0 | 0 | 0 | 1513.583
1560 | 2023-03-07 00:00 | 96.1243 | 53.53 | 10 | 0 | 0 | 0 | 1496.5433
1561 | 2023-03-07 01:00 | -74.9448 | 53.53 | 20 | 10 | 0 | 9.5 | -428.2965
1562 | 2023-03-07 02:00 | 73.4665 | 53.53 | 10 | 0 | 0 | 9.5 | 1269.9646
1563 | 2023-03-07 03:00 | 71.6206 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1383.244
1564 | 2023-03-07 04:00 | 72.7539 | 53.53 | 10 | 0 | 0 | 10.5 | 1262.839
1565 | 2023-03-07 05:00 | 74.5631 | 53.53 | 10 | 0 | 0 | 10.5 | 1280.9311
1566 | 2023-03-07 06:00 | 71.5324 | 53.53 | 20 | 10 | 0 | 20 | 2501.2478
1567 | 2023-03-07 07:00 | 100.1438 | 53.53 | 10 | 0 | 0 | 20 | 1536.7378
1568 | 2023-03-07 08:00 | 115.0164 | 65.03 | 0 | 0 | 10 | 10 | 0
1569 | 2023-03-07 09:00 | 99.4279 | 65.03 | 20 | 10 | 0 | 19.5 | 3289.1576
1570 | 2023-03-07 10:00 | 109.0875 | 65.03 | 10 | 0 | 0 | 19.5 | 1741.1748
1571 | 2023-03-07 11:00 | 107.302 | 65.03 | 10 | 0 | 0 | 19.5 | 1723.3203
1572 | 2023-03-07 12:00 | 111.5954 | 65.03 | 0 | 0 | 10 | 9.5 | 0
1573 | 2023-03-07 13:00 | 108.8015 | 65.03 | 10 | 0 | 0 | 9.5 | 1738.3145
1574 | 2023-03-07 14:00 | 100.0625 | 65.03 | 20 | 10 | 0 | 19 | 3301.8492
1575 | 2023-03-07 15:00 | 101.0168 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1835.254
1576 | 2023-03-07 16:00 | 109.12 | 65.03 | 10 | 0 | 0 | 20 | 1741.4996
1577 | 2023-03-07 17:00 | 132.9374 | 66.4 | 0 | 0 | 10 | 10 | 0
1578 | 2023-03-07 18:00 | 111.7647 | 66.4 | 10 | 0 | 0 | 10 | 1781.6471
1579 | 2023-03-07 19:00 | 126.6305 | 65.03 | 0 | 0 | 10 | 0 | 0
1580 | 2023-03-07 20:00 | 114.6202 | 65.03 | 10 | 0 | 0 | 0 | 1796.5015
1581 | 2023-03-07 21:00 | 102.7766 | 65.03 | 10 | 0 | 0 | 0 | 1678.0656
1582 | 2023-03-07 22:00 | 108.3849 | 65.03 | 10 | 0 | 0 | 0 | 1734.1493
1583 | 2023-03-07 23:00 | 94.1443 | 53.53 | 10 | 0 | 0 | 0 | 1476.7426
1584 | 2023-03-08 00:00 | 98.0189 | 53.53 | 10 | 0 | 0 | 0 | 1515.489
1585 | 2023-03-08 01:00 | 89.2711 | 53.53 | 10 | 0 | 0 | 0 | 1428.0114
1586 | 2023-03-08 02:00 | 66.272 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1324.1274
1587 | 2023-03-08 03:00 | -56.0253 | 53.53 | 20 | 10 | 0 | 10.5 | -49.9059
1588 | 2023-03-08 04:00 | -30.0626 | 53.53 | 20 | 10 | 0 | 20 | 469.3472
1589 | 2023-03-08 05:00 | 75.705 | 53.53 | 10 | 0 | 0 | 20 | 1292.3501
1590 | 2023-03-08 06:00 | 70.3914 | 53.53 | 10 | 0 | 0 | 20 | 1239.2142
1591 | 2023-03-08 07:00 | 90.2754 | 53.53 | 10 | 0 | 0 | 20 | 1438.0542
1592 | 2023-03-08 08:00 | 107.6279 | 65.03 | 10 | 0 | 0 | 20 | 1726.5794
1593 | 2023-03-08 09:00 | 103.9839 | 65.03 | 10 | 0 | 0 | 20 | 1690.139
1594 | 2023-03-08 10:00 | 111.9001 | 65.03 | 10 | 0 | 0 | 20 | 1769.3006
1595 | 2023-03-08 11:00 | 112.5335 | 65.03 | 10 | 0 | 0 | 20 | 1775.6352
1596 | 2023-03-08 12:00 | 111.4243 | 65.03 | 10 | 0 | 0 | 20 | 1764.543
1597 | 2023-03-08 13:00 | 110.7534 | 65.03 | 10 | 0 | 0 | 20 | 1757.8341
1598 | 2023-03-08 14:00 | 124.0316 | 65.03 | 0 | 0 | 10 | 10 | 0
1599 | 2023-03-08 15:00 | 102.047 | 65.03 | 20 | 10 | 0 | 19.5 | 3341.5397
1600 | 2023-03-08 16:00 | 108.4897 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1826.5229
1601 | 2023-03-08 17:00 | 134.0152 | 66.4 | 0 | 0 | 10 | 10 | 0
1602 | 2023-03-08 18:00 | 135.4321 | 66.4 | 0 | 0 | 10 | 0 | 0
1603 | 2023-03-08 19:00 | 115.2176 | 65.03 | 10 | 0 | 0 | 0 | 1802.4758
1604 | 2023-03-08 20:00 | 101.6621 | 65.03 | 20 | 10 | 0 | 9.5 | 3333.841
1605 | 2023-03-08 21:00 | 116.4723 | 65.03 | 0.5 | 0 | 9.5 | 0 | 90.7511
1606 | 2023-03-08 22:00 | 108.0146 | 65.03 | 10 | 0 | 0 | 0 | 1730.4465
1607 | 2023-03-08 23:00 | 100.4065 | 53.53 | 10 | 0 | 0 | 0 | 1539.3652
1608 | 2023-03-09 00:00 | 97.3178 | 53.53 | 10 | 0 | 0 | 0 | 1508.4784
1609 | 2023-03-09 01:00 | -64.0977 | 53.53 | 20 | 10 | 0 | 9.5 | -211.354
1610 | 2023-03-09 02:00 | -62.108 | 53.53 | 20 | 10 | 0 | 19 | -171.5606
1611 | 2023-03-09 03:00 | -26.0618 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 303.5963
1612 | 2023-03-09 04:00 | 78.581 | 53.53 | 10 | 0 | 0 | 20 | 1321.11
1613 | 2023-03-09 05:00 | 79.4948 | 53.53 | 10 | 0 | 0 | 20 | 1330.248
1614 | 2023-03-09 06:00 | 74.2967 | 53.53 | 10 | 0 | 0 | 20 | 1278.2666
1615 | 2023-03-09 07:00 | 103.2255 | 53.53 | 10 | 0 | 0 | 20 | 1567.5548
1616 | 2023-03-09 08:00 | 143.8266 | 65.03 | 0 | 0 | 10 | 10 | 0
1617 | 2023-03-09 09:00 | 98.5679 | 65.03 | 20 | 10 | 0 | 19.5 | 3271.9589
1618 | 2023-03-09 10:00 | 111.4504 | 65.03 | 10 | 0 | 0 | 19.5 | 1764.8043
1619 | 2023-03-09 11:00 | 103.8003 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1777.1608
1620 | 2023-03-09 12:00 | 113.6265 | 65.03 | 10 | 0 | 0 | 20 | 1786.5652
1621 | 2023-03-09 13:00 | 109.2499 | 65.03 | 10 | 0 | 0 | 20 | 1742.7994
1622 | 2023-03-09 14:00 | 115.3179 | 65.03 | 10 | 0 | 0 | 20 | 1803.4792
1623 | 2023-03-09 15:00 | 119.4692 | 65.03 | 10 | 0 | 0 | 20 | 1844.992
1624 | 2023-03-09 16:00 | 110.3839 | 65.03 | 10 | 0 | 0 | 20 | 1754.1393
1625 | 2023-03-09 17:00 | 134.0085 | 66.4 | 0 | 0 | 10 | 10 | 0
1626 | 2023-03-09 18:00 | 111.2722 | 66.4 | 10 | 0 | 0 | 10 | 1776.7217
1627 | 2023-03-09 19:00 | 139.1846 | 65.03 | 0 | 0 | 10 | 0 | 0
1628 | 2023-03-09 20:00 | 106.8756 | 65.03 | 10 | 0 | 0 | 0 | 1719.0563
1629 | 2023-03-09 21:00 | 113.4421 | 65.03 | 10 | 0 | 0 | 0 | 1784.7213
1630 | 2023-03-09 22:00 | 96.2365 | 65.03 | 10 | 0 | 0 | 0 | 1612.6652
1631 | 2023-03-09 23:00 | 93.3833 | 53.53 | 10 | 0 | 0 | 0 | 1469.133
1632 | 2023-03-10 00:00 | 100.0172 | 53.53 | 10 | 0 | 0 | 0 | 1535.4716
1633 | 2023-03-10 01:00 | 98.7708 | 53.53 | 10 | 0 | 0 | 0 | 1523.0085
1634 | 2023-03-10 02:00 | 81.1141 | 53.53 | 20 | 10 | 0 | 9.5 | 2692.8814
1635 | 2023-03-10 03:00 | 88.5113 | 53.53 | 1.5 | 0 | 8.5 | 1 | 213.062
1636 | 2023-03-10 04:00 | 68.6198 | 53.53 | 20 | 10 | 0 | 10.5 | 2442.9963
1637 | 2023-03-10 05:00 | 87.3808 | 53.53 | 10 | 0 | 0 | 10.5 | 1409.1076
1638 | 2023-03-10 06:00 | 78.9605 | 53.53 | 20 | 10 | 0 | 20 | 2649.81
1639 | 2023-03-10 07:00 | 97.4157 | 53.53 | 10 | 0 | 0 | 20 | 1509.4572
1640 | 2023-03-10 08:00 | 99.9777 | 65.03 | 10 | 0 | 0 | 20 | 1650.0774
1641 | 2023-03-10 09:00 | 112.9707 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 89.0004
1642 | 2023-03-10 10:00 | 96.0157 | 65.03 | 20 | 10 | 0 | 20 | 3220.9144
1643 | 2023-03-10 11:00 | 114.2664 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 89.6482
1644 | 2023-03-10 12:00 | 99.8768 | 65.03 | 20 | 10 | 0 | 20 | 3298.1361
1645 | 2023-03-10 13:00 | 109.3025 | 65.03 | 10 | 0 | 0 | 20 | 1743.3247
1646 | 2023-03-10 14:00 | 108.0203 | 65.03 | 10 | 0 | 0 | 20 | 1730.5033
1647 | 2023-03-10 15:00 | 119.4056 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 92.2178
1648 | 2023-03-10 16:00 | 107.5937 | 65.03 | 20 | 10 | 0 | 20 | 3452.4733
1649 | 2023-03-10 17:00 | 119.1986 | 66.4 | 10 | 0 | 0 | 20 | 1855.9858
1650 | 2023-03-10 18:00 | 120.3734 | 66.4 | 0 | 0 | 10 | 10 | 0
1651 | 2023-03-10 19:00 | 135.5237 | 65.03 | 0 | 0 | 10 | 0 | 0
1652 | 2023-03-10 20:00 | 108.2622 | 65.03 | 10 | 0 | 0 | 0 | 1732.9217
1653 | 2023-03-10 21:00 | 101.1671 | 65.03 | 10 | 0 | 0 | 0 | 1661.9711
1654 | 2023-03-10 22:00 | 102.1864 | 65.03 | 10 | 0 | 0 | 0 | 1672.1639
1655 | 2023-03-10 23:00 | 89.521 | 53.53 | 10 | 0 | 0 | 0 | 1430.5097
1656 | 2023-03-11 00:00 | 93.9884 | 53.53 | 10 | 0 | 0 | 0 | 1475.1843
1657 | 2023-03-11 01:00 | -13.0495 | 53.53 | 20 | 10 | 0 | 9.5 | 809.6107
1658 | 2023-03-11 02:00 | -26.9134 | 53.53 | 20 | 10 | 0 | 19 | 532.3317
1659 | 2023-03-11 03:00 | 71.8818 | 53.53 | 10 | 0 | 0 | 19 | 1254.1182
1660 | 2023-03-11 04:00 | 97.0585 | 53.53 | 0 | 0 | 10 | 9 | 0
1661 | 2023-03-11 05:00 | 63.8707 | 53.53 | 20 | 10 | 0 | 18.5 | 2348.0134
1662 | 2023-03-11 06:00 | 70.1401 | 53.53 | 11.5789 | 1.5789 | 0 | 20 | 1431.9693
1663 | 2023-03-11 07:00 | 108.7764 | 53.53 | 0 | 0 | 10 | 10 | 0
1664 | 2023-03-11 08:00 | 111.6391 | 53.53 | 0 | 0 | 10 | 0 | 0
1665 | 2023-03-11 09:00 | 96.186 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1654.7553
1666 | 2023-03-11 10:00 | 102.6358 | 53.53 | 10 | 0 | 0 | 1 | 1561.6578
1667 | 2023-03-11 11:00 | 100.9133 | 53.53 | 10 | 0 | 0 | 1 | 1544.4331
1668 | 2023-03-11 12:00 | 103.105 | 53.53 | 10 | 0 | 0 | 1 | 1566.3499
1669 | 2023-03-11 13:00 | 96.1709 | 53.53 | 20 | 10 | 0 | 10.5 | 2994.0187
1670 | 2023-03-11 14:00 | 100.2373 | 53.53 | 10 | 0 | 0 | 10.5 | 1537.673
1671 | 2023-03-11 15:00 | 91.3769 | 53.53 | 20 | 10 | 0 | 20 | 2898.1386
1672 | 2023-03-11 16:00 | 101.9326 | 53.53 | 10 | 0 | 0 | 20 | 1554.6255
1673 | 2023-03-11 17:00 | 119.5119 | 53.53 | 0 | 0 | 10 | 10 | 0
1674 | 2023-03-11 18:00 | 114.2495 | 53.53 | 0 | 0 | 10 | 0 | 0
1675 | 2023-03-11 19:00 | 106.2982 | 53.53 | 10 | 0 | 0 | 0 | 1598.282
1676 | 2023-03-11 20:00 | 104.5289 | 53.53 | 10 | 0 | 0 | 0 | 1580.5887
1677 | 2023-03-11 21:00 | 98.7873 | 53.53 | 10 | 0 | 0 | 0 | 1523.1733
1678 | 2023-03-11 22:00 | 91.0054 | 53.53 | 10 | 0 | 0 | 0 | 1445.3537
1679 | 2023-03-11 23:00 | 88.8799 | 53.53 | 10 | 0 | 0 | 0 | 1424.0995
1680 | 2023-03-12 00:00 | 81.8358 | 53.53 | 10 | 0 | 0 | 0 | 1353.6581
1681 | 2023-03-12 01:00 | 84.2781 | 53.53 | 10 | 0 | 0 | 0 | 1378.0812
1682 | 2023-03-12 02:00 | 67.1733 | 53.53 | 20 | 10 | 0 | 9.5 | 2414.066
1683 | 2023-03-12 03:00 | 82.0384 | 53.53 | 1.5 | 0 | 8.5 | 1 | 203.3526
1684 | 2023-03-12 04:00 | 66.5341 | 53.53 | 20 | 10 | 0 | 10.5 | 2401.281
1685 | 2023-03-12 05:00 | 76.192 | 53.53 | 10 | 0 | 0 | 10.5 | 1297.2201
1686 | 2023-03-12 06:00 | 67.1701 | 53.53 | 20 | 10 | 0 | 20 | 2414.0016
1687 | 2023-03-12 07:00 | 92.8288 | 53.53 | 10 | 0 | 0 | 20 | 1463.5882
1688 | 2023-03-12 08:00 | 99.86 | 53.53 | 10 | 0 | 0 | 20 | 1533.9002
1689 | 2023-03-12 09:00 | 108.3838 | 53.53 | 0 | 0 | 10 | 10 | 0
1690 | 2023-03-12 10:00 | 97.1925 | 53.53 | 10 | 0 | 0 | 10 | 1507.2246
1691 | 2023-03-12 11:00 | 91.4959 | 53.53 | 20 | 10 | 0 | 19.5 | 2900.5182
1692 | 2023-03-12 12:00 | 92.4137 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1536.2492
1693 | 2023-03-12 13:00 | 97.2112 | 53.53 | 10 | 0 | 0 | 20 | 1507.4121
1694 | 2023-03-12 14:00 | 93.0854 | 53.53 | 10 | 0 | 0 | 20 | 1466.1538
1695 | 2023-03-12 15:00 | 104.1722 | 53.53 | 10 | 0 | 0 | 20 | 1577.0221
1696 | 2023-03-12 16:00 | 97.6381 | 53.53 | 10 | 0 | 0 | 20 | 1511.6812
1697 | 2023-03-12 17:00 | 141.8694 | 53.53 | 0 | 0 | 10 | 10 | 0
1698 | 2023-03-12 18:00 | 105.7418 | 53.53 | 10 | 0 | 0 | 10 | 1592.718
1699 | 2023-03-12 19:00 | 117.4732 | 53.53 | 0 | 0 | 10 | 0 | 0
1700 | 2023-03-12 20:00 | 88.7213 | 53.53 | 20 | 10 | 0 | 9.5 | 2845.0262
1701 | 2023-03-12 21:00 | 92.4586 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1613.5587
1702 | 2023-03-12 22:00 | 96.9818 | 53.53 | 10 | 0 | 0 | 10.5 | 1505.1177
1703 | 2023-03-12 23:00 | 78.3426 | 53.53 | 20 | 10 | 0 | 20 | 2637.4526
1704 | 2023-03-13 00:00 | 100.7391 | 53.53 | 0 | 0 | 10 | 10 | 0
1705 | 2023-03-13 01:00 | 118.1436 | 53.53 | 0 | 0 | 10 | 0 | 0
1706 | 2023-03-13 02:00 | 75.7187 | 53.53 | 20 | 10 | 0 | 9.5 | 2584.9737
1707 | 2023-03-13 03:00 | 80.9248 | 53.53 | 10 | 0 | 0 | 9.5 | 1344.5481
1708 | 2023-03-13 04:00 | 87.898 | 53.53 | 1.5 | 0 | 8.5 | 1 | 212.142
1709 | 2023-03-13 05:00 | 77.6984 | 53.53 | 20 | 10 | 0 | 10.5 | 2624.5681
1710 | 2023-03-13 06:00 | 74.8997 | 53.53 | 20 | 10 | 0 | 20 | 2568.5936
1711 | 2023-03-13 07:00 | 86.5293 | 53.53 | 10 | 0 | 0 | 20 | 1400.5932
1712 | 2023-03-13 08:00 | 114.1991 | 65.03 | 0 | 0 | 10 | 10 | 0
1713 | 2023-03-13 09:00 | 108.0638 | 65.03 | 10 | 0 | 0 | 10 | 1730.9379
1714 | 2023-03-13 10:00 | 102.3484 | 65.03 | 20 | 10 | 0 | 19.5 | 3347.5684
1715 | 2023-03-13 11:00 | 109.866 | 65.03 | 10 | 0 | 0 | 19.5 | 1748.9604
1716 | 2023-03-13 12:00 | 104.8825 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1788.5531
1717 | 2023-03-13 13:00 | 105.2333 | 65.03 | 10 | 0 | 0 | 20 | 1702.6329
1718 | 2023-03-13 14:00 | 113.8853 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 89.4576
1719 | 2023-03-13 15:00 | 100.6309 | 65.03 | 20 | 10 | 0 | 20 | 3313.2189
1720 | 2023-03-13 16:00 | 118.1272 | 65.03 | 10 | 0 | 0 | 20 | 1831.5721
1721 | 2023-03-13 17:00 | 115.3359 | 66.4 | 10 | 0 | 0 | 20 | 1817.3588
1722 | 2023-03-13 18:00 | 119.3909 | 66.4 | 0 | 0 | 10 | 10 | 0
1723 | 2023-03-13 19:00 | 143.4103 | 65.03 | 0 | 0 | 10 | 0 | 0
1724 | 2023-03-13 20:00 | 113.9591 | 65.03 | 10 | 0 | 0 | 0 | 1789.8906
1725 | 2023-03-13 21:00 | 104.6412 | 65.03 | 10 | 0 | 0 | 0 | 1696.7116
1726 | 2023-03-13 22:00 | 97.7521 | 65.03 | 10 | 0 | 0 | 0 | 1627.8215
1727 | 2023-03-13 23:00 | 95.2279 | 53.53 | 10 | 0 | 0 | 0 | 1487.5787
1728 | 2023-03-14 00:00 | 99.454 | 53.53 | 10 | 0 | 0 | 0 | 1529.8396
1729 | 2023-03-14 01:00 | 99.1813 | 53.53 | 10 | 0 | 0 | 0 | 1527.1132
1730 | 2023-03-14 02:00 | 78.226 | 53.53 | 10 | 0 | 0 | 0 | 1317.5598
1731 | 2023-03-14 03:00 | 78.6681 | 53.53 | 10 | 0 | 0 | 0 | 1321.9813
1732 | 2023-03-14 04:00 | 77.3411 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1446.4701
1733 | 2023-03-14 05:00 | 70.1189 | 53.53 | 20 | 10 | 0 | 10.5 | 2472.9782
1734 | 2023-03-14 06:00 | 75.3097 | 53.53 | 20 | 10 | 0 | 20 | 2576.7937
1735 | 2023-03-14 07:00 | 106.7914 | 53.53 | 10 | 0 | 0 | 20 | 1603.2141
1736 | 2023-03-14 08:00 | 100.4813 | 65.03 | 10 | 0 | 0 | 20 | 1655.1126
1737 | 2023-03-14 09:00 | 107.5163 | 65.03 | 10 | 0 | 0 | 20 | 1725.4631
1738 | 2023-03-14 10:00 | 103.4478 | 65.03 | 10 | 0 | 0 | 20 | 1684.778
1739 | 2023-03-14 11:00 | 109.7475 | 65.03 | 10 | 0 | 0 | 20 | 1747.7754
1740 | 2023-03-14 12:00 | 106.1471 | 65.03 | 10 | 0 | 0 | 20 | 1711.7706
1741 | 2023-03-14 13:00 | 122.8411 | 65.03 | 0 | 0 | 10 | 10 | 0
1742 | 2023-03-14 14:00 | 113.0016 | 65.03 | 10 | 0 | 0 | 10 | 1780.3158
1743 | 2023-03-14 15:00 | 100.7649 | 65.03 | 20 | 10 | 0 | 19.5 | 3315.898
1744 | 2023-03-14 16:00 | 114.4752 | 65.03 | 10 | 0 | 0 | 19.5 | 1795.0519
1745 | 2023-03-14 17:00 | 118.7141 | 66.4 | 10 | 0 | 0 | 19.5 | 1851.1412
1746 | 2023-03-14 18:00 | 119.9247 | 66.4 | 0.5 | 0 | 9.5 | 10 | 93.1623
1747 | 2023-03-14 19:00 | 126.3663 | 65.03 | 0 | 0 | 10 | 0 | 0
1748 | 2023-03-14 20:00 | -60.0378 | 65.03 | 20 | 10 | 0 | 9.5 | 99.8432
1749 | 2023-03-14 21:00 | 111.5773 | 65.03 | 0.5 | 0 | 9.5 | 0 | 88.3037
1750 | 2023-03-14 22:00 | 98.715 | 65.03 | 10 | 0 | 0 | 0 | 1637.4496
1751 | 2023-03-14 23:00 | 94.6617 | 53.53 | 10 | 0 | 0 | 0 | 1481.9171
1752 | 2023-03-15 00:00 | 94.4299 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1635.3462
1753 | 2023-03-15 01:00 | 94.9964 | 53.53 | 10 | 0 | 0 | 1 | 1485.2643
1754 | 2023-03-15 02:00 | 88.6641 | 53.53 | 20 | 10 | 0 | 10.5 | 2843.8815
1755 | 2023-03-15 03:00 | 84.0884 | 53.53 | 20 | 10 | 0 | 20 | 2752.3685
1756 | 2023-03-15 04:00 | 95.655 | 53.53 | 10 | 0 | 0 | 20 | 1491.8497
1757 | 2023-03-15 05:00 | 103.2597 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 78.3949
1758 | 2023-03-15 06:00 | 72.2489 | 53.53 | 20 | 10 | 0 | 20 | 2515.5775
1759 | 2023-03-15 07:00 | 99.4321 | 53.53 | 10 | 0 | 0 | 20 | 1529.6207
1760 | 2023-03-15 08:00 | 101.4652 | 65.03 | 10 | 0 | 0 | 20 | 1664.9519
1761 | 2023-03-15 09:00 | 103.6966 | 65.03 | 10 | 0 | 0 | 20 | 1687.2657
1762 | 2023-03-15 10:00 | 104.5925 | 65.03 | 10 | 0 | 0 | 20 | 1696.2246
1763 | 2023-03-15 11:00 | 102.1039 | 65.03 | 10 | 0 | 0 | 20 | 1671.3391
1764 | 2023-03-15 12:00 | 102.1327 | 65.03 | 10 | 0 | 0 | 20 | 1671.627
1765 | 2023-03-15 13:00 | 107.8393 | 65.03 | 10 | 0 | 0 | 20 | 1728.6926
1766 | 2023-03-15 14:00 | 101.253 | 65.03 | 10 | 0 | 0 | 20 | 1662.8295
1767 | 2023-03-15 15:00 | 116.0837 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 90.5569
1768 | 2023-03-15 16:00 | 102.8814 | 65.03 | 20 | 10 | 0 | 20 | 3358.2284
1769 | 2023-03-15 17:00 | 156.974 | 66.4 | 0 | 0 | 10 | 10 | 0
1770 | 2023-03-15 18:00 | 120.7321 | 66.4 | 10 | 0 | 0 | 10 | 1871.3213
1771 | 2023-03-15 19:00 | 124.4443 | 65.03 | 0 | 0 | 10 | 0 | 0
1772 | 2023-03-15 20:00 | -6.9183 | 65.03 | 20 | 10 | 0 | 9.5 | 1162.2348
1773 | 2023-03-15 21:00 | -24.2854 | 65.03 | 20 | 10 | 0 | 19 | 814.892
1774 | 2023-03-15 22:00 | 113.8765 | 65.03 | 0 | 0 | 10 | 9 | 0
1775 | 2023-03-15 23:00 | 101.2274 | 53.53 | 1 | 0 | 9 | 0 | 154.7574
1776 | 2023-03-16 00:00 | 90.5887 | 53.53 | 20 | 10 | 0 | 9.5 | 2882.3746
1777 | 2023-03-16 01:00 | 100.5293 | 53.53 | 0.5 | 0 | 9.5 | 0 | 77.0297
1778 | 2023-03-16 02:00 | 71.7562 | 53.53 | 20 | 10 | 0 | 9.5 | 2505.7243
1779 | 2023-03-16 03:00 | 92.6658 | 53.53 | 1.5 | 0 | 8.5 | 1 | 219.2937
1780 | 2023-03-16 04:00 | 85.7673 | 53.53 | 10 | 0 | 0 | 1 | 1392.9732
1781 | 2023-03-16 05:00 | 79.6244 | 53.53 | 20 | 10 | 0 | 10.5 | 2663.0889
1782 | 2023-03-16 06:00 | 65.935 | 53.53 | 20 | 10 | 0 | 20 | 2389.3008
1783 | 2023-03-16 07:00 | 92.5111 | 53.53 | 10 | 0 | 0 | 20 | 1460.4113
1784 | 2023-03-16 08:00 | 114.6272 | 65.03 | 10 | 0 | 0 | 20 | 1796.5722
1785 | 2023-03-16 09:00 | 119.8703 | 65.03 | 0 | 0 | 10 | 10 | 0
1786 | 2023-03-16 10:00 | 118.7683 | 65.03 | 0 | 0 | 10 | 0 | 0
1787 | 2023-03-16 11:00 | 99.405 | 65.03 | 20 | 10 | 0 | 9.5 | 3288.7
1788 | 2023-03-16 12:00 | 111.2654 | 65.03 | 10 | 0 | 0 | 9.5 | 1762.954
1789 | 2023-03-16 13:00 | 117.8022 | 65.03 | 10 | 0 | 0 | 9.5 | 1828.3222
1790 | 2023-03-16 14:00 | 99.0995 | 65.03 | 20 | 10 | 0 | 19 | 3282.5904
1791 | 2023-03-16 15:00 | 108.8391 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1921.711
1792 | 2023-03-16 16:00 | 111.0388 | 65.03 | 10 | 0 | 0 | 20 | 1760.6885
1793 | 2023-03-16 17:00 | 121.7413 | 66.4 | 0 | 0 | 10 | 10 | 0
1794 | 2023-03-16 18:00 | 113.2408 | 66.4 | 10 | 0 | 0 | 10 | 1796.4081
1795 | 2023-03-16 19:00 | 121.5711 | 65.03 | 0 | 0 | 10 | 0 | 0
1796 | 2023-03-16 20:00 | 101.5602 | 65.03 | 10 | 0 | 0 | 0 | 1665.9019
1797 | 2023-03-16 21:00 | 102.8121 | 65.03 | 10 | 0 | 0 | 0 | 1678.4207
1798 | 2023-03-16 22:00 | 100.0102 | 65.03 | 10 | 0 | 0 | 0 | 1650.4015
1799 | 2023-03-16 23:00 | 95.787 | 53.53 | 10 | 0 | 0 | 0 | 1493.1704
1800 | 2023-03-17 00:00 | 98.6023 | 53.53 | 10 | 0 | 0 | 0 | 1521.3228
1801 | 2023-03-17 01:00 | 102.447 | 53.53 | 10 | 0 | 0 | 0 | 1559.7703
1802 | 2023-03-17 02:00 | 76.7163 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1439.564
1803 | 2023-03-17 03:00 | 76.0072 | 53.53 | 20 | 10 | 0 | 10.5 | 2590.7445
1804 | 2023-03-17 04:00 | 79.6006 | 53.53 | 10 | 0 | 0 | 10.5 | 1331.3065
1805 | 2023-03-17 05:00 | 67.948 | 53.53 | 20 | 10 | 0 | 20 | 2429.5601
1806 | 2023-03-17 06:00 | 82.7447 | 53.53 | 10 | 0 | 0 | 20 | 1362.7474
1807 | 2023-03-17 07:00 | 98.8941 | 53.53 | 10 | 0 | 0 | 20 | 1524.2408
1808 | 2023-03-17 08:00 | 109.1978 | 65.03 | 1 | 0 | 9 | 11 | 174.2278
1809 | 2023-03-17 09:00 | 117.2496 | 65.03 | 0 | 0 | 10 | 1 | 0
1810 | 2023-03-17 10:00 | 97.8142 | 65.03 | 20 | 10 | 0 | 10.5 | 3256.8839
1811 | 2023-03-17 11:00 | 97.7267 | 65.03 | 20 | 10 | 0 | 20 | 3255.1345
1812 | 2023-03-17 12:00 | 111.0385 | 65.03 | 10 | 0 | 0 | 20 | 1760.6853
1813 | 2023-03-17 13:00 | 108.845 | 65.03 | 10 | 0 | 0 | 20 | 1738.7499
1814 | 2023-03-17 14:00 | 110.2078 | 65.03 | 10 | 0 | 0 | 20 | 1752.3777
1815 | 2023-03-17 15:00 | 105.6619 | 65.03 | 10 | 0 | 0 | 20 | 1706.9188
1816 | 2023-03-17 16:00 | 114.4122 | 65.03 | 10 | 0 | 0 | 20 | 1794.4219
1817 | 2023-03-17 17:00 | 131.9697 | 66.4 | 0 | 0 | 10 | 10 | 0
1818 | 2023-03-17 18:00 | 127.8049 | 66.4 | 0 | 0 | 10 | 0 | 0
1819 | 2023-03-17 19:00 | 122.0167 | 65.03 | 10 | 0 | 0 | 0 | 1870.4667
1820 | 2023-03-17 20:00 | 92.1824 | 65.03 | 20 | 10 | 0 | 9.5 | 3144.2484
1821 | 2023-03-17 21:00 | 110.3876 | 65.03 | 10 | 0 | 0 | 9.5 | 1754.1757
1822 | 2023-03-17 22:00 | 114.9659 | 65.03 | 0.5 | 0 | 9.5 | 0 | 89.9979
1823 | 2023-03-17 23:00 | 104.2315 | 53.53 | 10 | 0 | 0 | 0 | 1577.6152
1824 | 2023-03-18 00:00 | 85.0997 | 53.53 | 20 | 10 | 0 | 9.5 | 2772.5941
1825 | 2023-03-18 01:00 | 96.4987 | 53.53 | 0.5 | 0 | 9.5 | 0 | 75.0144
1826 | 2023-03-18 02:00 | 78.2619 | 53.53 | 20 | 10 | 0 | 9.5 | 2635.8384
1827 | 2023-03-18 03:00 | 85.8041 | 53.53 | 0.5 | 0 | 9.5 | 0 | 69.667
1828 | 2023-03-18 04:00 | 65.1201 | 53.53 | 20 | 10 | 0 | 9.5 | 2373.0013
1829 | 2023-03-18 05:00 | 69.2563 | 53.53 | 20 | 10 | 0 | 19 | 2455.7261
1830 | 2023-03-18 06:00 | 77.1808 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1444.6979
1831 | 2023-03-18 07:00 | 91.3326 | 53.53 | 10 | 0 | 0 | 20 | 1448.6261
1832 | 2023-03-18 08:00 | 93.7782 | 53.53 | 10 | 0 | 0 | 20 | 1473.0821
1833 | 2023-03-18 09:00 | 104.2096 | 53.53 | 10 | 0 | 0 | 20 | 1577.396
1834 | 2023-03-18 10:00 | 105.6378 | 53.53 | 1 | 0 | 9 | 11 | 159.1678
1835 | 2023-03-18 11:00 | 101.5668 | 53.53 | 10 | 0 | 0 | 11 | 1550.9681
1836 | 2023-03-18 12:00 | 102.6006 | 53.53 | 10 | 0 | 0 | 11 | 1561.3065
1837 | 2023-03-18 13:00 | 99.0314 | 53.53 | 10 | 0 | 0 | 11 | 1525.614
1838 | 2023-03-18 14:00 | 114.8515 | 53.53 | 0 | 0 | 10 | 1 | 0
1839 | 2023-03-18 15:00 | 94.9788 | 53.53 | 20 | 10 | 0 | 10.5 | 2970.1766
1840 | 2023-03-18 16:00 | 96.8596 | 53.53 | 20 | 10 | 0 | 20 | 3007.7928
1841 | 2023-03-18 17:00 | 115.9808 | 53.53 | 0 | 0 | 10 | 10 | 0
1842 | 2023-03-18 18:00 | 123.4413 | 53.53 | 0 | 0 | 10 | 0 | 0
1843 | 2023-03-18 19:00 | 106.8516 | 53.53 | 10 | 0 | 0 | 0 | 1603.8158
1844 | 2023-03-18 20:00 | 87.7725 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1561.7647
1845 | 2023-03-18 21:00 | 84.4642 | 53.53 | 20 | 10 | 0 | 10.5 | 2759.8836
1846 | 2023-03-18 22:00 | 96.1447 | 53.53 | 0 | 0 | 10 | 0.5 | 0
1847 | 2023-03-18 23:00 | 83.773 | 53.53 | 20 | 10 | 0 | 10 | 2746.0593
1848 | 2023-03-19 00:00 | 88.1743 | 53.53 | 10 | 0 | 0 | 10 | 1417.0433
1849 | 2023-03-19 01:00 | 96.385 | 53.53 | 0 | 0 | 10 | 0 | 0
1850 | 2023-03-19 02:00 | 66.5214 | 53.53 | 20 | 10 | 0 | 9.5 | 2401.0286
1851 | 2023-03-19 03:00 | 72.6945 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1395.1131
1852 | 2023-03-19 04:00 | 68.7511 | 53.53 | 20 | 10 | 0 | 20 | 2445.6225
1853 | 2023-03-19 05:00 | 76.4833 | 53.53 | 10 | 0 | 0 | 20 | 1300.1332
1854 | 2023-03-19 06:00 | 74.7282 | 53.53 | 10 | 0 | 0 | 20 | 1282.5824
1855 | 2023-03-19 07:00 | 86.212 | 53.53 | 10 | 0 | 0 | 20 | 1397.4201
1856 | 2023-03-19 08:00 | 99.6649 | 53.53 | 10 | 0 | 0 | 20 | 1531.9488
1857 | 2023-03-19 09:00 | 110.0906 | 53.53 | 0 | 0 | 10 | 10 | 0
1858 | 2023-03-19 10:00 | 104.0298 | 53.53 | 10 | 0 | 0 | 10 | 1575.5978
1859 | 2023-03-19 11:00 | 92.3395 | 53.53 | 20 | 10 | 0 | 19.5 | 2917.3891
1860 | 2023-03-19 12:00 | 106.3323 | 53.53 | 1 | 0 | 9 | 10.5 | 159.8623
1861 | 2023-03-19 13:00 | 93.9546 | 53.53 | 20 | 10 | 0 | 20 | 2949.6914
1862 | 2023-03-19 14:00 | 114.0904 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 83.8102
1863 | 2023-03-19 15:00 | 109.8896 | 53.53 | 10 | 0 | 0 | 10.5 | 1634.1964
1864 | 2023-03-19 16:00 | 103.1698 | 53.53 | 20 | 10 | 0 | 20 | 3133.9957
1865 | 2023-03-19 17:00 | 117.1058 | 53.53 | 0 | 0 | 10 | 10 | 0
1866 | 2023-03-19 18:00 | 114.3787 | 53.53 | 10 | 0 | 0 | 10 | 1679.0871
1867 | 2023-03-19 19:00 | 121.5422 | 53.53 | 0 | 0 | 10 | 0 | 0
1868 | 2023-03-19 20:00 | 93.2666 | 53.53 | 20 | 10 | 0 | 9.5 | 2935.931
1869 | 2023-03-19 21:00 | 97.729 | 53.53 | 10 | 0 | 0 | 9.5 | 1512.5901
1870 | 2023-03-19 22:00 | 103.3728 | 53.53 | 0.5 | 0 | 9.5 | 0 | 78.4514
1871 | 2023-03-19 23:00 | 87.0207 | 53.53 | 20 | 10 | 0 | 9.5 | 2811.014
1872 | 2023-03-20 00:00 | 94.6789 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.1044
1873 | 2023-03-20 01:00 | 91.3697 | 53.53 | 10 | 0 | 0 | 0 | 1448.9972
1874 | 2023-03-20 02:00 | 72.064 | 53.53 | 20 | 10 | 0 | 9.5 | 2511.8797
1875 | 2023-03-20 03:00 | 68.3434 | 53.53 | 20 | 10 | 0 | 19 | 2437.4687
1876 | 2023-03-20 04:00 | 85.0175 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 207.8212
1877 | 2023-03-20 05:00 | -43.0741 | 53.53 | 20 | 10 | 0 | 20 | 209.1187
1878 | 2023-03-20 06:00 | 92.2376 | 53.53 | 10 | 0 | 0 | 20 | 1457.6757
1879 | 2023-03-20 07:00 | 89.2473 | 53.53 | 10 | 0 | 0 | 20 | 1427.7731
1880 | 2023-03-20 08:00 | 114.9711 | 65.03 | 0 | 0 | 10 | 10 | 0
1881 | 2023-03-20 09:00 | 122.2005 | 65.03 | 0 | 0 | 10 | 0 | 0
1882 | 2023-03-20 10:00 | 105.6966 | 65.03 | 10 | 0 | 0 | 0 | 1707.2662
1883 | 2023-03-20 11:00 | 109.6709 | 65.03 | 10 | 0 | 0 | 0 | 1747.0086
1884 | 2023-03-20 12:00 | 97.5861 | 65.03 | 20 | 10 | 0 | 9.5 | 3252.3229
1885 | 2023-03-20 13:00 | 110.981 | 65.03 | 1.5 | 0 | 8.5 | 1 | 264.0166
1886 | 2023-03-20 14:00 | 102.069 | 65.03 | 20 | 10 | 0 | 10.5 | 3341.9792
1887 | 2023-03-20 15:00 | 110.4413 | 65.03 | 10 | 0 | 0 | 10.5 | 1754.7131
1888 | 2023-03-20 16:00 | 99.549 | 65.03 | 20 | 10 | 0 | 20 | 3291.5799
1889 | 2023-03-20 17:00 | 128.32 | 66.4 | 0 | 0 | 10 | 10 | 0
1890 | 2023-03-20 18:00 | 132.8939 | 66.4 | 0 | 0 | 10 | 0 | 0
1891 | 2023-03-20 19:00 | 118.6635 | 65.03 | 10 | 0 | 0 | 0 | 1836.9349
1892 | 2023-03-20 20:00 | 96.6734 | 65.03 | 10 | 0 | 0 | 0 | 1617.0341
1893 | 2023-03-20 21:00 | 91.9912 | 65.03 | 20 | 10 | 0 | 9.5 | 3140.4238
1894 | 2023-03-20 22:00 | 101.978 | 65.03 | 0.5 | 0 | 9.5 | 0 | 83.504
1895 | 2023-03-20 23:00 | 94.8957 | 53.53 | 10 | 0 | 0 | 0 | 1484.2569
1896 | 2023-03-21 00:00 | 89.5969 | 53.53 | 10 | 0 | 0 | 0 | 1431.2688
1897 | 2023-03-21 01:00 | -63.4201 | 53.53 | 20 | 10 | 0 | 9.5 | -197.8026
1898 | 2023-03-21 02:00 | -39.4507 | 53.53 | 20 | 10 | 0 | 19 | 281.585
1899 | 2023-03-21 03:00 | -18.5791 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 386.2997
1900 | 2023-03-21 04:00 | 75.0666 | 53.53 | 10 | 0 | 0 | 20 | 1285.9659
1901 | 2023-03-21 05:00 | 88.3744 | 53.53 | 10 | 0 | 0 | 20 | 1419.0444
1902 | 2023-03-21 06:00 | 83.8551 | 53.53 | 10 | 0 | 0 | 20 | 1373.8512
1903 | 2023-03-21 07:00 | 97.9419 | 53.53 | 10 | 0 | 0 | 20 | 1514.7189
1904 | 2023-03-21 08:00 | 114.0008 | 65.03 | 0 | 0 | 10 | 10 | 0
1905 | 2023-03-21 09:00 | 101.5459 | 65.03 | 20 | 10 | 0 | 19.5 | 3331.519
1906 | 2023-03-21 10:00 | 109.1423 | 65.03 | 10 | 0 | 0 | 19.5 | 1741.7226
1907 | 2023-03-21 11:00 | 110.028 | 65.03 | 10 | 0 | 0 | 19.5 | 1750.58
1908 | 2023-03-21 12:00 | 105.6116 | 65.03 | 10 | 0 | 0 | 19.5 | 1706.416
1909 | 2023-03-21 13:00 | 112.3872 | 65.03 | 10 | 0 | 0 | 19.5 | 1774.1717
1910 | 2023-03-21 14:00 | 103.6798 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1775.8924
1911 | 2023-03-21 15:00 | 113.0299 | 65.03 | 10 | 0 | 0 | 20 | 1780.5986
1912 | 2023-03-21 16:00 | 113.3996 | 65.03 | 0 | 0 | 10 | 10 | 0
1913 | 2023-03-21 17:00 | 109.3183 | 66.4 | 10 | 0 | 0 | 10 | 1757.1831
1914 | 2023-03-21 18:00 | 134.6275 | 66.4 | 0 | 0 | 10 | 0 | 0
1915 | 2023-03-21 19:00 | 108.9183 | 65.03 | 10 | 0 | 0 | 0 | 1739.4834
1916 | 2023-03-21 20:00 | 99.6798 | 65.03 | 20 | 10 | 0 | 9.5 | 3294.1953
1917 | 2023-03-21 21:00 | 112.9024 | 65.03 | 0.5 | 0 | 9.5 | 0 | 88.9662
1918 | 2023-03-21 22:00 | 101.6284 | 65.03 | 10 | 0 | 0 | 0 | 1666.584
1919 | 2023-03-21 23:00 | 90.0015 | 53.53 | 20 | 10 | 0 | 9.5 | 2870.6308
1920 | 2023-03-22 00:00 | 91.9052 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1530.8968
1921 | 2023-03-22 01:00 | 107.9183 | 53.53 | 0 | 0 | 10 | 0 | 0
1922 | 2023-03-22 02:00 | 67.9455 | 53.53 | 20 | 10 | 0 | 9.5 | 2429.5105
1923 | 2023-03-22 03:00 | 88.9763 | 53.53 | 0.5 | 0 | 9.5 | 0 | 71.2531
1924 | 2023-03-22 04:00 | 78.4884 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1459.1511
1925 | 2023-03-22 05:00 | 71.3801 | 53.53 | 20 | 10 | 0 | 10.5 | 2498.201
1926 | 2023-03-22 06:00 | 74.8861 | 53.53 | 20 | 10 | 0 | 20 | 2568.3221
1927 | 2023-03-22 07:00 | 92.3233 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 72.9267
1928 | 2023-03-22 08:00 | -50.6492 | 65.03 | 20 | 10 | 0 | 20 | 287.6162
1929 | 2023-03-22 09:00 | 115.0418 | 65.03 | 0 | 0 | 10 | 10 | 0
1930 | 2023-03-22 10:00 | 98.8246 | 65.03 | 20 | 10 | 0 | 19.5 | 3277.0929
1931 | 2023-03-22 11:00 | 106.0474 | 65.03 | 10 | 0 | 0 | 19.5 | 1710.7744
1932 | 2023-03-22 12:00 | 103.1947 | 65.03 | 10 | 0 | 0 | 19.5 | 1682.2474
1933 | 2023-03-22 13:00 | 120.751 | 65.03 | 0 | 0 | 10 | 9.5 | 0
1934 | 2023-03-22 14:00 | 100.5722 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1743.1814
1935 | 2023-03-22 15:00 | 124.3515 | 65.03 | 0 | 0 | 10 | 0 | 0
1936 | 2023-03-22 16:00 | 108.6498 | 65.03 | 10 | 0 | 0 | 0 | 1736.7984
1937 | 2023-03-22 17:00 | -66.2427 | 66.4 | 20 | 10 | 0 | 9.5 | 3.1467
1938 | 2023-03-22 18:00 | -31.8978 | 66.4 | 20 | 10 | 0 | 19 | 690.0433
1939 | 2023-03-22 19:00 | 118.5545 | 65.03 | 0 | 0 | 10 | 9 | 0
1940 | 2023-03-22 20:00 | 95.9541 | 65.03 | 11.0526 | 1.0526 | 0 | 10 | 1779.298
1941 | 2023-03-22 21:00 | 104.6197 | 65.03 | 0 | 0 | 10 | 0 | 0
1942 | 2023-03-22 22:00 | 96.1948 | 65.03 | 10 | 0 | 0 | 0 | 1612.2475
1943 | 2023-03-22 23:00 | 86.8959 | 53.53 | 20 | 10 | 0 | 9.5 | 2808.5184
1944 | 2023-03-23 00:00 | 96.2069 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.8685
1945 | 2023-03-23 01:00 | 88.4545 | 53.53 | 10 | 0 | 0 | 0 | 1419.8453
1946 | 2023-03-23 02:00 | 73.8483 | 53.53 | 10 | 0 | 0 | 0 | 1273.7827
1947 | 2023-03-23 03:00 | 72.9307 | 53.53 | 20 | 10 | 0 | 9.5 | 2529.2149
1948 | 2023-03-23 04:00 | 73.1483 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1400.1286
1949 | 2023-03-23 05:00 | -17.4738 | 53.53 | 20 | 10 | 0 | 20 | 721.1249
1950 | 2023-03-23 06:00 | 79.325 | 53.53 | 10 | 0 | 0 | 20 | 1328.5499
1951 | 2023-03-23 07:00 | 100.808 | 53.53 | 10 | 0 | 0 | 20 | 1543.3801
1952 | 2023-03-23 08:00 | 98.5705 | 65.03 | 10 | 0 | 0 | 20 | 1636.0053
1953 | 2023-03-23 09:00 | 104.4447 | 65.03 | 10 | 0 | 0 | 20 | 1694.7473
1954 | 2023-03-23 10:00 | 110.5664 | 65.03 | 10 | 0 | 0 | 20 | 1755.9637
1955 | 2023-03-23 11:00 | 102.283 | 65.03 | 10 | 0 | 0 | 20 | 1673.1298
1956 | 2023-03-23 12:00 | 116.7267 | 65.03 | 0 | 0 | 10 | 10 | 0
1957 | 2023-03-23 13:00 | 101.3261 | 65.03 | 20 | 10 | 0 | 19.5 | 3327.1222
1958 | 2023-03-23 14:00 | 106.8402 | 65.03 | 10 | 0 | 0 | 19.5 | 1718.7023
1959 | 2023-03-23 15:00 | 104.8676 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1788.396
1960 | 2023-03-23 16:00 | 110.1616 | 65.03 | 10 | 0 | 0 | 20 | 1751.9159
1961 | 2023-03-23 17:00 | 119.5279 | 66.4 | 10 | 0 | 0 | 20 | 1859.2794
1962 | 2023-03-23 18:00 | 121.947 | 66.4 | 0 | 0 | 10 | 10 | 0
1963 | 2023-03-23 19:00 | 122.1886 | 65.03 | 0 | 0 | 10 | 0 | 0
1964 | 2023-03-23 20:00 | 98.9549 | 65.03 | 20 | 10 | 0 | 9.5 | 3279.6986
1965 | 2023-03-23 21:00 | 107.8146 | 65.03 | 0.5 | 0 | 9.5 | 0 | 86.4223
1966 | 2023-03-23 22:00 | 105.7517 | 65.03 | 10 | 0 | 0 | 0 | 1707.817
1967 | 2023-03-23 23:00 | 98.2425 | 53.53 | 10 | 0 | 0 | 0 | 1517.7246
1968 | 2023-03-24 00:00 | 95.8696 | 53.53 | 20 | 10 | 0 | 9.5 | 2987.9927
1969 | 2023-03-24 01:00 | 105.6466 | 53.53 | 0.5 | 0 | 9.5 | 0 | 79.5883
1970 | 2023-03-24 02:00 | 77.1907 | 53.53 | 20 | 10 | 0 | 9.5 | 2614.4134
1971 | 2023-03-24 03:00 | 76.7007 | 53.53 | 20 | 10 | 0 | 19 | 2604.6145
1972 | 2023-03-24 04:00 | 79.6959 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1472.4972
1973 | 2023-03-24 05:00 | 95.488 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 74.509
1974 | 2023-03-24 06:00 | 70.621 | 53.53 | 20 | 10 | 0 | 20 | 2483.0208
1975 | 2023-03-24 07:00 | 105.3934 | 53.53 | 10 | 0 | 0 | 20 | 1589.2343
1976 | 2023-03-24 08:00 | 98.0654 | 65.03 | 10 | 0 | 0 | 20 | 1630.9544
1977 | 2023-03-24 09:00 | 110.5821 | 65.03 | 10 | 0 | 0 | 20 | 1756.1214
1978 | 2023-03-24 10:00 | 123.9993 | 65.03 | 0 | 0 | 10 | 10 | 0
1979 | 2023-03-24 11:00 | 112.8456 | 65.03 | 10 | 0 | 0 | 10 | 1778.7559
1980 | 2023-03-24 12:00 | 110.2113 | 65.03 | 10 | 0 | 0 | 10 | 1752.4131
1981 | 2023-03-24 13:00 | 105.0293 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1790.0979
1982 | 2023-03-24 14:00 | 109.1322 | 65.03 | 10 | 0 | 0 | 10.5 | 1741.6225
1983 | 2023-03-24 15:00 | 107.0775 | 65.03 | 10 | 0 | 0 | 10.5 | 1721.0754
1984 | 2023-03-24 16:00 | 103.6469 | 65.03 | 20 | 10 | 0 | 20 | 3373.5382
1985 | 2023-03-24 17:00 | 121.8161 | 66.4 | 0 | 0 | 10 | 10 | 0
1986 | 2023-03-24 18:00 | 125.4313 | 66.4 | 0 | 0 | 10 | 0 | 0
1987 | 2023-03-24 19:00 | 118.7584 | 65.03 | 10 | 0 | 0 | 0 | 1837.8837
1988 | 2023-03-24 20:00 | 98.527 | 65.03 | 10 | 0 | 0 | 0 | 1635.5698
1989 | 2023-03-24 21:00 | 95.5216 | 65.03 | 20 | 10 | 0 | 9.5 | 3211.0313
1990 | 2023-03-24 22:00 | 107.0074 | 65.03 | 0.5 | 0 | 9.5 | 0 | 86.0187
1991 | 2023-03-24 23:00 | 103.3418 | 53.53 | 10 | 0 | 0 | 0 | 1568.718
1992 | 2023-03-25 00:00 | 92.6976 | 53.53 | 10 | 0 | 0 | 0 | 1462.2756
1993 | 2023-03-25 01:00 | 99.294 | 53.53 | 10 | 0 | 0 | 0 | 1528.24
1994 | 2023-03-25 02:00 | 71.5661 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1382.6408
1995 | 2023-03-25 03:00 | 74.0183 | 53.53 | 10 | 0 | 0 | 1 | 1275.4825
1996 | 2023-03-25 04:00 | 73.2842 | 53.53 | 10 | 0 | 0 | 1 | 1268.1417
1997 | 2023-03-25 05:00 | 70.2211 | 53.53 | 20 | 10 | 0 | 10.5 | 2475.0219
1998 | 2023-03-25 06:00 | 67.218 | 53.53 | 20 | 10 | 0 | 20 | 2414.9592
1999 | 2023-03-25 07:00 | 114.4739 | 53.53 | 0 | 0 | 10 | 10 | 0
2000 | 2023-03-25 08:00 | 97.7284 | 53.53 | 10 | 0 | 0 | 10 | 1512.5842
2001 | 2023-03-25 09:00 | 96.3714 | 53.53 | 20 | 10 | 0 | 19.5 | 2998.0284
2002 | 2023-03-25 10:00 | 104.3748 | 53.53 | 1 | 0 | 9 | 10.5 | 157.9048
2003 | 2023-03-25 11:00 | 102.8604 | 53.53 | 10 | 0 | 0 | 10.5 | 1563.9041
2004 | 2023-03-25 12:00 | 92.3009 | 53.53 | 20 | 10 | 0 | 20 | 2916.6176
2005 | 2023-03-25 13:00 | 110.9099 | 53.53 | 0 | 0 | 10 | 10 | 0
2006 | 2023-03-25 14:00 | 100.2017 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1618.2288
2007 | 2023-03-25 15:00 | 93.8126 | 53.53 | 20 | 10 | 0 | 20 | 2946.8511
2008 | 2023-03-25 16:00 | 111.6112 | 53.53 | 10 | 0 | 0 | 20 | 1651.4117
2009 | 2023-03-25 17:00 | 121.0602 | 53.53 | 0 | 0 | 10 | 10 | 0
2010 | 2023-03-25 18:00 | 108.0057 | 53.53 | 10 | 0 | 0 | 10 | 1615.3574
2011 | 2023-03-25 19:00 | 133.5058 | 53.53 | 0 | 0 | 10 | 0 | 0
2012 | 2023-03-25 20:00 | 101.3614 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1630.4355
2013 | 2023-03-25 21:00 | 95.822 | 53.53 | 20 | 10 | 0 | 10 | 2987.039
2014 | 2023-03-25 22:00 | 111.1818 | 53.53 | 0 | 0 | 10 | 0 | 0
2015 | 2023-03-25 23:00 | 92.122 | 53.53 | 10 | 0 | 0 | 0 | 1456.5205
2016 | 2023-03-26 00:00 | 90.6886 | 53.53 | 10 | 0 | 0 | 0 | 1442.1857
2017 | 2023-03-26 01:00 | 86.4057 | 53.53 | 10 | 0 | 0 | 0 | 1399.3571
2018 | 2023-03-26 02:00 | 75.6662 | 53.53 | 10 | 0 | 0 | 0 | 1291.9622
2019 | 2023-03-26 03:00 | 74.741 | 53.53 | 10 | 0 | 0 | 0 | 1282.71
2020 | 2023-03-26 04:00 | 71.0086 | 53.53 | 20 | 10 | 0 | 9.5 | 2490.773
2021 | 2023-03-26 05:00 | 65.6232 | 53.53 | 20 | 10 | 0 | 19 | 2383.0634
2022 | 2023-03-26 06:00 | 71.892 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1386.2434
2023 | 2023-03-26 07:00 | 90.3803 | 53.53 | 10 | 0 | 0 | 20 | 1439.1026
2024 | 2023-03-26 08:00 | 92.6556 | 53.53 | 10 | 0 | 0 | 20 | 1461.856
2025 | 2023-03-26 09:00 | 91.9744 | 53.53 | 10 | 0 | 0 | 20 | 1455.0438
2026 | 2023-03-26 10:00 | 105.5175 | 53.53 | 0 | 0 | 10 | 10 | 0
2027 | 2023-03-26 11:00 | 87.352 | 53.53 | 20 | 10 | 0 | 19.5 | 2817.6393
2028 | 2023-03-26 12:00 | 102.4873 | 53.53 | 10 | 0 | 0 | 19.5 | 1560.1734
2029 | 2023-03-26 13:00 | 97.558 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1590.3995
2030 | 2023-03-26 14:00 | 112.9143 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 83.2221
2031 | 2023-03-26 15:00 | 97.4582 | 53.53 | 20 | 10 | 0 | 20 | 3019.7642
2032 | 2023-03-26 16:00 | 106.3677 | 53.53 | 10 | 0 | 0 | 20 | 1598.9765
2033 | 2023-03-26 17:00 | 113.0919 | 53.53 | 10 | 0 | 0 | 20 | 1666.2186
2034 | 2023-03-26 18:00 | 116.7661 | 53.53 | 0 | 0 | 10 | 10 | 0
2035 | 2023-03-26 19:00 | 122.083 | 53.53 | 0 | 0 | 10 | 0 | 0
2036 | 2023-03-26 20:00 | 92.6591 | 53.53 | 20 | 10 | 0 | 9.5 | 2923.7817
2037 | 2023-03-26 21:00 | 104.6099 | 53.53 | 0.5 | 0 | 9.5 | 0 | 79.07
2038 | 2023-03-26 22:00 | 89.4538 | 53.53 | 20 | 10 | 0 | 9.5 | 2859.6762
2039 | 2023-03-26 23:00 | 93.2083 | 53.53 | 20 | 10 | 0 | 19 | 2934.7665
2040 | 2023-03-27 00:00 | 106.8706 | 53.53 | 0 | 0 | 10 | 9 | 0
2041 | 2023-03-27 01:00 | 104.3727 | 53.53 | 1 | 0 | 9 | 0 | 157.9027
2042 | 2023-03-27 02:00 | 98.3236 | 53.53 | 10 | 0 | 0 | 0 | 1518.5361
2043 | 2023-03-27 03:00 | 73.7809 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1407.1203
2044 | 2023-03-27 04:00 | 70.4275 | 53.53 | 20 | 10 | 0 | 10.5 | 2479.151
2045 | 2023-03-27 05:00 | 72.4503 | 53.53 | 20 | 10 | 0 | 20 | 2519.6053
2046 | 2023-03-27 06:00 | 84.3764 | 53.53 | 10 | 0 | 0 | 20 | 1379.0641
2047 | 2023-03-27 07:00 | 102.9261 | 53.53 | 10 | 0 | 0 | 20 | 1564.5607
2048 | 2023-03-27 08:00 | 109.6771 | 65.03 | 10 | 0 | 0 | 20 | 1747.0712
2049 | 2023-03-27 09:00 | 101.748 | 65.03 | 10 | 0 | 0 | 20 | 1667.7804
2050 | 2023-03-27 10:00 | 115.3652 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 90.1976
2051 | 2023-03-27 11:00 | 101.2114 | 65.03 | 20 | 10 | 0 | 20 | 3324.8284
2052 | 2023-03-27 12:00 | 119.293 | 65.03 | 1 | 0 | 9 | 11 | 184.323
2053 | 2023-03-27 13:00 | 142.814 | 65.03 | 0 | 0 | 10 | 1 | 0
2054 | 2023-03-27 14:00 | 111.8035 | 65.03 | 10 | 0 | 0 | 1 | 1768.3345
2055 | 2023-03-27 15:00 | 113.6774 | 65.03 | 10 | 0 | 0 | 1 | 1787.0745
2056 | 2023-03-27 16:00 | -71.0023 | 65.03 | 20 | 10 | 0 | 10.5 | -119.4461
2057 | 2023-03-27 17:00 | 113.4224 | 66.4 | 10 | 0 | 0 | 10.5 | 1798.2244
2058 | 2023-03-27 18:00 | 119.763 | 66.4 | 0 | 0 | 10 | 0.5 | 0
2059 | 2023-03-27 19:00 | 116.9097 | 65.03 | 10 | 0 | 0 | 0.5 | 1819.3975
2060 | 2023-03-27 20:00 | 95.0945 | 65.03 | 20 | 10 | 0 | 10 | 3202.4894
2061 | 2023-03-27 21:00 | 120.8108 | 65.03 | 0 | 0 | 10 | 0 | 0
2062 | 2023-03-27 22:00 | 106.0309 | 65.03 | 10 | 0 | 0 | 0 | 1710.6087
2063 | 2023-03-27 23:00 | 101.9145 | 53.53 | 10 | 0 | 0 | 0 | 1554.4448
2064 | 2023-03-28 00:00 | 96.6848 | 53.53 | 10 | 0 | 0 | 0 | 1502.1483
2065 | 2023-03-28 01:00 | 97.6348 | 53.53 | 10 | 0 | 0 | 0 | 1511.6482
2066 | 2023-03-28 02:00 | 87.2878 | 53.53 | 10 | 0 | 0 | 0 | 1408.1779
2067 | 2023-03-28 03:00 | 78.657 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1461.0137
2068 | 2023-03-28 04:00 | 83.2129 | 53.53 | 10 | 0 | 0 | 1 | 1367.4286
2069 | 2023-03-28 05:00 | 77.4707 | 53.53 | 20 | 10 | 0 | 10.5 | 2620.0132
2070 | 2023-03-28 06:00 | 76.4595 | 53.53 | 20 | 10 | 0 | 20 | 2599.7894
2071 | 2023-03-28 07:00 | 90.2904 | 53.53 | 10 | 0 | 0 | 20 | 1438.2044
2072 | 2023-03-28 08:00 | 97.7105 | 65.03 | 10 | 0 | 0 | 20 | 1627.4049
2073 | 2023-03-28 09:00 | 107.0116 | 65.03 | 10 | 0 | 0 | 20 | 1720.4158
2074 | 2023-03-28 10:00 | 109.3256 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.1778
2075 | 2023-03-28 11:00 | 100.8953 | 65.03 | 10 | 0 | 0 | 10.5 | 1659.2531
2076 | 2023-03-28 12:00 | 108.6411 | 65.03 | 10 | 0 | 0 | 10.5 | 1736.7108
2077 | 2023-03-28 13:00 | 109.3047 | 65.03 | 10 | 0 | 0 | 10.5 | 1743.3472
2078 | 2023-03-28 14:00 | 96.9912 | 65.03 | 20 | 10 | 0 | 20 | 3240.425
2079 | 2023-03-28 15:00 | 102.8964 | 65.03 | 10 | 0 | 0 | 20 | 1679.264
2080 | 2023-03-28 16:00 | 112.1472 | 65.03 | 10 | 0 | 0 | 20 | 1771.7722
2081 | 2023-03-28 17:00 | 126.9765 | 66.4 | 0 | 0 | 10 | 10 | 0
2082 | 2023-03-28 18:00 | 116.5843 | 66.4 | 10 | 0 | 0 | 10 | 1829.8431
2083 | 2023-03-28 19:00 | 125.1154 | 65.03 | 0 | 0 | 10 | 0 | 0
2084 | 2023-03-28 20:00 | 112.8724 | 65.03 | 10 | 0 | 0 | 0 | 1779.0239
2085 | 2023-03-28 21:00 | 110.4617 | 65.03 | 10 | 0 | 0 | 0 | 1754.9169
2086 | 2023-03-28 22:00 | 103.1938 | 65.03 | 10 | 0 | 0 | 0 | 1682.2378
2087 | 2023-03-28 23:00 | 95.6237 | 53.53 | 10 | 0 | 0 | 0 | 1491.5372
2088 | 2023-03-29 00:00 | 94.597 | 53.53 | 10 | 0 | 0 | 0 | 1481.2704
2089 | 2023-03-29 01:00 | -14.4854 | 53.53 | 20 | 10 | 0 | 9.5 | 780.8916
2090 | 2023-03-29 02:00 | 80.4053 | 53.53 | 10 | 0 | 0 | 9.5 | 1339.3526
2091 | 2023-03-29 03:00 | -70.5951 | 53.53 | 20 | 10 | 0 | 19 | -341.3012
2092 | 2023-03-29 04:00 | 79.9072 | 53.53 | 10 | 0 | 0 | 19 | 1334.3718
2093 | 2023-03-29 05:00 | 85.8589 | 53.53 | 10 | 0 | 0 | 19 | 1393.8894
2094 | 2023-03-29 06:00 | 79.6179 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1471.6348
2095 | 2023-03-29 07:00 | 105.5339 | 53.53 | 10 | 0 | 0 | 20 | 1590.6389
2096 | 2023-03-29 08:00 | 116.362 | 65.03 | 0 | 0 | 10 | 10 | 0
2097 | 2023-03-29 09:00 | 103.5373 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1774.3928
2098 | 2023-03-29 10:00 | 98.4315 | 65.03 | 20 | 10 | 0 | 20 | 3269.2292
2099 | 2023-03-29 11:00 | 123.621 | 65.03 | 0 | 0 | 10 | 10 | 0
2100 | 2023-03-29 12:00 | 110.8993 | 65.03 | 10 | 0 | 0 | 10 | 1759.2929
2101 | 2023-03-29 13:00 | 98.8456 | 65.03 | 20 | 10 | 0 | 19.5 | 3277.5119
2102 | 2023-03-29 14:00 | 104.0791 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1780.0955
2103 | 2023-03-29 15:00 | 115.4125 | 65.03 | 10 | 0 | 0 | 20 | 1804.425
2104 | 2023-03-29 16:00 | 106.8863 | 65.03 | 10 | 0 | 0 | 20 | 1719.1632
2105 | 2023-03-29 17:00 | 120.3383 | 66.4 | 0 | 0 | 10 | 10 | 0
2106 | 2023-03-29 18:00 | 136.9574 | 66.4 | 0 | 0 | 10 | 0 | 0
2107 | 2023-03-29 19:00 | 117.1579 | 65.03 | 10 | 0 | 0 | 0 | 1821.8788
2108 | 2023-03-29 20:00 | 98.5749 | 65.03 | 10 | 0 | 0 | 0 | 1636.049
2109 | 2023-03-29 21:00 | 105.5351 | 65.03 | 10 | 0 | 0 | 0 | 1705.6505
2110 | 2023-03-29 22:00 | 107.0051 | 65.03 | 10 | 0 | 0 | 0 | 1720.3513
2111 | 2023-03-29 23:00 | 102.9123 | 53.53 | 10 | 0 | 0 | 0 | 1564.4231
2112 | 2023-03-30 00:00 | 106.758 | 53.53 | 10 | 0 | 0 | 0 | 1602.8801
2113 | 2023-03-30 01:00 | 100.4329 | 53.53 | 10 | 0 | 0 | 0 | 1539.629
2114 | 2023-03-30 02:00 | 82.8518 | 53.53 | 10 | 0 | 0 | 0 | 1363.818
2115 | 2023-03-30 03:00 | 77.0279 | 53.53 | 20 | 10 | 0 | 9.5 | 2611.1581
2116 | 2023-03-30 04:00 | 79.373 | 53.53 | 20 | 10 | 0 | 19 | 2658.0599
2117 | 2023-03-30 05:00 | 79.718 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1472.7406
2118 | 2023-03-30 06:00 | 80.5647 | 53.53 | 10 | 0 | 0 | 20 | 1340.9473
2119 | 2023-03-30 07:00 | 105.4188 | 53.53 | 10 | 0 | 0 | 20 | 1589.4879
2120 | 2023-03-30 08:00 | 113.4287 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 89.2293
2121 | 2023-03-30 09:00 | 109.2321 | 65.03 | 10 | 0 | 0 | 10.5 | 1742.6214
2122 | 2023-03-30 10:00 | 103.5102 | 65.03 | 20 | 10 | 0 | 20 | 3370.8047
2123 | 2023-03-30 11:00 | 109.411 | 65.03 | 10 | 0 | 0 | 20 | 1744.4103
2124 | 2023-03-30 12:00 | 108.6891 | 65.03 | 10 | 0 | 0 | 20 | 1737.1905
2125 | 2023-03-30 13:00 | 110.39 | 65.03 | 10 | 0 | 0 | 20 | 1754.1997
2126 | 2023-03-30 14:00 | 132.3629 | 65.03 | 0 | 0 | 10 | 10 | 0
2127 | 2023-03-30 15:00 | 105.2631 | 65.03 | 20 | 10 | 0 | 19.5 | 3405.8618
2128 | 2023-03-30 16:00 | 112.2748 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1866.3667
2129 | 2023-03-30 17:00 | 133.345 | 66.4 | 0 | 0 | 10 | 10 | 0
2130 | 2023-03-30 18:00 | 124.6442 | 66.4 | 10 | 0 | 0 | 10 | 1910.4423
2131 | 2023-03-30 19:00 | 149.3103 | 65.03 | 0 | 0 | 10 | 0 | 0
2132 | 2023-03-30 20:00 | 101.2179 | 65.03 | 10 | 0 | 0 | 0 | 1662.4788
2133 | 2023-03-30 21:00 | 106.4511 | 65.03 | 10 | 0 | 0 | 0 | 1714.8106
2134 | 2023-03-30 22:00 | 98.571 | 65.03 | 10 | 0 | 0 | 0 | 1636.0105
2135 | 2023-03-30 23:00 | 96.3961 | 53.53 | 20 | 10 | 0 | 9.5 | 2998.5225
2136 | 2023-03-31 00:00 | 100.8368 | 53.53 | 10 | 0 | 0 | 9.5 | 1543.6679
2137 | 2023-03-31 01:00 | 106.1241 | 53.53 | 0.5 | 0 | 9.5 | 0 | 79.827
2138 | 2023-03-31 02:00 | 81.4098 | 53.53 | 20 | 10 | 0 | 9.5 | 2698.7962
2139 | 2023-03-31 03:00 | 90.3727 | 53.53 | 1.5 | 0 | 8.5 | 1 | 215.854
2140 | 2023-03-31 04:00 | 78.1961 | 53.53 | 20 | 10 | 0 | 10.5 | 2634.5223
2141 | 2023-03-31 05:00 | 76.5271 | 53.53 | 20 | 10 | 0 | 20 | 2601.143
2142 | 2023-03-31 06:00 | 110.1632 | 53.53 | 10 | 0 | 0 | 20 | 1636.9323
2143 | 2023-03-31 07:00 | 102.037 | 53.53 | 10 | 0 | 0 | 20 | 1555.6704
2144 | 2023-03-31 08:00 | 104.0448 | 65.03 | 10 | 0 | 0 | 20 | 1690.7482
2145 | 2023-03-31 09:00 | 104.1978 | 65.03 | 10 | 0 | 0 | 20 | 1692.2781
2146 | 2023-03-31 10:00 | 102.74 | 65.03 | 10 | 0 | 0 | 20 | 1677.6999
2147 | 2023-03-31 11:00 | 117.0087 | 65.03 | 0 | 0 | 10 | 10 | 0
2148 | 2023-03-31 12:00 | 106.3095 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1803.5742
2149 | 2023-03-31 13:00 | 109.872 | 65.03 | 10 | 0 | 0 | 10.5 | 1749.0201
2150 | 2023-03-31 14:00 | 108.4265 | 65.03 | 10 | 0 | 0 | 10.5 | 1734.565
2151 | 2023-03-31 15:00 | 115.033 | 65.03 | 10 | 0 | 0 | 10.5 | 1800.6302
2152 | 2023-03-31 16:00 | 103.2902 | 65.03 | 20 | 10 | 0 | 20 | 3366.403
2153 | 2023-03-31 17:00 | 117.0036 | 66.4 | 10 | 0 | 0 | 20 | 1834.036
2154 | 2023-03-31 18:00 | 125.6384 | 66.4 | 0 | 0 | 10 | 10 | 0
2155 | 2023-03-31 19:00 | 128.8374 | 65.03 | 0 | 0 | 10 | 0 | 0
2156 | 2023-03-31 20:00 | 106.5209 | 65.03 | 10 | 0 | 0 | 0 | 1715.5094
2157 | 2023-03-31 21:00 | 98.5083 | 65.03 | 20 | 10 | 0 | 9.5 | 3270.7661
2158 | 2023-03-31 22:00 | 109.5326 | 65.03 | 0.5 | 0 | 9.5 | 0 | 87.2813
2159 | 2023-03-31 23:00 | 93.898 | 53.53 | 10 | 0 | 0 | 0 | 1474.2801
2160 | 2023-04-01 00:00 | 72.2774 | 53.53 | 10 | 0 | 0 | 0 | 1258.0742
2161 | 2023-04-01 01:00 | 69.7328 | 53.53 | 10 | 0 | 0 | 0 | 1232.628
2162 | 2023-04-01 02:00 | 67.8357 | 53.53 | 10 | 0 | 0 | 0 | 1213.6566
2163 | 2023-04-01 03:00 | 61.1303 | 53.53 | 20 | 10 | 0 | 9.5 | 2293.2069
2164 | 2023-04-01 04:00 | 60.8736 | 53.53 | 20 | 10 | 0 | 19 | 2288.0722
2165 | 2023-04-01 05:00 | 67.2427 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1334.8559
2166 | 2023-04-01 06:00 | 89.0277 | 53.53 | 0 | 0 | 10 | 10 | 0
2167 | 2023-04-01 07:00 | 65.8692 | 53.53 | 20 | 10 | 0 | 19.5 | 2387.984
2168 | 2023-04-01 08:00 | 80.9309 | 53.53 | 10 | 0 | 0 | 19.5 | 1344.6094
2169 | 2023-04-01 09:00 | 81.679 | 53.53 | 1.5 | 0 | 8.5 | 11 | 202.8135
2170 | 2023-04-01 10:00 | 80.2665 | 53.53 | 10 | 0 | 0 | 11 | 1337.9646
2171 | 2023-04-01 11:00 | 78.9927 | 53.53 | 10 | 0 | 0 | 11 | 1325.2268
2172 | 2023-04-01 12:00 | 83.749 | 53.53 | 0 | 0 | 10 | 1 | 0
2173 | 2023-04-01 13:00 | -76.5562 | 53.53 | 20 | 10 | 0 | 10.5 | -460.5244
2174 | 2023-04-01 14:00 | -19.2308 | 53.53 | 20 | 10 | 0 | 20 | 685.984
2175 | 2023-04-01 15:00 | 86.2891 | 53.53 | 10 | 0 | 0 | 20 | 1398.1907
2176 | 2023-04-01 16:00 | 89.7793 | 53.53 | 10 | 0 | 0 | 20 | 1433.0932
2177 | 2023-04-01 17:00 | 105.0116 | 53.53 | 0 | 0 | 10 | 10 | 0
2178 | 2023-04-01 18:00 | 105.8558 | 53.53 | 0 | 0 | 10 | 0 | 0
2179 | 2023-04-01 19:00 | 98.2489 | 53.53 | 10 | 0 | 0 | 0 | 1517.7891
2180 | 2023-04-01 20:00 | 103.1373 | 53.53 | 10 | 0 | 0 | 0 | 1566.6726
2181 | 2023-04-01 21:00 | 82.7198 | 53.53 | 10 | 0 | 0 | 0 | 1362.4984
2182 | 2023-04-01 22:00 | 70.1965 | 53.53 | 10 | 0 | 0 | 0 | 1237.2646
2183 | 2023-04-01 23:00 | 69.4056 | 53.53 | 10 | 0 | 0 | 0 | 1229.3557
2184 | 2023-04-02 00:00 | 65.7294 | 53.53 | 10 | 0 | 0 | 0 | 1192.5939
2185 | 2023-04-02 01:00 | -57.5294 | 53.53 | 20 | 10 | 0 | 9.5 | -79.9881
2186 | 2023-04-02 02:00 | -55.7174 | 53.53 | 20 | 10 | 0 | 19 | -43.7478
2187 | 2023-04-02 03:00 | 52.6208 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1173.2456
2188 | 2023-04-02 04:00 | 76.6008 | 53.53 | 0 | 0 | 10 | 10 | 0
2189 | 2023-04-02 05:00 | 60.3741 | 53.53 | 20 | 10 | 0 | 19.5 | 2278.0828
2190 | 2023-04-02 06:00 | 61.9827 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1215.923
2191 | 2023-04-02 07:00 | 69.8057 | 53.53 | 10 | 0 | 0 | 20 | 1233.3571
2192 | 2023-04-02 08:00 | 79.4235 | 53.53 | 10 | 0 | 0 | 20 | 1329.5351
2193 | 2023-04-02 09:00 | 86.1759 | 53.53 | 0 | 0 | 10 | 10 | 0
2194 | 2023-04-02 10:00 | 87.2301 | 53.53 | 0 | 0 | 10 | 0 | 0
2195 | 2023-04-02 11:00 | 75.223 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1423.0591
2196 | 2023-04-02 12:00 | -69.5085 | 53.53 | 20 | 10 | 0 | 10.5 | -319.5699
2197 | 2023-04-02 13:00 | -27.1224 | 53.53 | 20 | 10 | 0 | 20 | 528.1521
2198 | 2023-04-02 14:00 | 84.3357 | 53.53 | 10 | 0 | 0 | 20 | 1378.6566
2199 | 2023-04-02 15:00 | 80.4852 | 53.53 | 10 | 0 | 0 | 20 | 1340.1516
2200 | 2023-04-02 16:00 | 82.1623 | 53.53 | 10 | 0 | 0 | 20 | 1356.923
2201 | 2023-04-02 17:00 | 99.6064 | 53.53 | 10 | 0 | 0 | 20 | 1531.3644
2202 | 2023-04-02 18:00 | 101.5887 | 53.53 | 0 | 0 | 10 | 10 | 0
2203 | 2023-04-02 19:00 | 105.8718 | 53.53 | 0 | 0 | 10 | 0 | 0
2204 | 2023-04-02 20:00 | 90.4734 | 53.53 | 10 | 0 | 0 | 0 | 1440.0337
2205 | 2023-04-02 21:00 | 78.7854 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1392.7933
2206 | 2023-04-02 22:00 | 77.7009 | 53.53 | 20 | 10 | 0 | 10 | 2624.618
2207 | 2023-04-02 23:00 | 79.406 | 53.53 | 10 | 0 | 0 | 10 | 1329.3596
2208 | 2023-04-03 00:00 | 88.9263 | 53.53 | 0 | 0 | 10 | 0 | 0
2209 | 2023-04-03 01:00 | 80.845 | 53.53 | 10 | 0 | 0 | 0 | 1343.7498
2210 | 2023-04-03 02:00 | 70.5881 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1437.1567
2211 | 2023-04-03 03:00 | -28.6051 | 53.53 | 20 | 10 | 0 | 11 | 498.4983
2212 | 2023-04-03 04:00 | 75.7308 | 53.53 | 10 | 0 | 0 | 11 | 1292.6085
2213 | 2023-04-03 05:00 | 81.5204 | 53.53 | 0 | 0 | 10 | 1 | 0
2214 | 2023-04-03 06:00 | -41.5759 | 53.53 | 20 | 10 | 0 | 10.5 | 239.0826
2215 | 2023-04-03 07:00 | -29.3651 | 53.53 | 20 | 10 | 0 | 20 | 483.2976
2216 | 2023-04-03 08:00 | 93.983 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 79.5065
2217 | 2023-04-03 09:00 | 93.1735 | 65.03 | 10 | 0 | 0 | 10.5 | 1582.0347
2218 | 2023-04-03 10:00 | 89.4737 | 65.03 | 10 | 0 | 0 | 10.5 | 1545.0372
2219 | 2023-04-03 11:00 | 84.9082 | 65.03 | 20 | 10 | 0 | 20 | 2998.7641
2220 | 2023-04-03 12:00 | 94.6032 | 65.03 | 0 | 0 | 10 | 10 | 0
2221 | 2023-04-03 13:00 | 88.7516 | 65.03 | 10 | 0 | 0 | 10 | 1537.8158
2222 | 2023-04-03 14:00 | 94.5516 | 65.03 | 10 | 0 | 0 | 10 | 1595.8165
2223 | 2023-04-03 15:00 | 88.5992 | 65.03 | 10 | 0 | 0 | 10 | 1536.2918
2224 | 2023-04-03 16:00 | 86.8732 | 65.03 | 10 | 0 | 0 | 10 | 1519.0324
2225 | 2023-04-03 17:00 | 110.7188 | 66.4 | 0 | 0 | 10 | 0 | 0
2226 | 2023-04-03 18:00 | -9.5495 | 66.4 | 20 | 10 | 0 | 9.5 | 1137.0094
2227 | 2023-04-03 19:00 | -54.8066 | 65.03 | 20 | 10 | 0 | 19 | 204.4688
2228 | 2023-04-03 20:00 | 112.0634 | 65.03 | 0 | 0 | 10 | 9 | 0
2229 | 2023-04-03 21:00 | 91.0669 | 65.03 | 10 | 0 | 0 | 9 | 1560.9693
2230 | 2023-04-03 22:00 | 92.8145 | 65.03 | 1 | 0 | 9 | 0 | 157.8445
2231 | 2023-04-03 23:00 | 76.9928 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1373.9242
2232 | 2023-04-04 00:00 | 75.8913 | 53.53 | 20 | 10 | 0 | 10 | 2588.4268
2233 | 2023-04-04 01:00 | 99.0926 | 53.53 | 0 | 0 | 10 | 0 | 0
2234 | 2023-04-04 02:00 | 57.8488 | 53.53 | 20 | 10 | 0 | 9.5 | 2227.5767
2235 | 2023-04-04 03:00 | 57.1762 | 53.53 | 20 | 10 | 0 | 19 | 2214.1241
2236 | 2023-04-04 04:00 | 63.6068 | 53.53 | 10 | 0 | 0 | 19 | 1171.3678
2237 | 2023-04-04 05:00 | 63.2309 | 53.53 | 10 | 0 | 0 | 19 | 1167.6093
2238 | 2023-04-04 06:00 | 57.9684 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1232.3513
2239 | 2023-04-04 07:00 | 81.7125 | 53.53 | 10 | 0 | 0 | 20 | 1352.4252
2240 | 2023-04-04 08:00 | 105.0487 | 65.03 | 0 | 0 | 10 | 10 | 0
2241 | 2023-04-04 09:00 | 88.5287 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1616.4071
2242 | 2023-04-04 10:00 | 85.3557 | 65.03 | 20 | 10 | 0 | 20 | 3007.7137
2243 | 2023-04-04 11:00 | 102.0686 | 65.03 | 0 | 0 | 10 | 10 | 0
2244 | 2023-04-04 12:00 | 97.8771 | 65.03 | 0 | 0 | 10 | 0 | 0
2245 | 2023-04-04 13:00 | 89.6519 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1709.6422
2246 | 2023-04-04 14:00 | 84.4509 | 65.03 | 20 | 10 | 0 | 10.5 | 2989.6175
2247 | 2023-04-04 15:00 | 88.8934 | 65.03 | 20 | 10 | 0 | 20 | 3078.4688
2248 | 2023-04-04 16:00 | 93.4914 | 65.03 | 10 | 0 | 0 | 20 | 1585.2137
2249 | 2023-04-04 17:00 | 119.3644 | 66.4 | 0 | 0 | 10 | 10 | 0
2250 | 2023-04-04 18:00 | 102.2166 | 66.4 | 10 | 0 | 0 | 10 | 1686.1662
2251 | 2023-04-04 19:00 | 108.2724 | 65.03 | 0 | 0 | 10 | 0 | 0
2252 | 2023-04-04 20:00 | 94.5111 | 65.03 | 10 | 0 | 0 | 0 | 1595.4114
2253 | 2023-04-04 21:00 | 76.1357 | 65.03 | 20 | 10 | 0 | 9.5 | 2823.3138
2254 | 2023-04-04 22:00 | 97.9886 | 65.03 | 0.5 | 0 | 9.5 | 0 | 81.5093
2255 | 2023-04-04 23:00 | 76.4323 | 53.53 | 20 | 10 | 0 | 9.5 | 2599.2457
2256 | 2023-04-05 00:00 | 86.5165 | 53.53 | 0.5 | 0 | 9.5 | 0 | 70.0232
2257 | 2023-04-05 01:00 | 85.8186 | 53.53 | 10 | 0 | 0 | 0 | 1393.4861
2258 | 2023-04-05 02:00 | 73.5121 | 53.53 | 10 | 0 | 0 | 0 | 1270.4208
2259 | 2023-04-05 03:00 | 68.3913 | 53.53 | 10 | 0 | 0 | 0 | 1219.2131
2260 | 2023-04-05 04:00 | -52.5364 | 53.53 | 20 | 10 | 0 | 9.5 | 19.8711
2261 | 2023-04-05 05:00 | -67.8737 | 53.53 | 20 | 10 | 0 | 19 | -286.8745
2262 | 2023-04-05 06:00 | -27.8781 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 283.5205
2263 | 2023-04-05 07:00 | 82.4779 | 53.53 | 10 | 0 | 0 | 20 | 1360.079
2264 | 2023-04-05 08:00 | 97.7497 | 65.03 | 10 | 0 | 0 | 20 | 1627.7972
2265 | 2023-04-05 09:00 | 100.5783 | 65.03 | 0 | 0 | 10 | 10 | 0
2266 | 2023-04-05 10:00 | 98.9047 | 65.03 | 0 | 0 | 10 | 0 | 0
2267 | 2023-04-05 11:00 | 92.3418 | 65.03 | 10 | 0 | 0 | 0 | 1573.7181
2268 | 2023-04-05 12:00 | 83.2659 | 65.03 | 20 | 10 | 0 | 9.5 | 2965.9178
2269 | 2023-04-05 13:00 | 90.7053 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1721.2851
2270 | 2023-04-05 14:00 | 97.2245 | 65.03 | 10 | 0 | 0 | 10.5 | 1622.5448
2271 | 2023-04-05 15:00 | 86.923 | 65.03 | 20 | 10 | 0 | 20 | 3039.0596
2272 | 2023-04-05 16:00 | 99.1109 | 65.03 | 10 | 0 | 0 | 20 | 1641.4088
2273 | 2023-04-05 17:00 | 116.73 | 66.4 | 0 | 0 | 10 | 10 | 0
2274 | 2023-04-05 18:00 | 109.8681 | 66.4 | 0 | 0 | 10 | 0 | 0
2275 | 2023-04-05 19:00 | 93.8699 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1672.6307
2276 | 2023-04-05 20:00 | 80.9364 | 65.03 | 20 | 10 | 0 | 10 | 2919.3272
2277 | 2023-04-05 21:00 | 107.9222 | 65.03 | 0 | 0 | 10 | 0 | 0
2278 | 2023-04-05 22:00 | 85.1177 | 65.03 | 10 | 0 | 0 | 0 | 1501.4768
2279 | 2023-04-05 23:00 | 72.684 | 53.53 | 20 | 10 | 0 | 9.5 | 2524.2804
2280 | 2023-04-06 00:00 | 95.1125 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.3212
2281 | 2023-04-06 01:00 | 83.9987 | 53.53 | 10 | 0 | 0 | 0 | 1375.2867
2282 | 2023-04-06 02:00 | 73.7241 | 53.53 | 10 | 0 | 0 | 0 | 1272.5409
2283 | 2023-04-06 03:00 | 66.0642 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1321.831
2284 | 2023-04-06 04:00 | 67.5853 | 53.53 | 10 | 0 | 0 | 1 | 1211.1529
2285 | 2023-04-06 05:00 | -22.8756 | 53.53 | 20 | 10 | 0 | 10.5 | 613.0886
2286 | 2023-04-06 06:00 | -16.3232 | 53.53 | 20 | 10 | 0 | 20 | 744.135
2287 | 2023-04-06 07:00 | 108.4049 | 53.53 | 10 | 0 | 0 | 20 | 1619.3485
2288 | 2023-04-06 08:00 | 102.3525 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 83.6913
2289 | 2023-04-06 09:00 | 84.4594 | 65.03 | 20 | 10 | 0 | 20 | 2989.7881
2290 | 2023-04-06 10:00 | 97.4831 | 65.03 | 10 | 0 | 0 | 20 | 1625.1308
2291 | 2023-04-06 11:00 | 104.108 | 65.03 | 10 | 0 | 0 | 20 | 1691.3795
2292 | 2023-04-06 12:00 | 104.7606 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 84.8953
2293 | 2023-04-06 13:00 | 90.895 | 65.03 | 20 | 10 | 0 | 20 | 3118.501
2294 | 2023-04-06 14:00 | 104.3567 | 65.03 | 10 | 0 | 0 | 20 | 1693.8667
2295 | 2023-04-06 15:00 | 101.9211 | 65.03 | 10 | 0 | 0 | 20 | 1669.5112
2296 | 2023-04-06 16:00 | 122.9873 | 65.03 | 0 | 0 | 10 | 10 | 0
2297 | 2023-04-06 17:00 | 103.8612 | 66.4 | 10 | 0 | 0 | 10 | 1702.612
2298 | 2023-04-06 18:00 | 105.3683 | 66.4 | 0 | 0 | 10 | 0 | 0
2299 | 2023-04-06 19:00 | 106.7047 | 65.03 | 10 | 0 | 0 | 0 | 1717.3468
2300 | 2023-04-06 20:00 | 85.4792 | 65.03 | 10 | 0 | 0 | 0 | 1505.0922
2301 | 2023-04-06 21:00 | 83.04 | 65.03 | 10 | 0 | 0 | 0 | 1480.7001
2302 | 2023-04-06 22:00 | 74.8126 | 65.03 | 10 | 0 | 0 | 0 | 1398.426
2303 | 2023-04-06 23:00 | 80.8417 | 53.53 | 10 | 0 | 0 | 0 | 1343.717
2304 | 2023-04-07 00:00 | 86.8278 | 53.53 | 10 | 0 | 0 | 0 | 1403.578
2305 | 2023-04-07 01:00 | 80.4598 | 53.53 | 10 | 0 | 0 | 0 | 1339.8981
2306 | 2023-04-07 02:00 | 83.5767 | 53.53 | 10 | 0 | 0 | 0 | 1371.0671
2307 | 2023-04-07 03:00 | 63.9988 | 53.53 | 20 | 10 | 0 | 9.5 | 2350.5765
2308 | 2023-04-07 04:00 | 75.7236 | 53.53 | 10 | 0 | 0 | 9.5 | 1292.5359
2309 | 2023-04-07 05:00 | 65.9379 | 53.53 | 20 | 10 | 0 | 19 | 2389.3578
2310 | 2023-04-07 06:00 | 70.9323 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1375.6361
2311 | 2023-04-07 07:00 | 86.0828 | 53.53 | 10 | 0 | 0 | 20 | 1396.1284
2312 | 2023-04-07 08:00 | 106.5927 | 65.03 | 0 | 0 | 10 | 10 | 0
2313 | 2023-04-07 09:00 | 94.3214 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1677.3831
2314 | 2023-04-07 10:00 | 97.9104 | 65.03 | 10 | 0 | 0 | 10.5 | 1629.4038
2315 | 2023-04-07 11:00 | 96.8025 | 65.03 | 10 | 0 | 0 | 10.5 | 1618.3246
2316 | 2023-04-07 12:00 | 91.827 | 65.03 | 20 | 10 | 0 | 20 | 3137.1405
2317 | 2023-04-07 13:00 | 97.1279 | 65.03 | 10 | 0 | 0 | 20 | 1621.5789
2318 | 2023-04-07 14:00 | 117.7697 | 65.03 | 0 | 0 | 10 | 10 | 0
2319 | 2023-04-07 15:00 | 91.9504 | 65.03 | 20 | 10 | 0 | 19.5 | 3139.6081
2320 | 2023-04-07 16:00 | 97.2508 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1708.219
2321 | 2023-04-07 17:00 | 120.3581 | 66.4 | 0 | 0 | 10 | 10 | 0
2322 | 2023-04-07 18:00 | 119.095 | 66.4 | 0 | 0 | 10 | 0 | 0
2323 | 2023-04-07 19:00 | 108.9863 | 65.03 | 10 | 0 | 0 | 0 | 1740.1633
2324 | 2023-04-07 20:00 | 76.1279 | 65.03 | 20 | 10 | 0 | 9.5 | 2823.1581
2325 | 2023-04-07 21:00 | 93.0901 | 65.03 | 0.5 | 0 | 9.5 | 0 | 79.06
2326 | 2023-04-07 22:00 | 76.7443 | 65.03 | 20 | 10 | 0 | 9.5 | 2835.4864
2327 | 2023-04-07 23:00 | 97.7541 | 53.53 | 0.5 | 0 | 9.5 | 0 | 75.642
2328 | 2023-04-08 00:00 | 77.2022 | 53.53 | 20 | 10 | 0 | 9.5 | 2614.6445
2329 | 2023-04-08 01:00 | 84.6415 | 53.53 | 0.5 | 0 | 9.5 | 0 | 69.0857
2330 | 2023-04-08 02:00 | 49.9707 | 53.53 | 20 | 10 | 0 | 9.5 | 2070.0142
2331 | 2023-04-08 03:00 | 46.5899 | 53.53 | 20 | 10 | 0 | 19 | 2002.3975
2332 | 2023-04-08 04:00 | 57.9325 | 53.53 | 10 | 0 | 0 | 19 | 1114.6249
2333 | 2023-04-08 05:00 | 55.6475 | 53.53 | 10 | 0 | 0 | 19 | 1091.7755
2334 | 2023-04-08 06:00 | 52.4707 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1171.5865
2335 | 2023-04-08 07:00 | 76.5414 | 53.53 | 10 | 0 | 0 | 20 | 1300.714
2336 | 2023-04-08 08:00 | 118.2445 | 53.53 | 0 | 0 | 10 | 10 | 0
2337 | 2023-04-08 09:00 | 93.0104 | 53.53 | 0 | 0 | 10 | 0 | 0
2338 | 2023-04-08 10:00 | -36.5375 | 53.53 | 20 | 10 | 0 | 9.5 | 339.851
2339 | 2023-04-08 11:00 | -17.1327 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 402.2865
2340 | 2023-04-08 12:00 | -33.0121 | 53.53 | 20 | 10 | 0 | 20 | 410.3573
2341 | 2023-04-08 13:00 | 84.5127 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 69.0213
2342 | 2023-04-08 14:00 | 74.395 | 53.53 | 20 | 10 | 0 | 20 | 2558.5007
2343 | 2023-04-08 15:00 | 84.5232 | 53.53 | 10 | 0 | 0 | 20 | 1380.5318
2344 | 2023-04-08 16:00 | 92.7916 | 53.53 | 10 | 0 | 0 | 20 | 1463.2162
2345 | 2023-04-08 17:00 | 94.5873 | 53.53 | 0 | 0 | 10 | 10 | 0
2346 | 2023-04-08 18:00 | 99.6099 | 53.53 | 0 | 0 | 10 | 0 | 0
2347 | 2023-04-08 19:00 | -17.9424 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 393.3372
2348 | 2023-04-08 20:00 | -62.9445 | 53.53 | 20 | 10 | 0 | 10.5 | -188.2891
2349 | 2023-04-08 21:00 | -56.2843 | 53.53 | 20 | 10 | 0 | 20 | -55.085
2350 | 2023-04-08 22:00 | 86.2951 | 53.53 | 0 | 0 | 10 | 10 | 0
2351 | 2023-04-08 23:00 | 81.0233 | 53.53 | 0 | 0 | 10 | 0 | 0
2352 | 2023-04-09 00:00 | 75.6205 | 53.53 | 10 | 0 | 0 | 0 | 1291.5049
2353 | 2023-04-09 01:00 | 77.4248 | 53.53 | 10 | 0 | 0 | 0 | 1309.5477
2354 | 2023-04-09 02:00 | 48.4179 | 53.53 | 20 | 10 | 0 | 9.5 | 2038.9582
2355 | 2023-04-09 03:00 | 43.8723 | 53.53 | 20 | 10 | 0 | 19 | 1948.0451
2356 | 2023-04-09 04:00 | 57.0496 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 165.8695
2357 | 2023-04-09 05:00 | -48.0396 | 53.53 | 20 | 10 | 0 | 20 | 109.8079
2358 | 2023-04-09 06:00 | 66.8313 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 60.1806
2359 | 2023-04-09 07:00 | -23.4029 | 53.53 | 20 | 10 | 0 | 20 | 602.5415
2360 | 2023-04-09 08:00 | 100.9382 | 53.53 | 0 | 0 | 10 | 10 | 0
2361 | 2023-04-09 09:00 | 79.4297 | 53.53 | 20 | 10 | 0 | 19.5 | 2659.1949
2362 | 2023-04-09 10:00 | 83.3911 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1441.2751
2363 | 2023-04-09 11:00 | 89.7733 | 53.53 | 10 | 0 | 0 | 20 | 1433.033
2364 | 2023-04-09 12:00 | 114.3323 | 53.53 | 0 | 0 | 10 | 10 | 0
2365 | 2023-04-09 13:00 | 99.8727 | 53.53 | 0 | 0 | 10 | 0 | 0
2366 | 2023-04-09 14:00 | 95.8755 | 53.53 | 10 | 0 | 0 | 0 | 1494.0546
2367 | 2023-04-09 15:00 | 83.1527 | 53.53 | 20 | 10 | 0 | 9.5 | 2733.654
2368 | 2023-04-09 16:00 | 80.0792 | 53.53 | 20 | 10 | 0 | 19 | 2672.1845
2369 | 2023-04-09 17:00 | 107.574 | 53.53 | 0 | 0 | 10 | 9 | 0
2370 | 2023-04-09 18:00 | 93.8678 | 53.53 | 10 | 0 | 0 | 9 | 1473.9783
2371 | 2023-04-09 19:00 | 99.1725 | 53.53 | 1 | 0 | 9 | 0 | 152.7025
2372 | 2023-04-09 20:00 | 80.0521 | 53.53 | 20 | 10 | 0 | 9.5 | 2671.6425
2373 | 2023-04-09 21:00 | 96.2143 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.8722
2374 | 2023-04-09 22:00 | 78.3747 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1388.4708
2375 | 2023-04-09 23:00 | 62.9247 | 53.53 | 20 | 10 | 0 | 10 | 2329.0933
2376 | 2023-04-10 00:00 | 87.9829 | 53.53 | 0 | 0 | 10 | 0 | 0
2377 | 2023-04-10 01:00 | -24.6364 | 53.53 | 20 | 10 | 0 | 9.5 | 577.8717
2378 | 2023-04-10 02:00 | 64.2201 | 53.53 | 0.5 | 0 | 9.5 | 0 | 58.875
2379 | 2023-04-10 03:00 | 63.2564 | 53.53 | 10 | 0 | 0 | 0 | 1167.8641
2380 | 2023-04-10 04:00 | -67.1701 | 53.53 | 20 | 10 | 0 | 9.5 | -272.8014
2381 | 2023-04-10 05:00 | -49.186 | 53.53 | 20 | 10 | 0 | 19 | 86.8809
2382 | 2023-04-10 06:00 | -5.0355 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 72.7417
2383 | 2023-04-10 07:00 | -25.0627 | 53.53 | 20 | 10 | 0 | 20 | 569.3461
2384 | 2023-04-10 08:00 | 99.5929 | 65.03 | 0 | 0 | 10 | 10 | 0
2385 | 2023-04-10 09:00 | 89.692 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1628.6528
2386 | 2023-04-10 10:00 | 84.3271 | 65.03 | 20 | 10 | 0 | 20 | 2987.1415
2387 | 2023-04-10 11:00 | 99.4507 | 65.03 | 10 | 0 | 0 | 20 | 1644.8068
2388 | 2023-04-10 12:00 | 103.9143 | 65.03 | 0 | 0 | 10 | 10 | 0
2389 | 2023-04-10 13:00 | 93.5631 | 65.03 | 10 | 0 | 0 | 10 | 1585.9311
2390 | 2023-04-10 14:00 | 82.7807 | 65.03 | 20 | 10 | 0 | 19.5 | 2956.2142
2391 | 2023-04-10 15:00 | 99.7955 | 65.03 | 1 | 0 | 9 | 10.5 | 164.8255
2392 | 2023-04-10 16:00 | 84.0924 | 65.03 | 20 | 10 | 0 | 20 | 2982.4488
2393 | 2023-04-10 17:00 | 111.325 | 66.4 | 0 | 0 | 10 | 10 | 0
2394 | 2023-04-10 18:00 | 103.0547 | 66.4 | 0 | 0 | 10 | 0 | 0
2395 | 2023-04-10 19:00 | 101.5516 | 65.03 | 10 | 0 | 0 | 0 | 1665.8163
2396 | 2023-04-10 20:00 | 85.7943 | 65.03 | 10 | 0 | 0 | 0 | 1508.2428
2397 | 2023-04-10 21:00 | 87.5607 | 65.03 | 10 | 0 | 0 | 0 | 1525.9069
2398 | 2023-04-10 22:00 | 84.5049 | 65.03 | 10 | 0 | 0 | 0 | 1495.3495
2399 | 2023-04-10 23:00 | 88.7275 | 53.53 | 10 | 0 | 0 | 0 | 1422.5748
2400 | 2023-04-11 00:00 | 80.767 | 53.53 | 20 | 10 | 0 | 9.5 | 2685.9395
2401 | 2023-04-11 01:00 | 92.4448 | 53.53 | 0.5 | 0 | 9.5 | 0 | 72.9874
2402 | 2023-04-11 02:00 | 66.0986 | 53.53 | 10 | 0 | 0 | 0 | 1196.286
2403 | 2023-04-11 03:00 | 59.1778 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1245.7174
2404 | 2023-04-11 04:00 | -66.9765 | 53.53 | 20 | 10 | 0 | 10.5 | -268.9295
2405 | 2023-04-11 05:00 | -17.765 | 53.53 | 20 | 10 | 0 | 20 | 715.3009
2406 | 2023-04-11 06:00 | 66.1767 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 59.8534
2407 | 2023-04-11 07:00 | -56.7913 | 53.53 | 20 | 10 | 0 | 20 | -65.225
2408 | 2023-04-11 08:00 | 81.169 | 65.03 | 10 | 0 | 0 | 20 | 1461.9904
2409 | 2023-04-11 09:00 | 90.1867 | 65.03 | 10 | 0 | 0 | 20 | 1552.1669
2410 | 2023-04-11 10:00 | 87.9769 | 65.03 | 10 | 0 | 0 | 20 | 1530.0687
2411 | 2023-04-11 11:00 | 109.0064 | 65.03 | 0 | 0 | 10 | 10 | 0
2412 | 2023-04-11 12:00 | 83.8982 | 65.03 | 20 | 10 | 0 | 19.5 | 2978.5637
2413 | 2023-04-11 13:00 | 85.122 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1580.547
2414 | 2023-04-11 14:00 | 103.7767 | 65.03 | 10 | 0 | 0 | 20 | 1688.0667
2415 | 2023-04-11 15:00 | 106.457 | 65.03 | 0 | 0 | 10 | 10 | 0
2416 | 2023-04-11 16:00 | 88.8913 | 65.03 | 20 | 10 | 0 | 19.5 | 3078.4256
2417 | 2023-04-11 17:00 | 104.58 | 66.4 | 0.5 | 0 | 9.5 | 10 | 85.49
2418 | 2023-04-11 18:00 | 113.9749 | 66.4 | 0 | 0 | 10 | 0 | 0
2419 | 2023-04-11 19:00 | 96.3362 | 65.03 | 10 | 0 | 0 | 0 | 1613.6618
2420 | 2023-04-11 20:00 | 78.202 | 65.03 | 20 | 10 | 0 | 9.5 | 2864.64
2421 | 2023-04-11 21:00 | 86.879 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1599.0424
2422 | 2023-04-11 22:00 | 103.6974 | 65.03 | 0 | 0 | 10 | 0 | 0
2423 | 2023-04-11 23:00 | 80.8349 | 53.53 | 20 | 10 | 0 | 9.5 | 2687.2983
2424 | 2023-04-12 00:00 | 84.6669 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1454.7043
2425 | 2023-04-12 01:00 | 94.0268 | 53.53 | 0 | 0 | 10 | 0 | 0
2426 | 2023-04-12 02:00 | 85.9356 | 53.53 | 10 | 0 | 0 | 0 | 1394.6562
2427 | 2023-04-12 03:00 | 59.9256 | 53.53 | 20 | 10 | 0 | 9.5 | 2269.112
2428 | 2023-04-12 04:00 | 63.7723 | 53.53 | 20 | 10 | 0 | 19 | 2346.047
2429 | 2023-04-12 05:00 | 82.0833 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 203.4199
2430 | 2023-04-12 06:00 | 54.7332 | 53.53 | 20 | 10 | 0 | 20 | 2165.264
2431 | 2023-04-12 07:00 | 92.9252 | 53.53 | 10 | 0 | 0 | 20 | 1464.5516
2432 | 2023-04-12 08:00 | 87.3173 | 65.03 | 10 | 0 | 0 | 20 | 1523.4728
2433 | 2023-04-12 09:00 | 94.6788 | 65.03 | 10 | 0 | 0 | 20 | 1597.0878
2434 | 2023-04-12 10:00 | 92.1433 | 65.03 | 10 | 0 | 0 | 20 | 1571.7331
2435 | 2023-04-12 11:00 | 87.6535 | 65.03 | 10 | 0 | 0 | 20 | 1526.8353
2436 | 2023-04-12 12:00 | 87.5129 | 65.03 | 10 | 0 | 0 | 20 | 1525.4289
2437 | 2023-04-12 13:00 | 96.0598 | 65.03 | 10 | 0 | 0 | 20 | 1610.898
2438 | 2023-04-12 14:00 | 102.5996 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 83.8148
2439 | 2023-04-12 15:00 | 92.944 | 65.03 | 20 | 10 | 0 | 20 | 3159.4795
2440 | 2023-04-12 16:00 | 94.4297 | 65.03 | 10 | 0 | 0 | 20 | 1594.5972
2441 | 2023-04-12 17:00 | 113.571 | 66.4 | 0 | 0 | 10 | 10 | 0
2442 | 2023-04-12 18:00 | 102.5771 | 66.4 | 10.5263 | 0.52632 | 0 | 10.5 | 1778.7066
2443 | 2023-04-12 19:00 | 115.1097 | 65.03 | 0 | 0 | 10 | 0.5 | 0
2444 | 2023-04-12 20:00 | 95.8645 | 65.03 | 20 | 10 | 0 | 10 | 3217.8899
2445 | 2023-04-12 21:00 | 118.4945 | 65.03 | 0 | 0 | 10 | 0 | 0
2446 | 2023-04-12 22:00 | 86.2308 | 65.03 | 10 | 0 | 0 | 0 | 1512.6084
2447 | 2023-04-12 23:00 | 80.6883 | 53.53 | 20 | 10 | 0 | 9.5 | 2684.3662
2448 | 2023-04-13 00:00 | 90.385 | 53.53 | 10 | 0 | 0 | 9.5 | 1439.1502
2449 | 2023-04-13 01:00 | 90.8622 | 53.53 | 0.5 | 0 | 9.5 | 0 | 72.1961
2450 | 2023-04-13 02:00 | 60.1907 | 53.53 | 20 | 10 | 0 | 9.5 | 2274.4139
2451 | 2023-04-13 03:00 | 61.0503 | 53.53 | 11.5789 | 1.5789 | 0 | 11 | 1326.7191
2452 | 2023-04-13 04:00 | 68.3048 | 53.53 | 0 | 0 | 10 | 1 | 0
2453 | 2023-04-13 05:00 | 58.4019 | 53.53 | 20 | 10 | 0 | 10.5 | 2238.6387
2454 | 2023-04-13 06:00 | -64.0671 | 53.53 | 20 | 10 | 0 | 20 | -210.7427
2455 | 2023-04-13 07:00 | 84.5794 | 53.53 | 10 | 0 | 0 | 20 | 1381.0936
2456 | 2023-04-13 08:00 | 102.6037 | 65.03 | 0 | 0 | 10 | 10 | 0
2457 | 2023-04-13 09:00 | 89.7513 | 65.03 | 10 | 0 | 0 | 10 | 1547.8127
2458 | 2023-04-13 10:00 | 83.2829 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1561.1888
2459 | 2023-04-13 11:00 | 82.9662 | 65.03 | 20 | 10 | 0 | 20 | 2959.9244
2460 | 2023-04-13 12:00 | 86.0321 | 65.03 | 10 | 0 | 0 | 20 | 1510.6209
2461 | 2023-04-13 13:00 | 85.758 | 65.03 | 10 | 0 | 0 | 20 | 1507.88
2462 | 2023-04-13 14:00 | 92.7652 | 65.03 | 10 | 0 | 0 | 20 | 1577.9521
2463 | 2023-04-13 15:00 | 86.3985 | 65.03 | 10 | 0 | 0 | 20 | 1514.285
2464 | 2023-04-13 16:00 | 89.1462 | 65.03 | 10 | 0 | 0 | 20 | 1541.7617
2465 | 2023-04-13 17:00 | 103.7175 | 66.4 | 10 | 0 | 0 | 20 | 1701.1748
2466 | 2023-04-13 18:00 | 105.8035 | 66.4 | 0 | 0 | 10 | 10 | 0
2467 | 2023-04-13 19:00 | 121.073 | 65.03 | 0 | 0 | 10 | 0 | 0
2468 | 2023-04-13 20:00 | 94.3902 | 65.03 | 10 | 0 | 0 | 0 | 1594.2018
2469 | 2023-04-13 21:00 | 89.0196 | 65.03 | 10 | 0 | 0 | 0 | 1540.4957
2470 | 2023-04-13 22:00 | 85.6691 | 65.03 | 10 | 0 | 0 | 0 | 1506.9907
2471 | 2023-04-13 23:00 | 80.8514 | 53.53 | 10 | 0 | 0 | 0 | 1343.8135
2472 | 2023-04-14 00:00 | 86.4813 | 53.53 | 10 | 0 | 0 | 0 | 1400.1131
2473 | 2023-04-14 01:00 | -21.3119 | 53.53 | 20 | 10 | 0 | 9.5 | 644.362
2474 | 2023-04-14 02:00 | 57.9392 | 53.53 | 0.5 | 0 | 9.5 | 0 | 55.7346
2475 | 2023-04-14 03:00 | -15.4061 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 421.3698
2476 | 2023-04-14 04:00 | -79.5261 | 53.53 | 20 | 10 | 0 | 10.5 | -519.9226
2477 | 2023-04-14 05:00 | -34.7382 | 53.53 | 20 | 10 | 0 | 20 | 375.8351
2478 | 2023-04-14 06:00 | 70.3207 | 53.53 | 10 | 0 | 0 | 20 | 1238.5069
2479 | 2023-04-14 07:00 | 81.8836 | 53.53 | 10 | 0 | 0 | 20 | 1354.1361
2480 | 2023-04-14 08:00 | 112.0117 | 65.03 | 0 | 0 | 10 | 10 | 0
2481 | 2023-04-14 09:00 | 88.0905 | 65.03 | 10 | 0 | 0 | 10 | 1531.2051
2482 | 2023-04-14 10:00 | 95.5835 | 65.03 | 0 | 0 | 10 | 0 | 0
2483 | 2023-04-14 11:00 | 93.6311 | 65.03 | 10 | 0 | 0 | 0 | 1586.6106
2484 | 2023-04-14 12:00 | 93.1573 | 65.03 | 10 | 0 | 0 | 0 | 1581.8728
2485 | 2023-04-14 13:00 | -14.2519 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 561.2313
2486 | 2023-04-14 14:00 | -34.9313 | 65.03 | 20 | 10 | 0 | 10.5 | 601.9745
2487 | 2023-04-14 15:00 | -32.9334 | 65.03 | 20 | 10 | 0 | 20 | 641.932
2488 | 2023-04-14 16:00 | 106.6941 | 65.03 | 0 | 0 | 10 | 10 | 0
2489 | 2023-04-14 17:00 | -44.3211 | 66.4 | 20 | 10 | 0 | 19.5 | 441.5777
2490 | 2023-04-14 18:00 | 115.8259 | 66.4 | 0 | 0 | 10 | 9.5 | 0
2491 | 2023-04-14 19:00 | 104.1522 | 65.03 | 0.5 | 0 | 9.5 | 0 | 84.5911
2492 | 2023-04-14 20:00 | 95.3566 | 65.03 | 10 | 0 | 0 | 0 | 1603.8659
2493 | 2023-04-14 21:00 | 83.7895 | 65.03 | 20 | 10 | 0 | 9.5 | 2976.3905
2494 | 2023-04-14 22:00 | 98.5752 | 65.03 | 0.5 | 0 | 9.5 | 0 | 81.8026
2495 | 2023-04-14 23:00 | 107.4228 | 53.53 | 10 | 0 | 0 | 0 | 1609.5277
2496 | 2023-04-15 00:00 | 74.9992 | 53.53 | 10 | 0 | 0 | 0 | 1285.2924
2497 | 2023-04-15 01:00 | 63.8485 | 53.53 | 10 | 0 | 0 | 0 | 1173.7853
2498 | 2023-04-15 02:00 | 52.1079 | 53.53 | 20 | 10 | 0 | 9.5 | 2112.7581
2499 | 2023-04-15 03:00 | 67.0758 | 53.53 | 0.5 | 0 | 9.5 | 0 | 60.3029
2500 | 2023-04-15 04:00 | 60.4104 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1259.3408
2501 | 2023-04-15 05:00 | 57.8366 | 53.53 | 20 | 10 | 0 | 10.5 | 2227.3326
2502 | 2023-04-15 06:00 | -47.839 | 53.53 | 20 | 10 | 0 | 20 | 113.8195
2503 | 2023-04-15 07:00 | 79.809 | 53.53 | 10 | 0 | 0 | 20 | 1333.3901
2504 | 2023-04-15 08:00 | 96.9226 | 53.53 | 0 | 0 | 10 | 10 | 0
2505 | 2023-04-15 09:00 | -17.4657 | 53.53 | 20 | 10 | 0 | 19.5 | 721.2867
2506 | 2023-04-15 10:00 | 100.3622 | 53.53 | 0 | 0 | 10 | 9.5 | 0
2507 | 2023-04-15 11:00 | 88.7394 | 53.53 | 10 | 0 | 0 | 9.5 | 1422.6944
2508 | 2023-04-15 12:00 | 93.6991 | 53.53 | 1.5 | 0 | 8.5 | 1 | 220.8437
2509 | 2023-04-15 13:00 | 83.6978 | 53.53 | 20 | 10 | 0 | 10.5 | 2744.5557
2510 | 2023-04-15 14:00 | 81.7709 | 53.53 | 20 | 10 | 0 | 20 | 2706.0182
2511 | 2023-04-15 15:00 | 102.6152 | 53.53 | 0 | 0 | 10 | 10 | 0
2512 | 2023-04-15 16:00 | 87.5736 | 53.53 | 20 | 10 | 0 | 19.5 | 2822.0717
2513 | 2023-04-15 17:00 | 107.7261 | 53.53 | 0 | 0 | 10 | 9.5 | 0
2514 | 2023-04-15 18:00 | 101.8438 | 53.53 | 0.5 | 0 | 9.5 | 0 | 77.6869
2515 | 2023-04-15 19:00 | 96.8647 | 53.53 | 10 | 0 | 0 | 0 | 1503.9471
2516 | 2023-04-15 20:00 | 80.9808 | 53.53 | 20 | 10 | 0 | 9.5 | 2690.2163
2517 | 2023-04-15 21:00 | 94.3604 | 53.53 | 0.5 | 0 | 9.5 | 0 | 73.9452
2518 | 2023-04-15 22:00 | 85.4295 | 53.53 | 10 | 0 | 0 | 0 | 1389.5952
2519 | 2023-04-15 23:00 | 65.8591 | 53.53 | 20 | 10 | 0 | 9.5 | 2387.7822
2520 | 2023-04-16 00:00 | 74.335 | 53.53 | 0.5 | 0 | 9.5 | 0 | 63.9325
2521 | 2023-04-16 01:00 | -36.5383 | 53.53 | 20 | 10 | 0 | 9.5 | 339.8338
2522 | 2023-04-16 02:00 | -33.4042 | 53.53 | 20 | 10 | 0 | 19 | 402.5152
2523 | 2023-04-16 03:00 | 45.4649 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1094.1544
2524 | 2023-04-16 04:00 | 75.0129 | 53.53 | 0 | 0 | 10 | 10 | 0
2525 | 2023-04-16 05:00 | 61.5778 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1211.6608
2526 | 2023-04-16 06:00 | -62.295 | 53.53 | 20 | 10 | 0 | 20 | -175.2993
2527 | 2023-04-16 07:00 | 73.2623 | 53.53 | 10 | 0 | 0 | 20 | 1267.9226
2528 | 2023-04-16 08:00 | 95.4889 | 53.53 | 0 | 0 | 10 | 10 | 0
2529 | 2023-04-16 09:00 | 82.1467 | 53.53 | 20 | 10 | 0 | 19.5 | 2713.5338
2530 | 2023-04-16 10:00 | 96.1796 | 53.53 | 0 | 0 | 10 | 9.5 | 0
2531 | 2023-04-16 11:00 | 90.3142 | 53.53 | 10 | 0 | 0 | 9.5 | 1438.4418
2532 | 2023-04-16 12:00 | 87.8025 | 53.53 | 10 | 0 | 0 | 9.5 | 1413.3245
2533 | 2023-04-16 13:00 | 87.0138 | 53.53 | 10 | 0 | 0 | 9.5 | 1405.4384
2534 | 2023-04-16 14:00 | 84.6199 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1454.2094
2535 | 2023-04-16 15:00 | 95.11 | 53.53 | 0 | 0 | 10 | 0 | 0
2536 | 2023-04-16 16:00 | 80.1823 | 53.53 | 10 | 0 | 0 | 0 | 1337.1225
2537 | 2023-04-16 17:00 | -46.5382 | 53.53 | 20 | 10 | 0 | 9.5 | 139.8355
2538 | 2023-04-16 18:00 | -59.8861 | 53.53 | 20 | 10 | 0 | 19 | -127.1215
2539 | 2023-04-16 19:00 | -19.1697 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 379.772
2540 | 2023-04-16 20:00 | 84.7725 | 53.53 | 0 | 0 | 10 | 10 | 0
2541 | 2023-04-16 21:00 | 84.1512 | 53.53 | 0.5 | 0 | 9.5 | 0.5 | 68.8406
2542 | 2023-04-16 22:00 | 78.6062 | 53.53 | 10 | 0 | 0 | 0.5 | 1321.3622
2543 | 2023-04-16 23:00 | 82.5604 | 53.53 | 10 | 0 | 0 | 0.5 | 1360.9041
2544 | 2023-04-17 00:00 | 83.5589 | 53.53 | 10 | 0 | 0 | 0.5 | 1370.8894
2545 | 2023-04-17 01:00 | 80.4994 | 53.53 | 10 | 0 | 0 | 0.5 | 1340.2935
2546 | 2023-04-17 02:00 | 61.6652 | 53.53 | 20 | 10 | 0 | 10 | 2303.9044
2547 | 2023-04-17 03:00 | 84.7342 | 53.53 | 0 | 0 | 10 | 0 | 0
2548 | 2023-04-17 04:00 | 53.754 | 53.53 | 20 | 10 | 0 | 9.5 | 2145.6799
2549 | 2023-04-17 05:00 | 67.9423 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1342.5888
2550 | 2023-04-17 06:00 | 54.0051 | 53.53 | 20 | 10 | 0 | 20 | 2150.7014
2551 | 2023-04-17 07:00 | 83.0996 | 53.53 | 10 | 0 | 0 | 20 | 1366.2959
2552 | 2023-04-17 08:00 | 90.8488 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 77.9394
2553 | 2023-04-17 09:00 | -52.2913 | 65.03 | 20 | 10 | 0 | 20 | 254.7733
2554 | 2023-04-17 10:00 | 96.9932 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 81.0116
2555 | 2023-04-17 11:00 | 91.2045 | 65.03 | 10 | 0 | 0 | 10.5 | 1562.345
2556 | 2023-04-17 12:00 | 82.2163 | 65.03 | 20 | 10 | 0 | 20 | 2944.9254
2557 | 2023-04-17 13:00 | 101.059 | 65.03 | 10 | 0 | 0 | 20 | 1660.8904
2558 | 2023-04-17 14:00 | 107.349 | 65.03 | 10 | 0 | 0 | 20 | 1723.7904
2559 | 2023-04-17 15:00 | 107.9901 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 86.5101
2560 | 2023-04-17 16:00 | 96.7408 | 65.03 | 20 | 10 | 0 | 20 | 3235.4156
2561 | 2023-04-17 17:00 | 109.2461 | 66.4 | 10 | 0 | 0 | 20 | 1756.4614
2562 | 2023-04-17 18:00 | 121.136 | 66.4 | 0 | 0 | 10 | 10 | 0
2563 | 2023-04-17 19:00 | 125.3111 | 65.03 | 0 | 0 | 10 | 0 | 0
2564 | 2023-04-17 20:00 | 99.0245 | 65.03 | 10 | 0 | 0 | 0 | 1640.5448
2565 | 2023-04-17 21:00 | 82.7465 | 65.03 | 10 | 0 | 0 | 0 | 1477.7645
2566 | 2023-04-17 22:00 | 90.4549 | 65.03 | 10 | 0 | 0 | 0 | 1554.8493
2567 | 2023-04-17 23:00 | 87.4219 | 53.53 | 10 | 0 | 0 | 0 | 1409.5187
2568 | 2023-04-18 00:00 | 73.425 | 53.53 | 20 | 10 | 0 | 9.5 | 2539.1008
2569 | 2023-04-18 01:00 | 87.6784 | 53.53 | 10 | 0 | 0 | 9.5 | 1412.084
2570 | 2023-04-18 02:00 | 88.339 | 53.53 | 0.5 | 0 | 9.5 | 0 | 70.9345
2571 | 2023-04-18 03:00 | -30.1009 | 53.53 | 20 | 10 | 0 | 9.5 | 468.5823
2572 | 2023-04-18 04:00 | 77.7946 | 53.53 | 1.5 | 0 | 8.5 | 1 | 196.9869
2573 | 2023-04-18 05:00 | 65.3085 | 53.53 | 20 | 10 | 0 | 10.5 | 2376.7701
2574 | 2023-04-18 06:00 | 63.3552 | 53.53 | 20 | 10 | 0 | 20 | 2337.7031
2575 | 2023-04-18 07:00 | 86.9278 | 53.53 | 10 | 0 | 0 | 20 | 1404.578
2576 | 2023-04-18 08:00 | 88.4709 | 65.03 | 10 | 0 | 0 | 20 | 1535.0085
2577 | 2023-04-18 09:00 | 87.6211 | 65.03 | 10 | 0 | 0 | 20 | 1526.5113
2578 | 2023-04-18 10:00 | 105.4514 | 65.03 | 0 | 0 | 10 | 10 | 0
2579 | 2023-04-18 11:00 | 106.6329 | 65.03 | 0 | 0 | 10 | 0 | 0
2580 | 2023-04-18 12:00 | 87.4682 | 65.03 | 20 | 10 | 0 | 9.5 | 3049.9648
2581 | 2023-04-18 13:00 | 102.3223 | 65.03 | 10 | 0 | 0 | 9.5 | 1673.5235
2582 | 2023-04-18 14:00 | 93.2545 | 65.03 | 20 | 10 | 0 | 19 | 3165.6908
2583 | 2023-04-18 15:00 | 96.5813 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1786.2302
2584 | 2023-04-18 16:00 | 97.5996 | 65.03 | 10 | 0 | 0 | 20 | 1626.2958
2585 | 2023-04-18 17:00 | 117.5876 | 66.4 | 0 | 0 | 10 | 10 | 0
2586 | 2023-04-18 18:00 | 109.5265 | 66.4 | 10 | 0 | 0 | 10 | 1759.2645
2587 | 2023-04-18 19:00 | 122.0635 | 65.03 | 0 | 0 | 10 | 0 | 0
2588 | 2023-04-18 20:00 | 91.33 | 65.03 | 10 | 0 | 0 | 0 | 1563.6002
2589 | 2023-04-18 21:00 | 94.0467 | 65.03 | 10 | 0 | 0 | 0 | 1590.7668
2590 | 2023-04-18 22:00 | 83.3687 | 65.03 | 20 | 10 | 0 | 9.5 | 2967.9748
2591 | 2023-04-18 23:00 | 106.6719 | 53.53 | 0.5 | 0 | 9.5 | 0 | 80.101
2592 | 2023-04-19 00:00 | 87.6824 | 53.53 | 10 | 0 | 0 | 0 | 1412.1241
2593 | 2023-04-19 01:00 | 89.8608 | 53.53 | 10 | 0 | 0 | 0 | 1433.9075
2594 | 2023-04-19 02:00 | 54.3299 | 53.53 | 20 | 10 | 0 | 9.5 | 2157.199
2595 | 2023-04-19 03:00 | 58.4305 | 53.53 | 20 | 10 | 0 | 19 | 2239.2104
2596 | 2023-04-19 04:00 | 75.1411 | 53.53 | 0 | 0 | 10 | 9 | 0
2597 | 2023-04-19 05:00 | 66.1453 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1385.714
2598 | 2023-04-19 06:00 | 52.9781 | 53.53 | 20 | 10 | 0 | 20 | 2130.1623
2599 | 2023-04-19 07:00 | 93.0347 | 53.53 | 10 | 0 | 0 | 20 | 1465.6466
2600 | 2023-04-19 08:00 | 90.1352 | 65.03 | 10 | 0 | 0 | 20 | 1551.6522
2601 | 2023-04-19 09:00 | 107.0767 | 65.03 | 0 | 0 | 10 | 10 | 0
2602 | 2023-04-19 10:00 | 93.2481 | 65.03 | 10 | 0 | 0 | 10 | 1582.7814
2603 | 2023-04-19 11:00 | 95.4817 | 65.03 | 10 | 0 | 0 | 10 | 1605.1173
2604 | 2023-04-19 12:00 | 104.506 | 65.03 | 0 | 0 | 10 | 0 | 0
2605 | 2023-04-19 13:00 | 87.9972 | 65.03 | 20 | 10 | 0 | 9.5 | 3060.543
2606 | 2023-04-19 14:00 | 87.4585 | 65.03 | 20 | 10 | 0 | 19 | 3049.771
2607 | 2023-04-19 15:00 | 92.4672 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1740.7581
2608 | 2023-04-19 16:00 | 100.9397 | 65.03 | 10 | 0 | 0 | 20 | 1659.6967
2609 | 2023-04-19 17:00 | 100.6687 | 66.4 | 0 | 0 | 10 | 10 | 0
2610 | 2023-04-19 18:00 | 99.0554 | 66.4 | 10 | 0 | 0 | 10 | 1654.5535
2611 | 2023-04-19 19:00 | 115.9065 | 65.03 | 0 | 0 | 10 | 0 | 0
2612 | 2023-04-19 20:00 | 84.7614 | 65.03 | 10 | 0 | 0 | 0 | 1497.9141
2613 | 2023-04-19 21:00 | 86.1231 | 65.03 | 10 | 0 | 0 | 0 | 1511.5309
2614 | 2023-04-19 22:00 | 78.2208 | 65.03 | 10 | 0 | 0 | 0 | 1432.5082
2615 | 2023-04-19 23:00 | 79.2911 | 53.53 | 20 | 10 | 0 | 9.5 | 2656.4222
2616 | 2023-04-20 00:00 | 83.8416 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1446.017
2617 | 2023-04-20 01:00 | 91.9472 | 53.53 | 0 | 0 | 10 | 0 | 0
2618 | 2023-04-20 02:00 | 58.7345 | 53.53 | 20 | 10 | 0 | 9.5 | 2245.2894
2619 | 2023-04-20 03:00 | 80.0016 | 53.53 | 1.5 | 0 | 8.5 | 1 | 200.2974
2620 | 2023-04-20 04:00 | 59.257 | 53.53 | 20 | 10 | 0 | 10.5 | 2255.7404
2621 | 2023-04-20 05:00 | 59.266 | 53.53 | 20 | 10 | 0 | 20 | 2255.9193
2622 | 2023-04-20 06:00 | 78.548 | 53.53 | 10 | 0 | 0 | 20 | 1320.7799
2623 | 2023-04-20 07:00 | 85.5356 | 53.53 | 10 | 0 | 0 | 20 | 1390.6564
2624 | 2023-04-20 08:00 | 90.0828 | 65.03 | 10 | 0 | 0 | 20 | 1551.1278
2625 | 2023-04-20 09:00 | 92.7615 | 65.03 | 10 | 0 | 0 | 20 | 1577.9147
2626 | 2023-04-20 10:00 | 106.4154 | 65.03 | 0 | 0 | 10 | 10 | 0
2627 | 2023-04-20 11:00 | 107.7106 | 65.03 | 0 | 0 | 10 | 0 | 0
2628 | 2023-04-20 12:00 | 88.4652 | 65.03 | 20 | 10 | 0 | 9.5 | 3069.9035
2629 | 2023-04-20 13:00 | 93.5821 | 65.03 | 10 | 0 | 0 | 9.5 | 1586.1207
2630 | 2023-04-20 14:00 | 94.5837 | 65.03 | 10 | 0 | 0 | 9.5 | 1596.1371
2631 | 2023-04-20 15:00 | 87.4954 | 65.03 | 20 | 10 | 0 | 19 | 3050.5074
2632 | 2023-04-20 16:00 | 93.4841 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1751.9984
2633 | 2023-04-20 17:00 | 108.9383 | 66.4 | 10 | 0 | 0 | 20 | 1753.3826
2634 | 2023-04-20 18:00 | 119.0945 | 66.4 | 0 | 0 | 10 | 10 | 0
2635 | 2023-04-20 19:00 | 119.8114 | 65.03 | 0 | 0 | 10 | 0 | 0
2636 | 2023-04-20 20:00 | 86.5472 | 65.03 | 10 | 0 | 0 | 0 | 1515.7724
2637 | 2023-04-20 21:00 | 87.3441 | 65.03 | 10 | 0 | 0 | 0 | 1523.7407
2638 | 2023-04-20 22:00 | 94.4116 | 65.03 | 10 | 0 | 0 | 0 | 1594.4163
2639 | 2023-04-20 23:00 | -65.2638 | 53.53 | 20 | 10 | 0 | 9.5 | -234.6751
2640 | 2023-04-21 00:00 | 88.7269 | 53.53 | 0.5 | 0 | 9.5 | 0 | 71.1285
2641 | 2023-04-21 01:00 | 83.2476 | 53.53 | 10 | 0 | 0 | 0 | 1367.7762
2642 | 2023-04-21 02:00 | 57.5896 | 53.53 | 20 | 10 | 0 | 9.5 | 2222.3914
2643 | 2023-04-21 03:00 | 57.6601 | 53.53 | 20 | 10 | 0 | 19 | 2223.8028
2644 | 2023-04-21 04:00 | 77.4883 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 196.5275
2645 | 2023-04-21 05:00 | 62.7522 | 53.53 | 20 | 10 | 0 | 20 | 2325.6449
2646 | 2023-04-21 06:00 | 79.7923 | 53.53 | 10 | 0 | 0 | 20 | 1333.2225
2647 | 2023-04-21 07:00 | 80.3282 | 53.53 | 10 | 0 | 0 | 20 | 1338.5816
2648 | 2023-04-21 08:00 | 96.1806 | 65.03 | 1 | 0 | 9 | 11 | 161.2106
2649 | 2023-04-21 09:00 | 120.1464 | 65.03 | 0 | 0 | 10 | 1 | 0
2650 | 2023-04-21 10:00 | 87.1026 | 65.03 | 20 | 10 | 0 | 10.5 | 3042.6528
2651 | 2023-04-21 11:00 | 83.0457 | 65.03 | 20 | 10 | 0 | 20 | 2961.5143
2652 | 2023-04-21 12:00 | 105.6746 | 65.03 | 0 | 0 | 10 | 10 | 0
2653 | 2023-04-21 13:00 | 88.4065 | 65.03 | 20 | 10 | 0 | 19.5 | 3068.7294
2654 | 2023-04-21 14:00 | 93.7435 | 65.03 | 10 | 0 | 0 | 19.5 | 1587.7349
2655 | 2023-04-21 15:00 | 89.8685 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1630.5101
2656 | 2023-04-21 16:00 | 95.9926 | 65.03 | 10 | 0 | 0 | 20 | 1610.2264
2657 | 2023-04-21 17:00 | 102.6956 | 66.4 | 10 | 0 | 0 | 20 | 1690.9564
2658 | 2023-04-21 18:00 | 107.5845 | 66.4 | 0 | 0 | 10 | 10 | 0
2659 | 2023-04-21 19:00 | 112.5101 | 65.03 | 0 | 0 | 10 | 0 | 0
2660 | 2023-04-21 20:00 | 82.3727 | 65.03 | 10 | 0 | 0 | 0 | 1474.0265
2661 | 2023-04-21 21:00 | 84.1624 | 65.03 | 10 | 0 | 0 | 0 | 1491.924
2662 | 2023-04-21 22:00 | 86.4241 | 65.03 | 10 | 0 | 0 | 0 | 1514.541
2663 | 2023-04-21 23:00 | 75.1831 | 53.53 | 10 | 0 | 0 | 0 | 1287.1309
2664 | 2023-04-22 00:00 | 72.9218 | 53.53 | 10 | 0 | 0 | 0 | 1264.5175
2665 | 2023-04-22 01:00 | 76.8053 | 53.53 | 10 | 0 | 0 | 0 | 1303.3535
2666 | 2023-04-22 02:00 | 53.0743 | 53.53 | 20 | 10 | 0 | 9.5 | 2132.0864
2667 | 2023-04-22 03:00 | 53.9436 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1187.8664
2668 | 2023-04-22 04:00 | 55.7495 | 53.53 | 10 | 0 | 0 | 10.5 | 1092.7949
2669 | 2023-04-22 05:00 | 51.4338 | 53.53 | 20 | 10 | 0 | 20 | 2099.2752
2670 | 2023-04-22 06:00 | 61.6577 | 53.53 | 10 | 0 | 0 | 20 | 1151.8767
2671 | 2023-04-22 07:00 | 89.3602 | 53.53 | 10 | 0 | 0 | 20 | 1428.9025
2672 | 2023-04-22 08:00 | 82.6472 | 53.53 | 10 | 0 | 0 | 20 | 1361.7717
2673 | 2023-04-22 09:00 | 89.8155 | 53.53 | 10 | 0 | 0 | 20 | 1433.4547
2674 | 2023-04-22 10:00 | 84.1643 | 53.53 | 10 | 0 | 0 | 20 | 1376.9425
2675 | 2023-04-22 11:00 | 88.7954 | 53.53 | 10 | 0 | 0 | 20 | 1423.2539
2676 | 2023-04-22 12:00 | 100.8875 | 53.53 | 0 | 0 | 10 | 10 | 0
2677 | 2023-04-22 13:00 | 90.0197 | 53.53 | 10 | 0 | 0 | 10 | 1435.4972
2678 | 2023-04-22 14:00 | 75.5837 | 53.53 | 20 | 10 | 0 | 19.5 | 2582.2734
2679 | 2023-04-22 15:00 | 89.546 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1506.0636
2680 | 2023-04-22 16:00 | 97.0866 | 53.53 | 10 | 0 | 0 | 20 | 1506.1657
2681 | 2023-04-22 17:00 | 99.2904 | 53.53 | 0 | 0 | 10 | 10 | 0
2682 | 2023-04-22 18:00 | 109.6006 | 53.53 | 0 | 0 | 10 | 0 | 0
2683 | 2023-04-22 19:00 | 96.2231 | 53.53 | 10 | 0 | 0 | 0 | 1497.5309
2684 | 2023-04-22 20:00 | 71.9083 | 53.53 | 20 | 10 | 0 | 9.5 | 2508.7663
2685 | 2023-04-22 21:00 | 81.9798 | 53.53 | 0.5 | 0 | 9.5 | 0 | 67.7549
2686 | 2023-04-22 22:00 | 70.6585 | 53.53 | 20 | 10 | 0 | 9.5 | 2483.7697
2687 | 2023-04-22 23:00 | 74.1632 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1344.1387
2688 | 2023-04-23 00:00 | 87.6774 | 53.53 | 0 | 0 | 10 | 0 | 0
2689 | 2023-04-23 01:00 | 64.9951 | 53.53 | 10 | 0 | 0 | 0 | 1185.2509
2690 | 2023-04-23 02:00 | 47.9292 | 53.53 | 20 | 10 | 0 | 9.5 | 2029.1833
2691 | 2023-04-23 03:00 | 49.2416 | 53.53 | 20 | 10 | 0 | 19 | 2055.4328
2692 | 2023-04-23 04:00 | 55.4279 | 53.53 | 10 | 0 | 0 | 19 | 1089.5789
2693 | 2023-04-23 05:00 | 53.3005 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1180.7586
2694 | 2023-04-23 06:00 | 68.9375 | 53.53 | 10 | 0 | 0 | 20 | 1224.6749
2695 | 2023-04-23 07:00 | 84.1858 | 53.53 | 10 | 0 | 0 | 20 | 1377.1575
2696 | 2023-04-23 08:00 | 89.903 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 71.7165
2697 | 2023-04-23 09:00 | 87.0147 | 53.53 | 10 | 0 | 0 | 10.5 | 1405.4474
2698 | 2023-04-23 10:00 | 89.0285 | 53.53 | 10 | 0 | 0 | 10.5 | 1425.5853
2699 | 2023-04-23 11:00 | 80.2017 | 53.53 | 20 | 10 | 0 | 20 | 2674.6341
2700 | 2023-04-23 12:00 | 93.2297 | 53.53 | 0 | 0 | 10 | 10 | 0
2701 | 2023-04-23 13:00 | 78.8066 | 53.53 | 20 | 10 | 0 | 19.5 | 2646.7315
2702 | 2023-04-23 14:00 | 93.0186 | 53.53 | 1 | 0 | 9 | 10.5 | 146.5486
2703 | 2023-04-23 15:00 | 96.5829 | 53.53 | 0 | 0 | 10 | 0.5 | 0
2704 | 2023-04-23 16:00 | -49.5686 | 53.53 | 20 | 10 | 0 | 10 | 79.2279
2705 | 2023-04-23 17:00 | 99.611 | 53.53 | 0 | 0 | 10 | 0 | 0
2706 | 2023-04-23 18:00 | -43.44 | 53.53 | 20 | 10 | 0 | 9.5 | 201.8003
2707 | 2023-04-23 19:00 | 86.4937 | 53.53 | 0.5 | 0 | 9.5 | 0 | 70.0119
2708 | 2023-04-23 20:00 | 83.2712 | 53.53 | 10 | 0 | 0 | 0 | 1368.012
2709 | 2023-04-23 21:00 | 80.0624 | 53.53 | 10 | 0 | 0 | 0 | 1335.9244
2710 | 2023-04-23 22:00 | 80.5215 | 53.53 | 10 | 0 | 0 | 0 | 1340.5146
2711 | 2023-04-23 23:00 | 81.8008 | 53.53 | 10 | 0 | 0 | 0 | 1353.3076
2712 | 2023-04-24 00:00 | 83.3438 | 53.53 | 10 | 0 | 0 | 0 | 1368.7378
2713 | 2023-04-24 01:00 | 76.6559 | 53.53 | 10 | 0 | 0 | 0 | 1301.8591
2714 | 2023-04-24 02:00 | 62.86 | 53.53 | 20 | 10 | 0 | 9.5 | 2327.7993
2715 | 2023-04-24 03:00 | 64.4101 | 53.53 | 20 | 10 | 0 | 19 | 2358.8028
2716 | 2023-04-24 04:00 | 64.7753 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1307.5854
2717 | 2023-04-24 05:00 | 65.1427 | 53.53 | 10 | 0 | 0 | 20 | 1186.7268
2718 | 2023-04-24 06:00 | 73.0457 | 53.53 | 10 | 0 | 0 | 20 | 1265.7571
2719 | 2023-04-24 07:00 | 76.9469 | 53.53 | 10 | 0 | 0 | 20 | 1304.7686
2720 | 2023-04-24 08:00 | 95.2514 | 65.03 | 10 | 0 | 0 | 20 | 1602.8141
2721 | 2023-04-24 09:00 | 105.7114 | 65.03 | 0 | 0 | 10 | 10 | 0
2722 | 2023-04-24 10:00 | 83.7556 | 65.03 | 20 | 10 | 0 | 19.5 | 2975.7124
2723 | 2023-04-24 11:00 | 95.2826 | 65.03 | 10 | 0 | 0 | 19.5 | 1603.1262
2724 | 2023-04-24 12:00 | 89.8719 | 65.03 | 10 | 0 | 0 | 19.5 | 1549.0186
2725 | 2023-04-24 13:00 | 91.267 | 65.03 | 10 | 0 | 0 | 19.5 | 1562.9701
2726 | 2023-04-24 14:00 | 87.9553 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1610.3715
2727 | 2023-04-24 15:00 | 92.6585 | 65.03 | 10 | 0 | 0 | 20 | 1576.8848
2728 | 2023-04-24 16:00 | 112.3327 | 65.03 | 0 | 0 | 10 | 10 | 0
2729 | 2023-04-24 17:00 | 101.0063 | 66.4 | 10 | 0 | 0 | 10 | 1674.0632
2730 | 2023-04-24 18:00 | 101.5 | 66.4 | 10 | 0 | 0 | 10 | 1678.9996
2731 | 2023-04-24 19:00 | 100.8149 | 65.03 | 10 | 0 | 0 | 10 | 1658.4491
2732 | 2023-04-24 20:00 | 105.8744 | 65.03 | 0 | 0 | 10 | 0 | 0
2733 | 2023-04-24 21:00 | 85.6605 | 65.03 | 10 | 0 | 0 | 0 | 1506.9049
2734 | 2023-04-24 22:00 | 88.7068 | 65.03 | 10 | 0 | 0 | 0 | 1537.3675
2735 | 2023-04-24 23:00 | 81.0528 | 53.53 | 10 | 0 | 0 | 0 | 1345.8281
2736 | 2023-04-25 00:00 | 77.7301 | 53.53 | 10 | 0 | 0 | 0 | 1312.6014
2737 | 2023-04-25 01:00 | -16.3451 | 53.53 | 20 | 10 | 0 | 9.5 | 743.6981
2738 | 2023-04-25 02:00 | -22.8209 | 53.53 | 20 | 10 | 0 | 19 | 614.1819
2739 | 2023-04-25 03:00 | 76.8569 | 53.53 | 0 | 0 | 10 | 9 | 0
2740 | 2023-04-25 04:00 | 58.2542 | 53.53 | 2 | 0 | 8 | 1 | 223.5683
2741 | 2023-04-25 05:00 | -39.0166 | 53.53 | 20 | 10 | 0 | 10.5 | 290.2685
2742 | 2023-04-25 06:00 | -34.168 | 53.53 | 20 | 10 | 0 | 20 | 387.2402
2743 | 2023-04-25 07:00 | 73.5707 | 53.53 | 10 | 0 | 0 | 20 | 1271.0067
2744 | 2023-04-25 08:00 | 102.8429 | 65.03 | 10 | 0 | 0 | 20 | 1678.7288
2745 | 2023-04-25 09:00 | 104.3051 | 65.03 | 0 | 0 | 10 | 10 | 0
2746 | 2023-04-25 10:00 | 103.1142 | 65.03 | 0 | 0 | 10 | 0 | 0
2747 | 2023-04-25 11:00 | 90.6114 | 65.03 | 20 | 10 | 0 | 9.5 | 3112.8283
2748 | 2023-04-25 12:00 | 92.6783 | 65.03 | 10 | 0 | 0 | 9.5 | 1577.0826
2749 | 2023-04-25 13:00 | 100.2042 | 65.03 | 1.5 | 0 | 8.5 | 1 | 247.8513
2750 | 2023-04-25 14:00 | 97.0139 | 65.03 | 10 | 0 | 0 | 1 | 1620.4391
2751 | 2023-04-25 15:00 | 91.1137 | 65.03 | 20 | 10 | 0 | 10.5 | 3122.8736
2752 | 2023-04-25 16:00 | 84.2796 | 65.03 | 20 | 10 | 0 | 20 | 2986.1927
2753 | 2023-04-25 17:00 | 109.7671 | 66.4 | 0 | 0 | 10 | 10 | 0
2754 | 2023-04-25 18:00 | 118.4542 | 66.4 | 0 | 0 | 10 | 0 | 0
2755 | 2023-04-25 19:00 | 101.3528 | 65.03 | 10 | 0 | 0 | 0 | 1663.8284
2756 | 2023-04-25 20:00 | 94.1788 | 65.03 | 10 | 0 | 0 | 0 | 1592.088
2757 | 2023-04-25 21:00 | 91.5127 | 65.03 | 10 | 0 | 0 | 0 | 1565.4273
2758 | 2023-04-25 22:00 | 95.2078 | 65.03 | 10 | 0 | 0 | 0 | 1602.3777
2759 | 2023-04-25 23:00 | 91.3732 | 53.53 | 10 | 0 | 0 | 0 | 1449.0324
2760 | 2023-04-26 00:00 | 79.1966 | 53.53 | 10 | 0 | 0 | 0 | 1327.2659
2761 | 2023-04-26 01:00 | 74.2894 | 53.53 | 10 | 0 | 0 | 0 | 1278.1938
2762 | 2023-04-26 02:00 | 60.2007 | 53.53 | 20 | 10 | 0 | 9.5 | 2274.6142
2763 | 2023-04-26 03:00 | 71.5408 | 53.53 | 0.5 | 0 | 9.5 | 0 | 62.5354
2764 | 2023-04-26 04:00 | 60.1466 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1256.4251
2765 | 2023-04-26 05:00 | 59.1992 | 53.53 | 20 | 10 | 0 | 10.5 | 2254.5831
2766 | 2023-04-26 06:00 | 53.374 | 53.53 | 20 | 10 | 0 | 20 | 2138.0799
2767 | 2023-04-26 07:00 | 101.1934 | 53.53 | 10 | 0 | 0 | 20 | 1547.2336
2768 | 2023-04-26 08:00 | 100.9256 | 65.03 | 1 | 0 | 9 | 11 | 165.9556
2769 | 2023-04-26 09:00 | 100.3938 | 65.03 | 10 | 0 | 0 | 11 | 1654.238
2770 | 2023-04-26 10:00 | 102.3196 | 65.03 | 0 | 0 | 10 | 1 | 0
2771 | 2023-04-26 11:00 | 98.6203 | 65.03 | 10 | 0 | 0 | 1 | 1636.5033
2772 | 2023-04-26 12:00 | 92.1314 | 65.03 | 20 | 10 | 0 | 10.5 | 3143.2277
2773 | 2023-04-26 13:00 | 92.6998 | 65.03 | 10 | 0 | 0 | 10.5 | 1577.2976
2774 | 2023-04-26 14:00 | 90.8887 | 65.03 | 20 | 10 | 0 | 20 | 3118.3743
2775 | 2023-04-26 15:00 | 124.0065 | 65.03 | 0 | 0 | 10 | 10 | 0
2776 | 2023-04-26 16:00 | 98.4355 | 65.03 | 10 | 0 | 0 | 10 | 1634.6547
2777 | 2023-04-26 17:00 | 105.651 | 66.4 | 10 | 0 | 0 | 10 | 1720.5096
2778 | 2023-04-26 18:00 | 112.6451 | 66.4 | 0 | 0 | 10 | 0 | 0
2779 | 2023-04-26 19:00 | 102.3585 | 65.03 | 10 | 0 | 0 | 0 | 1673.8847
2780 | 2023-04-26 20:00 | 103.1592 | 65.03 | 10 | 0 | 0 | 0 | 1681.8916
2781 | 2023-04-26 21:00 | 84.401 | 65.03 | 20 | 10 | 0 | 9.5 | 2988.6195
2782 | 2023-04-26 22:00 | 92.9536 | 65.03 | 0.5 | 0 | 9.5 | 0 | 78.9918
2783 | 2023-04-26 23:00 | 93.3194 | 53.53 | 10 | 0 | 0 | 0 | 1468.4938
2784 | 2023-04-27 00:00 | 86.9572 | 53.53 | 10 | 0 | 0 | 0 | 1404.8722
2785 | 2023-04-27 01:00 | 84.617 | 53.53 | 10 | 0 | 0 | 0 | 1381.4697
2786 | 2023-04-27 02:00 | 63.9795 | 53.53 | 10 | 0 | 0 | 0 | 1175.0945
2787 | 2023-04-27 03:00 | 63.4786 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1293.2525
2788 | 2023-04-27 04:00 | 59.9265 | 53.53 | 20 | 10 | 0 | 10.5 | 2269.1309
2789 | 2023-04-27 05:00 | 60.7446 | 53.53 | 20 | 10 | 0 | 20 | 2285.4918
2790 | 2023-04-27 06:00 | 77.8668 | 53.53 | 10 | 0 | 0 | 20 | 1313.9678
2791 | 2023-04-27 07:00 | 83.0974 | 53.53 | 10 | 0 | 0 | 20 | 1366.2739
2792 | 2023-04-27 08:00 | 88.648 | 65.03 | 10 | 0 | 0 | 20 | 1536.7798
2793 | 2023-04-27 09:00 | 90.3111 | 65.03 | 10 | 0 | 0 | 20 | 1553.4106
2794 | 2023-04-27 10:00 | 103.6764 | 65.03 | 0 | 0 | 10 | 10 | 0
2795 | 2023-04-27 11:00 | 99.5154 | 65.03 | 0 | 0 | 10 | 0 | 0
2796 | 2023-04-27 12:00 | 98.4746 | 65.03 | 10 | 0 | 0 | 0 | 1635.0464
2797 | 2023-04-27 13:00 | 92.0396 | 65.03 | 10 | 0 | 0 | 0 | 1570.6962
2798 | 2023-04-27 14:00 | -12.7967 | 65.03 | 20 | 10 | 0 | 9.5 | 1044.666
2799 | 2023-04-27 15:00 | 89.5089 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1708.062
2800 | 2023-04-27 16:00 | -48.7947 | 65.03 | 20 | 10 | 0 | 20 | 324.7062
2801 | 2023-04-27 17:00 | 117.3405 | 66.4 | 0 | 0 | 10 | 10 | 0
2802 | 2023-04-27 18:00 | 116.3957 | 66.4 | 0 | 0 | 10 | 0 | 0
2803 | 2023-04-27 19:00 | 102.5195 | 65.03 | 10 | 0 | 0 | 0 | 1675.4955
2804 | 2023-04-27 20:00 | 83.2391 | 65.03 | 10 | 0 | 0 | 0 | 1482.6913
2805 | 2023-04-27 21:00 | -62.5604 | 65.03 | 20 | 10 | 0 | 9.5 | 49.3912
2806 | 2023-04-27 22:00 | -47.0072 | 65.03 | 20 | 10 | 0 | 19 | 360.455
2807 | 2023-04-27 23:00 | -29.028 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 270.8117
2808 | 2023-04-28 00:00 | 86.0754 | 53.53 | 0 | 0 | 10 | 10 | 0
2809 | 2023-04-28 01:00 | 75.443 | 53.53 | 0 | 0 | 10 | 0 | 0
2810 | 2023-04-28 02:00 | -42.4688 | 53.53 | 20 | 10 | 0 | 9.5 | 221.2243
2811 | 2023-04-28 03:00 | 61.3092 | 53.53 | 10 | 0 | 0 | 9.5 | 1148.392
2812 | 2023-04-28 04:00 | 60.9353 | 53.53 | 10 | 0 | 0 | 9.5 | 1144.6532
2813 | 2023-04-28 05:00 | 60.1989 | 53.53 | 10 | 0 | 0 | 9.5 | 1137.2894
2814 | 2023-04-28 06:00 | 63.9524 | 53.53 | 0.5 | 0 | 9.5 | 0 | 58.7412
2815 | 2023-04-28 07:00 | -49.9574 | 53.53 | 20 | 10 | 0 | 9.5 | 71.4511
2816 | 2023-04-28 08:00 | -36.8767 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 311.1681
2817 | 2023-04-28 09:00 | -41.6967 | 65.03 | 20 | 10 | 0 | 20 | 466.6667
2818 | 2023-04-28 10:00 | 100.2334 | 65.03 | 1 | 0 | 9 | 11 | 165.2634
2819 | 2023-04-28 11:00 | 101.0939 | 65.03 | 0 | 0 | 10 | 1 | 0
2820 | 2023-04-28 12:00 | 84.6454 | 65.03 | 20 | 10 | 0 | 10.5 | 2993.5079
2821 | 2023-04-28 13:00 | 96.2438 | 65.03 | 10 | 0 | 0 | 10.5 | 1612.7379
2822 | 2023-04-28 14:00 | 99.5188 | 65.03 | 10 | 0 | 0 | 10.5 | 1645.488
2823 | 2023-04-28 15:00 | 87.2462 | 65.03 | 20 | 10 | 0 | 20 | 3045.5241
2824 | 2023-04-28 16:00 | 93.9672 | 65.03 | 10 | 0 | 0 | 20 | 1589.972
2825 | 2023-04-28 17:00 | 108.0413 | 66.4 | 10 | 0 | 0 | 20 | 1744.4134
2826 | 2023-04-28 18:00 | 127.3444 | 66.4 | 0 | 0 | 10 | 10 | 0
2827 | 2023-04-28 19:00 | 128.431 | 65.03 | 0 | 0 | 10 | 0 | 0
2828 | 2023-04-28 20:00 | 79.0721 | 65.03 | 20 | 10 | 0 | 9.5 | 2882.0417
2829 | 2023-04-28 21:00 | 116.727 | 65.03 | 0.5 | 0 | 9.5 | 0 | 90.8785
2830 | 2023-04-28 22:00 | 82.8958 | 65.03 | 10 | 0 | 0 | 0 | 1479.2582
2831 | 2023-04-28 23:00 | 92.4497 | 53.53 | 10 | 0 | 0 | 0 | 1459.7968
2832 | 2023-04-29 00:00 | 84.3474 | 53.53 | 10 | 0 | 0 | 0 | 1378.7742
2833 | 2023-04-29 01:00 | 69.4427 | 53.53 | 10 | 0 | 0 | 0 | 1229.7272
2834 | 2023-04-29 02:00 | 59.8856 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1253.5404
2835 | 2023-04-29 03:00 | 55.1047 | 53.53 | 20 | 10 | 0 | 10.5 | 2172.6935
2836 | 2023-04-29 04:00 | 60.4215 | 53.53 | 10 | 0 | 0 | 10.5 | 1139.5146
2837 | 2023-04-29 05:00 | 57.6896 | 53.53 | 20 | 10 | 0 | 20 | 2224.3923
2838 | 2023-04-29 06:00 | 66.6922 | 53.53 | 10 | 0 | 0 | 20 | 1202.2221
2839 | 2023-04-29 07:00 | 76.4702 | 53.53 | 10 | 0 | 0 | 20 | 1300.0025
2840 | 2023-04-29 08:00 | 84.6704 | 53.53 | 10 | 0 | 0 | 20 | 1382.0043
2841 | 2023-04-29 09:00 | 95.6315 | 53.53 | 0 | 0 | 10 | 10 | 0
2842 | 2023-04-29 10:00 | 90.6532 | 53.53 | 10 | 0 | 0 | 10 | 1441.8323
2843 | 2023-04-29 11:00 | 92.036 | 53.53 | 0 | 0 | 10 | 0 | 0
2844 | 2023-04-29 12:00 | 81.3794 | 53.53 | 20 | 10 | 0 | 9.5 | 2698.187
2845 | 2023-04-29 13:00 | 79.169 | 53.53 | 20 | 10 | 0 | 19 | 2653.9795
2846 | 2023-04-29 14:00 | 81.9832 | 53.53 | 10 | 0 | 0 | 19 | 1355.1325
2847 | 2023-04-29 15:00 | 81.65 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1494.0951
2848 | 2023-04-29 16:00 | 92.5482 | 53.53 | 10 | 0 | 0 | 20 | 1460.7823
2849 | 2023-04-29 17:00 | 109.4025 | 53.53 | 0 | 0 | 10 | 10 | 0
2850 | 2023-04-29 18:00 | 99.7615 | 53.53 | 10 | 0 | 0 | 10 | 1532.9149
2851 | 2023-04-29 19:00 | 114.3019 | 53.53 | 0 | 0 | 10 | 0 | 0
2852 | 2023-04-29 20:00 | 93.5891 | 53.53 | 10 | 0 | 0 | 0 | 1471.1913
2853 | 2023-04-29 21:00 | 82.7921 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1434.9695
2854 | 2023-04-29 22:00 | 75.4353 | 53.53 | 20 | 10 | 0 | 10 | 2579.3054
2855 | 2023-04-29 23:00 | 91.0028 | 53.53 | 0 | 0 | 10 | 0 | 0
2856 | 2023-04-30 00:00 | 75.4448 | 53.53 | 10 | 0 | 0 | 0 | 1289.7484
2857 | 2023-04-30 01:00 | 76.8627 | 53.53 | 10 | 0 | 0 | 0 | 1303.9268
2858 | 2023-04-30 02:00 | 53.4767 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1182.7059
2859 | 2023-04-30 03:00 | -28.663 | 53.53 | 20 | 10 | 0 | 10.5 | 497.3403
2860 | 2023-04-30 04:00 | 46.9897 | 53.53 | 20 | 10 | 0 | 20 | 2010.3938
2861 | 2023-04-30 05:00 | 61.1253 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 57.3277
2862 | 2023-04-30 06:00 | 50.6622 | 53.53 | 20 | 10 | 0 | 20 | 2083.8435
2863 | 2023-04-30 07:00 | 113.4964 | 53.53 | 0 | 0 | 10 | 10 | 0
2864 | 2023-04-30 08:00 | 78.9466 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1394.491
2865 | 2023-04-30 09:00 | 78.0425 | 53.53 | 20 | 10 | 0 | 20 | 2631.4505
2866 | 2023-04-30 10:00 | 90.0326 | 53.53 | 0 | 0 | 10 | 10 | 0
2867 | 2023-04-30 11:00 | 100.4524 | 53.53 | 0 | 0 | 10 | 0 | 0
2868 | 2023-04-30 12:00 | 86.3875 | 53.53 | 10 | 0 | 0 | 0 | 1399.1745
2869 | 2023-04-30 13:00 | -68.846 | 53.53 | 20 | 10 | 0 | 9.5 | -306.3203
2870 | 2023-04-30 14:00 | 75.2779 | 53.53 | 20 | 10 | 0 | 19 | 2576.1584
2871 | 2023-04-30 15:00 | 81.3001 | 53.53 | 10 | 0 | 0 | 19 | 1348.3009
2872 | 2023-04-30 16:00 | 79.0142 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1464.9625
2873 | 2023-04-30 17:00 | 90.0575 | 53.53 | 0 | 0 | 10 | 10 | 0
2874 | 2023-04-30 18:00 | 101.7912 | 53.53 | 0 | 0 | 10 | 0 | 0
2875 | 2023-04-30 19:00 | 88.6546 | 53.53 | 10 | 0 | 0 | 0 | 1421.8464
2876 | 2023-04-30 20:00 | 72.7124 | 53.53 | 20 | 10 | 0 | 9.5 | 2524.8479
2877 | 2023-04-30 21:00 | 77.1772 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1444.659
2878 | 2023-04-30 22:00 | 75.3803 | 53.53 | 20 | 10 | 0 | 20 | 2578.2058
2879 | 2023-04-30 23:00 | 79.0554 | 53.53 | 10 | 0 | 0 | 20 | 1325.8537
2880 | 2023-05-01 00:00 | 86.2985 | 53.53 | 0 | 0 | 10 | 10 | 0
2881 | 2023-05-01 01:00 | 91.5865 | 53.53 | 0 | 0 | 10 | 0 | 0
2882 | 2023-05-01 02:00 | 70.2288 | 53.53 | 10 | 0 | 0 | 0 | 1237.5877
2883 | 2023-05-01 03:00 | 74.1009 | 53.53 | 10 | 0 | 0 | 0 | 1276.309
2884 | 2023-05-01 04:00 | 63.8839 | 53.53 | 20 | 10 | 0 | 9.5 | 2348.2784
2885 | 2023-05-01 05:00 | 66.2811 | 53.53 | 20 | 10 | 0 | 19 | 2396.2226
2886 | 2023-05-01 06:00 | 68.0447 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1343.72
2887 | 2023-05-01 07:00 | 84.9836 | 53.53 | 10 | 0 | 0 | 20 | 1385.1363
2888 | 2023-05-01 08:00 | 91.09 | 65.03 | 10 | 0 | 0 | 20 | 1561.1999
2889 | 2023-05-01 09:00 | 91.5253 | 65.03 | 10 | 0 | 0 | 20 | 1565.5529
2890 | 2023-05-01 10:00 | 88.4607 | 65.03 | 10 | 0 | 0 | 20 | 1534.9069
2891 | 2023-05-01 11:00 | 97.2691 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 81.1496
2892 | 2023-05-01 12:00 | 93.203 | 65.03 | 10 | 0 | 0 | 10.5 | 1582.3304
2893 | 2023-05-01 13:00 | 89.388 | 65.03 | 10 | 0 | 0 | 10.5 | 1544.1803
2894 | 2023-05-01 14:00 | 89.3937 | 65.03 | 10 | 0 | 0 | 10.5 | 1544.2375
2895 | 2023-05-01 15:00 | 86.2859 | 65.03 | 20 | 10 | 0 | 20 | 3026.3177
2896 | 2023-05-01 16:00 | 102.4312 | 65.03 | 10 | 0 | 0 | 20 | 1674.6125
2897 | 2023-05-01 17:00 | 109.4949 | 66.4 | 0 | 0 | 10 | 10 | 0
2898 | 2023-05-01 18:00 | 103.197 | 66.4 | 10 | 0 | 0 | 10 | 1695.9697
2899 | 2023-05-01 19:00 | 115.7611 | 65.03 | 0 | 0 | 10 | 0 | 0
2900 | 2023-05-01 20:00 | 85.0293 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1579.5716
2901 | 2023-05-01 21:00 | 80.2925 | 65.03 | 20 | 10 | 0 | 10 | 2906.4495
2902 | 2023-05-01 22:00 | 97.8603 | 65.03 | 0 | 0 | 10 | 0 | 0
2903 | 2023-05-01 23:00 | -41.045 | 53.53 | 20 | 10 | 0 | 9.5 | 249.7006
2904 | 2023-05-02 00:00 | -31.358 | 53.53 | 2 | 0 | 8 | 1.5 | 44.3441
2905 | 2023-05-02 01:00 | -73.5546 | 53.53 | 20 | 10 | 0 | 11 | -400.4915
2906 | 2023-05-02 02:00 | 74.1197 | 53.53 | 0 | 0 | 10 | 1 | 0
2907 | 2023-05-02 03:00 | -69.5921 | 53.53 | 20 | 10 | 0 | 10.5 | -321.2415
2908 | 2023-05-02 04:00 | -32.8102 | 53.53 | 20 | 10 | 0 | 20 | 414.3962
2909 | 2023-05-02 05:00 | -11.7304 | 53.53 | 10 | 0 | 0 | 20 | 417.9958
2910 | 2023-05-02 06:00 | 60.5131 | 53.53 | 10 | 0 | 0 | 20 | 1140.4312
2911 | 2023-05-02 07:00 | 102.9451 | 53.53 | 10 | 0 | 0 | 20 | 1564.7512
2912 | 2023-05-02 08:00 | 93.8899 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 79.46
2913 | 2023-05-02 09:00 | 81.6845 | 65.03 | 20 | 10 | 0 | 20 | 2934.2898
2914 | 2023-05-02 10:00 | 96.7275 | 65.03 | 10 | 0 | 0 | 20 | 1617.5749
2915 | 2023-05-02 11:00 | 113.7004 | 65.03 | 0 | 0 | 10 | 10 | 0
2916 | 2023-05-02 12:00 | 109.0094 | 65.03 | 10 | 0 | 0 | 10 | 1740.3936
2917 | 2023-05-02 13:00 | 112.1987 | 65.03 | 0 | 0 | 10 | 0 | 0
2918 | 2023-05-02 14:00 | 87.3093 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1683.7501
2919 | 2023-05-02 15:00 | -17.7314 | 65.03 | 20 | 10 | 0 | 10.5 | 945.9722
2920 | 2023-05-02 16:00 | -54.8688 | 65.03 | 20 | 10 | 0 | 20 | 203.2231
2921 | 2023-05-02 17:00 | 110.6384 | 66.4 | 0 | 0 | 10 | 10 | 0
2922 | 2023-05-02 18:00 | 100.9626 | 66.4 | 10 | 0 | 0 | 10 | 1673.6263
2923 | 2023-05-02 19:00 | 104.5034 | 65.03 | 0 | 0 | 10 | 0 | 0
2924 | 2023-05-02 20:00 | 84.3078 | 65.03 | 20 | 10 | 0 | 9.5 | 2986.7567
2925 | 2023-05-02 21:00 | 96.6332 | 65.03 | 0.5 | 0 | 9.5 | 0 | 80.8316
2926 | 2023-05-02 22:00 | 95.6864 | 65.03 | 10 | 0 | 0 | 0 | 1607.1639
2927 | 2023-05-02 23:00 | 86.0631 | 53.53 | 10 | 0 | 0 | 0 | 1395.931
2928 | 2023-05-03 00:00 | 75.5706 | 53.53 | 10 | 0 | 0 | 0 | 1291.0062
2929 | 2023-05-03 01:00 | 81.6669 | 53.53 | 10 | 0 | 0 | 0 | 1351.9694
2930 | 2023-05-03 02:00 | 58.8845 | 53.53 | 20 | 10 | 0 | 9.5 | 2248.2897
2931 | 2023-05-03 03:00 | 71.3508 | 53.53 | 10 | 0 | 0 | 9.5 | 1248.8084
2932 | 2023-05-03 04:00 | 74.4978 | 53.53 | 10 | 0 | 0 | 9.5 | 1280.2779
2933 | 2023-05-03 05:00 | 73.2205 | 53.53 | 10 | 0 | 0 | 9.5 | 1267.5048
2934 | 2023-05-03 06:00 | 58.83 | 53.53 | 20 | 10 | 0 | 19 | 2247.1996
2935 | 2023-05-03 07:00 | 69.8886 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1364.1007
2936 | 2023-05-03 08:00 | 83.6121 | 65.03 | 10 | 0 | 0 | 20 | 1486.4213
2937 | 2023-05-03 09:00 | 107.195 | 65.03 | 0 | 0 | 10 | 10 | 0
2938 | 2023-05-03 10:00 | 91.063 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1643.0839
2939 | 2023-05-03 11:00 | 88.8569 | 65.03 | 20 | 10 | 0 | 20 | 3077.7374
2940 | 2023-05-03 12:00 | 109.8206 | 65.03 | 0 | 0 | 10 | 10 | 0
2941 | 2023-05-03 13:00 | 105.4389 | 65.03 | 0 | 0 | 10 | 0 | 0
2942 | 2023-05-03 14:00 | 94.0823 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1758.6101
2943 | 2023-05-03 15:00 | 91.7918 | 65.03 | 20 | 10 | 0 | 10.5 | 3136.437
2944 | 2023-05-03 16:00 | 92.9269 | 65.03 | 20 | 10 | 0 | 20 | 3159.1384
2945 | 2023-05-03 17:00 | 110.6614 | 66.4 | 10 | 0 | 0 | 20 | 1770.6142
2946 | 2023-05-03 18:00 | 124.3007 | 66.4 | 0 | 0 | 10 | 10 | 0
2947 | 2023-05-03 19:00 | 112.2764 | 65.03 | 0 | 0 | 10 | 0 | 0
2948 | 2023-05-03 20:00 | 94.982 | 65.03 | 10 | 0 | 0 | 0 | 1600.1204
2949 | 2023-05-03 21:00 | 99.4027 | 65.03 | 10 | 0 | 0 | 0 | 1644.3271
2950 | 2023-05-03 22:00 | 81.4996 | 65.03 | 10 | 0 | 0 | 0 | 1465.2961
2951 | 2023-05-03 23:00 | 90.2521 | 53.53 | 10 | 0 | 0 | 0 | 1437.8207
2952 | 2023-05-04 00:00 | 81.7838 | 53.53 | 10 | 0 | 0 | 0 | 1353.1384
2953 | 2023-05-04 01:00 | 70.6506 | 53.53 | 10 | 0 | 0 | 0 | 1241.8059
2954 | 2023-05-04 02:00 | 52.1011 | 53.53 | 20 | 10 | 0 | 9.5 | 2112.6211
2955 | 2023-05-04 03:00 | 57.3184 | 53.53 | 20 | 10 | 0 | 19 | 2216.9674
2956 | 2023-05-04 04:00 | 68.2175 | 53.53 | 10 | 0 | 0 | 19 | 1217.4751
2957 | 2023-05-04 05:00 | 64.7665 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1307.4881
2958 | 2023-05-04 06:00 | 65.32 | 53.53 | 10 | 0 | 0 | 20 | 1188.5001
2959 | 2023-05-04 07:00 | 103.7858 | 53.53 | 10 | 0 | 0 | 20 | 1573.1578
2960 | 2023-05-04 08:00 | 85.9824 | 65.03 | 10 | 0 | 0 | 20 | 1510.1242
2961 | 2023-05-04 09:00 | 93.6934 | 65.03 | 10 | 0 | 0 | 20 | 1587.234
2962 | 2023-05-04 10:00 | 96.2891 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 80.6595
2963 | 2023-05-04 11:00 | 88.9436 | 65.03 | 10 | 0 | 0 | 10.5 | 1539.7359
2964 | 2023-05-04 12:00 | 94.1117 | 65.03 | 10 | 0 | 0 | 10.5 | 1591.4166
2965 | 2023-05-04 13:00 | 84.3681 | 65.03 | 20 | 10 | 0 | 20 | 2987.9625
2966 | 2023-05-04 14:00 | 107.0606 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 86.0453
2967 | 2023-05-04 15:00 | 89.275 | 65.03 | 20 | 10 | 0 | 20 | 3086.0999
2968 | 2023-05-04 16:00 | 114.8824 | 65.03 | 0 | 0 | 10 | 10 | 0
2969 | 2023-05-04 17:00 | 108.6559 | 66.4 | 10 | 0 | 0 | 10 | 1750.5593
2970 | 2023-05-04 18:00 | 117.93 | 66.4 | 0 | 0 | 10 | 0 | 0
2971 | 2023-05-04 19:00 | 108.5017 | 65.03 | 10 | 0 | 0 | 0 | 1735.3171
2972 | 2023-05-04 20:00 | 88.6688 | 65.03 | 10 | 0 | 0 | 0 | 1536.9879
2973 | 2023-05-04 21:00 | 84.8804 | 65.03 | 10 | 0 | 0 | 0 | 1499.1035
2974 | 2023-05-04 22:00 | 89.8079 | 65.03 | 10 | 0 | 0 | 0 | 1548.3789
2975 | 2023-05-04 23:00 | 86.4008 | 53.53 | 10 | 0 | 0 | 0 | 1399.3077
2976 | 2023-05-05 00:00 | 78.6571 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1391.4431
2977 | 2023-05-05 01:00 | 82.9778 | 53.53 | 10 | 0 | 0 | 0.5 | 1365.0785
2978 | 2023-05-05 02:00 | 59.7169 | 53.53 | 20 | 10 | 0 | 10 | 2264.9378
2979 | 2023-05-05 03:00 | 88.7362 | 53.53 | 0 | 0 | 10 | 0 | 0
2980 | 2023-05-05 04:00 | 63.2343 | 53.53 | 20 | 10 | 0 | 9.5 | 2335.2861
2981 | 2023-05-05 05:00 | 78.6418 | 53.53 | 1.5 | 0 | 8.5 | 1 | 198.2577
2982 | 2023-05-05 06:00 | -78.5002 | 53.53 | 20 | 10 | 0 | 10.5 | -499.4044
2983 | 2023-05-05 07:00 | -63.148 | 53.53 | 20 | 10 | 0 | 20 | -192.3606
2984 | 2023-05-05 08:00 | 85.7166 | 65.03 | 10 | 0 | 0 | 20 | 1507.4659
2985 | 2023-05-05 09:00 | 90.7604 | 65.03 | 10 | 0 | 0 | 20 | 1557.904
2986 | 2023-05-05 10:00 | 95.5282 | 65.03 | 10 | 0 | 0 | 20 | 1605.5825
2987 | 2023-05-05 11:00 | 109.1309 | 65.03 | 0 | 0 | 10 | 10 | 0
2988 | 2023-05-05 12:00 | 95.6199 | 65.03 | 20 | 10 | 0 | 19.5 | 3212.9973
2989 | 2023-05-05 13:00 | 106.762 | 65.03 | 10 | 0 | 0 | 19.5 | 1717.9197
2990 | 2023-05-05 14:00 | 99.1967 | 65.03 | 10 | 0 | 0 | 19.5 | 1642.267
2991 | 2023-05-05 15:00 | 109.6337 | 65.03 | 0 | 0 | 10 | 9.5 | 0
2992 | 2023-05-05 16:00 | 93.4594 | 65.03 | 20 | 10 | 0 | 19 | 3169.7878
2993 | 2023-05-05 17:00 | 135.1087 | 66.4 | 0 | 0 | 10 | 9 | 0
2994 | 2023-05-05 18:00 | 105.5105 | 66.4 | 1.5 | 0 | 8.5 | 0.5 | 257.8657
2995 | 2023-05-05 19:00 | 103.7629 | 65.03 | 10 | 0 | 0 | 0.5 | 1687.9287
2996 | 2023-05-05 20:00 | 81.2877 | 65.03 | 20 | 10 | 0 | 10 | 2926.3538
2997 | 2023-05-05 21:00 | 114.2073 | 65.03 | 0 | 0 | 10 | 0 | 0
2998 | 2023-05-05 22:00 | 95.8655 | 65.03 | 10 | 0 | 0 | 0 | 1608.955
2999 | 2023-05-05 23:00 | 81.5139 | 53.53 | 10 | 0 | 0 | 0 | 1350.439
3000 | 2023-05-06 00:00 | 87.2624 | 53.53 | 10 | 0 | 0 | 0 | 1407.9243
3001 | 2023-05-06 01:00 | 81.6266 | 53.53 | 10 | 0 | 0 | 0 | 1351.5659
3002 | 2023-05-06 02:00 | 75.9907 | 53.53 | 10 | 0 | 0 | 0 | 1295.2072
3003 | 2023-05-06 03:00 | 46.6119 | 53.53 | 20 | 10 | 0 | 9.5 | 2002.8379
3004 | 2023-05-06 04:00 | 53.9853 | 53.53 | 1.5 | 0 | 8.5 | 1 | 161.2729
3005 | 2023-05-06 05:00 | 52.6593 | 53.53 | 10 | 0 | 0 | 1 | 1061.8931
3006 | 2023-05-06 06:00 | -45.7298 | 53.53 | 20 | 10 | 0 | 10.5 | 156.0043
3007 | 2023-05-06 07:00 | -22.1153 | 53.53 | 20 | 10 | 0 | 20 | 628.2945
3008 | 2023-05-06 08:00 | 83.9504 | 53.53 | 10 | 0 | 0 | 20 | 1374.8041
3009 | 2023-05-06 09:00 | 92.1091 | 53.53 | 0 | 0 | 10 | 10 | 0
3010 | 2023-05-06 10:00 | 111.643 | 53.53 | 0 | 0 | 10 | 0 | 0
3011 | 2023-05-06 11:00 | 83.3845 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1585.3261
3012 | 2023-05-06 12:00 | 82.9311 | 53.53 | 20 | 10 | 0 | 11 | 2729.2211
3013 | 2023-05-06 13:00 | 86.8043 | 53.53 | 10 | 0 | 0 | 11 | 1403.3432
3014 | 2023-05-06 14:00 | 94.5159 | 53.53 | 0 | 0 | 10 | 1 | 0
3015 | 2023-05-06 15:00 | 81.9896 | 53.53 | 20 | 10 | 0 | 10.5 | 2710.3927
3016 | 2023-05-06 16:00 | 81.587 | 53.53 | 20 | 10 | 0 | 20 | 2702.34
3017 | 2023-05-06 17:00 | 110.2288 | 53.53 | 0 | 0 | 10 | 10 | 0
3018 | 2023-05-06 18:00 | 103.9057 | 53.53 | 0 | 0 | 10 | 0 | 0
3019 | 2023-05-06 19:00 | 89.4357 | 53.53 | 10 | 0 | 0 | 0 | 1429.6572
3020 | 2023-05-06 20:00 | 73.2079 | 53.53 | 20 | 10 | 0 | 9.5 | 2534.7571
3021 | 2023-05-06 21:00 | 95.1207 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.3253
3022 | 2023-05-06 22:00 | 84.102 | 53.53 | 10 | 0 | 0 | 0 | 1376.3204
3023 | 2023-05-06 23:00 | 70.7883 | 53.53 | 10 | 0 | 0 | 0 | 1243.1831
3024 | 2023-05-07 00:00 | 74.6524 | 53.53 | 10 | 0 | 0 | 0 | 1281.8235
3025 | 2023-05-07 01:00 | 75.9978 | 53.53 | 10 | 0 | 0 | 0 | 1295.2778
3026 | 2023-05-07 02:00 | -43.0472 | 53.53 | 20 | 10 | 0 | 9.5 | 209.6554
3027 | 2023-05-07 03:00 | -62.6584 | 53.53 | 20 | 10 | 0 | 19 | -182.5672
3028 | 2023-05-07 04:00 | -5.3173 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 532.8775
3029 | 2023-05-07 05:00 | 58.0316 | 53.53 | 10 | 0 | 0 | 20 | 1115.6163
3030 | 2023-05-07 06:00 | 55.1606 | 53.53 | 10 | 0 | 0 | 20 | 1086.9065
3031 | 2023-05-07 07:00 | 80.5771 | 53.53 | 10 | 0 | 0 | 20 | 1341.0712
3032 | 2023-05-07 08:00 | 78.1865 | 53.53 | 10 | 0 | 0 | 20 | 1317.165
3033 | 2023-05-07 09:00 | 88.7255 | 53.53 | 10 | 0 | 0 | 20 | 1422.5552
3034 | 2023-05-07 10:00 | 95.5848 | 53.53 | 0 | 0 | 10 | 10 | 0
3035 | 2023-05-07 11:00 | 89.8295 | 53.53 | 10 | 0 | 0 | 10 | 1433.5953
3036 | 2023-05-07 12:00 | 86.9637 | 53.53 | 10 | 0 | 0 | 10 | 1404.9372
3037 | 2023-05-07 13:00 | 85.1894 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1460.2045
3038 | 2023-05-07 14:00 | 80.3595 | 53.53 | 20 | 10 | 0 | 20 | 2677.7892
3039 | 2023-05-07 15:00 | 85.3641 | 53.53 | 10 | 0 | 0 | 20 | 1388.9411
3040 | 2023-05-07 16:00 | 97.3792 | 53.53 | 10 | 0 | 0 | 20 | 1509.0916
3041 | 2023-05-07 17:00 | 100.0213 | 53.53 | 0 | 0 | 10 | 10 | 0
3042 | 2023-05-07 18:00 | 95.0413 | 53.53 | 10 | 0 | 0 | 10 | 1485.7126
3043 | 2023-05-07 19:00 | 97.4661 | 53.53 | 0 | 0 | 10 | 0 | 0
3044 | 2023-05-07 20:00 | 82.451 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1502.9478
3045 | 2023-05-07 21:00 | 78.2482 | 53.53 | 20 | 10 | 0 | 10.5 | 2635.564
3046 | 2023-05-07 22:00 | 84.8164 | 53.53 | 10 | 0 | 0 | 10.5 | 1383.4638
3047 | 2023-05-07 23:00 | 80.1439 | 53.53 | 20 | 10 | 0 | 20 | 2673.478
3048 | 2023-05-08 00:00 | 91.5394 | 53.53 | 0 | 0 | 10 | 10 | 0
3049 | 2023-05-08 01:00 | 97.2172 | 53.53 | 0 | 0 | 10 | 0 | 0
3050 | 2023-05-08 02:00 | 72.6029 | 53.53 | 10 | 0 | 0 | 0 | 1261.3288
3051 | 2023-05-08 03:00 | 57.7878 | 53.53 | 10 | 0 | 0 | 0 | 1113.1777
3052 | 2023-05-08 04:00 | 57.9626 | 53.53 | 10 | 0 | 0 | 0 | 1114.9257
3053 | 2023-05-08 05:00 | -25.9809 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 304.4897
3054 | 2023-05-08 06:00 | -48.4631 | 53.53 | 20 | 10 | 0 | 10.5 | 101.3388
3055 | 2023-05-08 07:00 | -57.7532 | 53.53 | 20 | 10 | 0 | 20 | -84.4634
3056 | 2023-05-08 08:00 | 90.7957 | 65.03 | 10 | 0 | 0 | 20 | 1558.2571
3057 | 2023-05-08 09:00 | 90.5812 | 65.03 | 10 | 0 | 0 | 20 | 1556.1116
3058 | 2023-05-08 10:00 | 89.3348 | 65.03 | 10 | 0 | 0 | 20 | 1543.6479
3059 | 2023-05-08 11:00 | 91.6386 | 65.03 | 10 | 0 | 0 | 20 | 1566.6861
3060 | 2023-05-08 12:00 | 104.5006 | 65.03 | 0 | 0 | 10 | 10 | 0
3061 | 2023-05-08 13:00 | 95.4382 | 65.03 | 11.0526 | 1.0526 | 0 | 11 | 1773.5954
3062 | 2023-05-08 14:00 | 121.3776 | 65.03 | 0 | 0 | 10 | 1 | 0
3063 | 2023-05-08 15:00 | 95.2104 | 65.03 | 20 | 10 | 0 | 10.5 | 3204.8078
3064 | 2023-05-08 16:00 | 91.8148 | 65.03 | 20 | 10 | 0 | 20 | 3136.8956
3065 | 2023-05-08 17:00 | 108.9293 | 66.4 | 10 | 0 | 0 | 20 | 1753.2932
3066 | 2023-05-08 18:00 | 110.8979 | 66.4 | 0 | 0 | 10 | 10 | 0
3067 | 2023-05-08 19:00 | 112.3854 | 65.03 | 0 | 0 | 10 | 0 | 0
3068 | 2023-05-08 20:00 | 110.5118 | 65.03 | 10 | 0 | 0 | 0 | 1755.4176
3069 | 2023-05-08 21:00 | 83.2984 | 65.03 | 20 | 10 | 0 | 9.5 | 2966.5687
3070 | 2023-05-08 22:00 | 96.2475 | 65.03 | 0.5 | 0 | 9.5 | 0 | 80.6388
3071 | 2023-05-08 23:00 | 85.506 | 53.53 | 10 | 0 | 0 | 0 | 1390.3602
3072 | 2023-05-09 00:00 | 74.5026 | 53.53 | 10 | 0 | 0 | 0 | 1280.3261
3073 | 2023-05-09 01:00 | -74.396 | 53.53 | 20 | 10 | 0 | 9.5 | -417.3201
3074 | 2023-05-09 02:00 | 75.4659 | 53.53 | 0.5 | 0 | 9.5 | 0 | 64.498
3075 | 2023-05-09 03:00 | 58.2296 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1235.2372
3076 | 2023-05-09 04:00 | 63.8314 | 53.53 | 10 | 0 | 0 | 1 | 1173.6139
3077 | 2023-05-09 05:00 | 53.7969 | 53.53 | 20 | 10 | 0 | 10.5 | 2146.5388
3078 | 2023-05-09 06:00 | 56.0352 | 53.53 | 20 | 10 | 0 | 20 | 2191.3041
3079 | 2023-05-09 07:00 | 93.1345 | 53.53 | 10 | 0 | 0 | 20 | 1466.6454
3080 | 2023-05-09 08:00 | 90.6339 | 65.03 | 10 | 0 | 0 | 20 | 1556.6389
3081 | 2023-05-09 09:00 | 86.824 | 65.03 | 10 | 0 | 0 | 20 | 1518.54
3082 | 2023-05-09 10:00 | 95.6799 | 65.03 | 10 | 0 | 0 | 20 | 1607.0988
3083 | 2023-05-09 11:00 | 90.2718 | 65.03 | 10 | 0 | 0 | 20 | 1553.0181
3084 | 2023-05-09 12:00 | 90.6052 | 65.03 | 10 | 0 | 0 | 20 | 1556.3519
3085 | 2023-05-09 13:00 | 100.1063 | 65.03 | 0 | 0 | 10 | 10 | 0
3086 | 2023-05-09 14:00 | 86.5416 | 65.03 | 20 | 10 | 0 | 19.5 | 3031.432
3087 | 2023-05-09 15:00 | 87.9521 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1610.3379
3088 | 2023-05-09 16:00 | 95.081 | 65.03 | 10 | 0 | 0 | 20 | 1601.1103
3089 | 2023-05-09 17:00 | 117.3365 | 66.4 | 0 | 0 | 10 | 10 | 0
3090 | 2023-05-09 18:00 | 120.1441 | 66.4 | 0 | 0 | 10 | 0 | 0
3091 | 2023-05-09 19:00 | 104.3764 | 65.03 | 10 | 0 | 0 | 0 | 1694.0643
3092 | 2023-05-09 20:00 | 97.0167 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1705.7548
3093 | 2023-05-09 21:00 | 83.6578 | 65.03 | 20 | 10 | 0 | 10 | 2973.7556
3094 | 2023-05-09 22:00 | 107.1371 | 65.03 | 0 | 0 | 10 | 0 | 0
3095 | 2023-05-09 23:00 | 76.6902 | 53.53 | 20 | 10 | 0 | 9.5 | 2604.4046
3096 | 2023-05-10 00:00 | 96.1396 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.8348
3097 | 2023-05-10 01:00 | 79.4292 | 53.53 | 10 | 0 | 0 | 0 | 1329.5918
3098 | 2023-05-10 02:00 | -49.5484 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 44.0067
3099 | 2023-05-10 03:00 | -75.3451 | 53.53 | 20 | 10 | 0 | 10.5 | -436.3024
3100 | 2023-05-10 04:00 | -76.8647 | 53.53 | 20 | 10 | 0 | 20 | -466.6937
3101 | 2023-05-10 05:00 | 60.2729 | 53.53 | 10 | 0 | 0 | 20 | 1138.0293
3102 | 2023-05-10 06:00 | 70.5006 | 53.53 | 10 | 0 | 0 | 20 | 1240.3061
3103 | 2023-05-10 07:00 | 93.182 | 53.53 | 10 | 0 | 0 | 20 | 1467.1198
3104 | 2023-05-10 08:00 | 93.3735 | 65.03 | 10 | 0 | 0 | 20 | 1584.0353
3105 | 2023-05-10 09:00 | 94.2355 | 65.03 | 10 | 0 | 0 | 20 | 1592.655
3106 | 2023-05-10 10:00 | 100.2849 | 65.03 | 0 | 0 | 10 | 10 | 0
3107 | 2023-05-10 11:00 | 94.9066 | 65.03 | 10 | 0 | 0 | 10 | 1599.366
3108 | 2023-05-10 12:00 | 85.8577 | 65.03 | 20 | 10 | 0 | 19.5 | 3017.7548
3109 | 2023-05-10 13:00 | 88.4876 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1615.9748
3110 | 2023-05-10 14:00 | 95.7254 | 65.03 | 10 | 0 | 0 | 20 | 1607.5539
3111 | 2023-05-10 15:00 | 104.8984 | 65.03 | 10 | 0 | 0 | 20 | 1699.2836
3112 | 2023-05-10 16:00 | 109.4943 | 65.03 | 10 | 0 | 0 | 20 | 1745.2435
3113 | 2023-05-10 17:00 | 115.485 | 66.4 | 0 | 0 | 10 | 10 | 0
3114 | 2023-05-10 18:00 | 111.1486 | 66.4 | 10 | 0 | 0 | 10 | 1775.4857
3115 | 2023-05-10 19:00 | 115.1952 | 65.03 | 0 | 0 | 10 | 0 | 0
3116 | 2023-05-10 20:00 | 84.3661 | 65.03 | 10 | 0 | 0 | 0 | 1493.9606
3117 | 2023-05-10 21:00 | 87.7751 | 65.03 | 10 | 0 | 0 | 0 | 1528.0509
3118 | 2023-05-10 22:00 | 83.4222 | 65.03 | 10 | 0 | 0 | 0 | 1484.5215
3119 | 2023-05-10 23:00 | 76.087 | 53.53 | 20 | 10 | 0 | 9.5 | 2592.3404
3120 | 2023-05-11 00:00 | 86.5294 | 53.53 | 0.5 | 0 | 9.5 | 0 | 70.0297
3121 | 2023-05-11 01:00 | 85.3291 | 53.53 | 10 | 0 | 0 | 0 | 1388.591
3122 | 2023-05-11 02:00 | 69.6262 | 53.53 | 10 | 0 | 0 | 0 | 1231.5622
3123 | 2023-05-11 03:00 | 68.3488 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1347.081
3124 | 2023-05-11 04:00 | 65.786 | 53.53 | 20 | 10 | 0 | 10.5 | 2386.3202
3125 | 2023-05-11 05:00 | 68.4417 | 53.53 | 10 | 0 | 0 | 10.5 | 1219.7172
3126 | 2023-05-11 06:00 | 63.5802 | 53.53 | 20 | 10 | 0 | 20 | 2342.2045
3127 | 2023-05-11 07:00 | 87.195 | 53.53 | 10 | 0 | 0 | 20 | 1407.2495
3128 | 2023-05-11 08:00 | 89.0046 | 65.03 | 10 | 0 | 0 | 20 | 1540.3459
3129 | 2023-05-11 09:00 | 96.8307 | 65.03 | 10 | 0 | 0 | 20 | 1618.6071
3130 | 2023-05-11 10:00 | 99.4494 | 65.03 | 0 | 0 | 10 | 10 | 0
3131 | 2023-05-11 11:00 | 89.3481 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1625.0323
3132 | 2023-05-11 12:00 | 94.2901 | 65.03 | 10 | 0 | 0 | 10.5 | 1593.2008
3133 | 2023-05-11 13:00 | 89.6327 | 65.03 | 10 | 0 | 0 | 10.5 | 1546.6273
3134 | 2023-05-11 14:00 | 90.2456 | 65.03 | 10 | 0 | 0 | 10.5 | 1552.7558
3135 | 2023-05-11 15:00 | 86.7375 | 65.03 | 20 | 10 | 0 | 20 | 3035.3497
3136 | 2023-05-11 16:00 | 105.4456 | 65.03 | 10 | 0 | 0 | 20 | 1704.7564
3137 | 2023-05-11 17:00 | 118.3164 | 66.4 | 0 | 0 | 10 | 10 | 0
3138 | 2023-05-11 18:00 | 113.2722 | 66.4 | 0 | 0 | 10 | 0 | 0
3139 | 2023-05-11 19:00 | -21.0889 | 65.03 | 20 | 10 | 0 | 9.5 | 878.8218
3140 | 2023-05-11 20:00 | -72.8645 | 65.03 | 20 | 10 | 0 | 19 | -156.6892
3141 | 2023-05-11 21:00 | 125.9771 | 65.03 | 0 | 0 | 10 | 9 | 0
3142 | 2023-05-11 22:00 | 87.2488 | 65.03 | 1 | 0 | 9 | 0 | 152.2788
3143 | 2023-05-11 23:00 | 85.8874 | 53.53 | 10 | 0 | 0 | 0 | 1394.1743
3144 | 2023-05-12 00:00 | 81.0861 | 53.53 | 10 | 0 | 0 | 0 | 1346.161
3145 | 2023-05-12 01:00 | 86.8527 | 53.53 | 10 | 0 | 0 | 0 | 1403.8267
3146 | 2023-05-12 02:00 | 71.0209 | 53.53 | 10 | 0 | 0 | 0 | 1245.5092
3147 | 2023-05-12 03:00 | 63.0584 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1288.6083
3148 | 2023-05-12 04:00 | -40.0892 | 53.53 | 20 | 10 | 0 | 10.5 | 268.8168
3149 | 2023-05-12 05:00 | -79.6225 | 53.53 | 20 | 10 | 0 | 20 | -521.8508
3150 | 2023-05-12 06:00 | 66.0115 | 53.53 | 10 | 0 | 0 | 20 | 1195.4153
3151 | 2023-05-12 07:00 | 77.9313 | 53.53 | 10 | 0 | 0 | 20 | 1314.6135
3152 | 2023-05-12 08:00 | 97.2426 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 81.1363
3153 | 2023-05-12 09:00 | 92.913 | 65.03 | 10 | 0 | 0 | 10.5 | 1579.4304
3154 | 2023-05-12 10:00 | 89.7285 | 65.03 | 10 | 0 | 0 | 10.5 | 1547.5851
3155 | 2023-05-12 11:00 | 88.7033 | 65.03 | 20 | 10 | 0 | 20 | 3074.6658
3156 | 2023-05-12 12:00 | 124.622 | 65.03 | 0 | 0 | 10 | 10 | 0
3157 | 2023-05-12 13:00 | 91.9983 | 65.03 | 10 | 0 | 0 | 10 | 1570.2831
3158 | 2023-05-12 14:00 | 85.046 | 65.03 | 20 | 10 | 0 | 19.5 | 3001.521
3159 | 2023-05-12 15:00 | 89.1737 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1623.1971
3160 | 2023-05-12 16:00 | 93.5145 | 65.03 | 10 | 0 | 0 | 20 | 1585.4452
3161 | 2023-05-12 17:00 | 113.3537 | 66.4 | 0 | 0 | 10 | 10 | 0
3162 | 2023-05-12 18:00 | 113.4256 | 66.4 | 0 | 0 | 10 | 0 | 0
3163 | 2023-05-12 19:00 | 114.5246 | 65.03 | 10 | 0 | 0 | 0 | 1795.5464
3164 | 2023-05-12 20:00 | 84.5009 | 65.03 | 10 | 0 | 0 | 0 | 1495.3092
3165 | 2023-05-12 21:00 | 91.5866 | 65.03 | 10 | 0 | 0 | 0 | 1566.1655
3166 | 2023-05-12 22:00 | 83.1204 | 65.03 | 10 | 0 | 0 | 0 | 1481.5035
3167 | 2023-05-12 23:00 | 79.6574 | 53.53 | 10 | 0 | 0 | 0 | 1331.8737
3168 | 2023-05-13 00:00 | 69.8817 | 53.53 | 10 | 0 | 0 | 0 | 1234.1167
3169 | 2023-05-13 01:00 | 68.4011 | 53.53 | 10 | 0 | 0 | 0 | 1219.3108
3170 | 2023-05-13 02:00 | 65.3011 | 53.53 | 10 | 0 | 0 | 0 | 1188.3113
3171 | 2023-05-13 03:00 | 61.6351 | 53.53 | 20 | 10 | 0 | 9.5 | 2303.3013
3172 | 2023-05-13 04:00 | 64.4094 | 53.53 | 10 | 0 | 0 | 9.5 | 1179.3936
3173 | 2023-05-13 05:00 | 56.1949 | 53.53 | 20 | 10 | 0 | 19 | 2194.498
3174 | 2023-05-13 06:00 | 62.4592 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1281.9857
3175 | 2023-05-13 07:00 | 65.6372 | 53.53 | 10 | 0 | 0 | 20 | 1191.6719
3176 | 2023-05-13 08:00 | 93.2868 | 53.53 | 0 | 0 | 10 | 10 | 0
3177 | 2023-05-13 09:00 | 87.2626 | 53.53 | 10 | 0 | 0 | 10 | 1407.9263
3178 | 2023-05-13 10:00 | 91.0732 | 53.53 | 0 | 0 | 10 | 0 | 0
3179 | 2023-05-13 11:00 | 88.9173 | 53.53 | 10 | 0 | 0 | 0 | 1424.473
3180 | 2023-05-13 12:00 | 79.4908 | 53.53 | 20 | 10 | 0 | 9.5 | 2660.4165
3181 | 2023-05-13 13:00 | 76.8484 | 53.53 | 20 | 10 | 0 | 19 | 2607.5677
3182 | 2023-05-13 14:00 | 81.0898 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1487.9026
3183 | 2023-05-13 15:00 | 90.5154 | 53.53 | 10 | 0 | 0 | 20 | 1440.4538
3184 | 2023-05-13 16:00 | 91.6487 | 53.53 | 10 | 0 | 0 | 20 | 1451.7871
3185 | 2023-05-13 17:00 | 92.4832 | 53.53 | 10 | 0 | 0 | 20 | 1460.1321
3186 | 2023-05-13 18:00 | 94.5241 | 53.53 | 0 | 0 | 10 | 10 | 0
3187 | 2023-05-13 19:00 | 96.0221 | 53.53 | 0 | 0 | 10 | 0 | 0
3188 | 2023-05-13 20:00 | 78.3571 | 53.53 | 10 | 0 | 0 | 0 | 1318.8715
3189 | 2023-05-13 21:00 | 72.5126 | 53.53 | 10 | 0 | 0 | 0 | 1260.4255
3190 | 2023-05-13 22:00 | -23.7615 | 53.53 | 20 | 10 | 0 | 9.5 | 595.3693
3191 | 2023-05-13 23:00 | 70.4356 | 53.53 | 10 | 0 | 0 | 9.5 | 1239.656
3192 | 2023-05-14 00:00 | 76.5537 | 53.53 | 0.5 | 0 | 9.5 | 0 | 65.0418
3193 | 2023-05-14 01:00 | 68.4421 | 53.53 | 10 | 0 | 0 | 0 | 1219.7205
3194 | 2023-05-14 02:00 | -52.6993 | 53.53 | 20 | 10 | 0 | 9.5 | 16.6147
3195 | 2023-05-14 03:00 | -10.9934 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 470.1411
3196 | 2023-05-14 04:00 | -55.4683 | 53.53 | 20 | 10 | 0 | 20 | -38.765
3197 | 2023-05-14 05:00 | 54.3969 | 53.53 | 10 | 0 | 0 | 20 | 1079.2694
3198 | 2023-05-14 06:00 | 64.8963 | 53.53 | 10 | 0 | 0 | 20 | 1184.2634
3199 | 2023-05-14 07:00 | 72.9501 | 53.53 | 10 | 0 | 0 | 20 | 1264.8013
3200 | 2023-05-14 08:00 | 81.9457 | 53.53 | 10 | 0 | 0 | 20 | 1354.7566
3201 | 2023-05-14 09:00 | 96.3413 | 53.53 | 0 | 0 | 10 | 10 | 0
3202 | 2023-05-14 10:00 | 83.7041 | 53.53 | 20 | 10 | 0 | 19.5 | 2744.6823
3203 | 2023-05-14 11:00 | 95.7194 | 53.53 | 1 | 0 | 9 | 10.5 | 149.2494
3204 | 2023-05-14 12:00 | 89.3317 | 53.53 | 10 | 0 | 0 | 10.5 | 1428.6173
3205 | 2023-05-14 13:00 | 83.4548 | 53.53 | 20 | 10 | 0 | 20 | 2739.6957
3206 | 2023-05-14 14:00 | 89.7677 | 53.53 | 10 | 0 | 0 | 20 | 1432.9773
3207 | 2023-05-14 15:00 | 88.421 | 53.53 | 10 | 0 | 0 | 20 | 1419.5099
3208 | 2023-05-14 16:00 | 94.8569 | 53.53 | 10 | 0 | 0 | 20 | 1483.8686
3209 | 2023-05-14 17:00 | 97.1062 | 53.53 | 10 | 0 | 0 | 20 | 1506.3617
3210 | 2023-05-14 18:00 | 101.2093 | 53.53 | 0 | 0 | 10 | 10 | 0
3211 | 2023-05-14 19:00 | 100.4412 | 53.53 | 0 | 0 | 10 | 0 | 0
3212 | 2023-05-14 20:00 | 86.7787 | 53.53 | 10 | 0 | 0 | 0 | 1403.0866
3213 | 2023-05-14 21:00 | 74.2794 | 53.53 | 20 | 10 | 0 | 9.5 | 2556.1878
3214 | 2023-05-14 22:00 | 89.8171 | 53.53 | 0.5 | 0 | 9.5 | 0 | 71.6735
3215 | 2023-05-14 23:00 | 79.6522 | 53.53 | 10 | 0 | 0 | 0 | 1331.8224
3216 | 2023-05-15 00:00 | -74.1991 | 53.53 | 20 | 10 | 0 | 9.5 | -413.3821
3217 | 2023-05-15 01:00 | -56.7159 | 53.53 | 20 | 10 | 0 | 19 | -63.7184
3218 | 2023-05-15 02:00 | -47.7431 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 63.9603
3219 | 2023-05-15 03:00 | 72.6633 | 53.53 | 1 | 0 | 9 | 11 | 126.1933
3220 | 2023-05-15 04:00 | 77.2566 | 53.53 | 0 | 0 | 10 | 1 | 0
3221 | 2023-05-15 05:00 | 64.5469 | 53.53 | 20 | 10 | 0 | 10.5 | 2361.5372
3222 | 2023-05-15 06:00 | -73.1627 | 53.53 | 20 | 10 | 0 | 20 | -392.6534
3223 | 2023-05-15 07:00 | 73.2754 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 63.4027
3224 | 2023-05-15 08:00 | -62.5308 | 65.03 | 20 | 10 | 0 | 20 | 49.9844
3225 | 2023-05-15 09:00 | 89.8304 | 65.03 | 10 | 0 | 0 | 20 | 1548.6037
3226 | 2023-05-15 10:00 | 87.8995 | 65.03 | 10 | 0 | 0 | 20 | 1529.2952
3227 | 2023-05-15 11:00 | 93.4321 | 65.03 | 10 | 0 | 0 | 20 | 1584.6211
3228 | 2023-05-15 12:00 | 98.969 | 65.03 | 0 | 0 | 10 | 10 | 0
3229 | 2023-05-15 13:00 | 85.0665 | 65.03 | 20 | 10 | 0 | 19.5 | 3001.9308
3230 | 2023-05-15 14:00 | 90.7486 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1639.7743
3231 | 2023-05-15 15:00 | 108.2224 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 86.6262
3232 | 2023-05-15 16:00 | 87.0051 | 65.03 | 20 | 10 | 0 | 20 | 3040.7028
3233 | 2023-05-15 17:00 | 116.3517 | 66.4 | 0 | 0 | 10 | 10 | 0
3234 | 2023-05-15 18:00 | 105.5148 | 66.4 | 10 | 0 | 0 | 10 | 1719.148
3235 | 2023-05-15 19:00 | 113.346 | 65.03 | 0 | 0 | 10 | 0 | 0
3236 | 2023-05-15 20:00 | 98.6446 | 65.03 | 10 | 0 | 0 | 0 | 1636.7464
3237 | 2023-05-15 21:00 | 95.1246 | 65.03 | 10 | 0 | 0 | 0 | 1601.546
3238 | 2023-05-15 22:00 | 96.7375 | 65.03 | 10 | 0 | 0 | 0 | 1617.6753
3239 | 2023-05-15 23:00 | 76.5954 | 53.53 | 20 | 10 | 0 | 9.5 | 2602.5071
3240 | 2023-05-16 00:00 | 93.8153 | 53.53 | 0.5 | 0 | 9.5 | 0 | 73.6727
3241 | 2023-05-16 01:00 | -40.3636 | 53.53 | 20 | 10 | 0 | 9.5 | 263.3289
3242 | 2023-05-16 02:00 | 65.9227 | 53.53 | 2 | 0 | 8 | 1.5 | 238.9053
3243 | 2023-05-16 03:00 | -75.2944 | 53.53 | 20 | 10 | 0 | 11 | -435.2883
3244 | 2023-05-16 04:00 | 67.8148 | 53.53 | 0 | 0 | 10 | 1 | 0
3245 | 2023-05-16 05:00 | -44.6882 | 53.53 | 20 | 10 | 0 | 10.5 | 176.8358
3246 | 2023-05-16 06:00 | -74.6628 | 53.53 | 20 | 10 | 0 | 20 | -422.6562
3247 | 2023-05-16 07:00 | 75.5734 | 53.53 | 10 | 0 | 0 | 20 | 1291.0339
3248 | 2023-05-16 08:00 | 101.3769 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 83.2034
3249 | 2023-05-16 09:00 | 95.3316 | 65.03 | 10 | 0 | 0 | 10.5 | 1603.6165
3250 | 2023-05-16 10:00 | 104.1915 | 65.03 | 0 | 0 | 10 | 0.5 | 0
3251 | 2023-05-16 11:00 | 93.5651 | 65.03 | 10 | 0 | 0 | 0.5 | 1585.9505
3252 | 2023-05-16 12:00 | 85.299 | 65.03 | 20 | 10 | 0 | 10 | 3006.5809
3253 | 2023-05-16 13:00 | 102.3036 | 65.03 | 0 | 0 | 10 | 0 | 0
3254 | 2023-05-16 14:00 | 91.2693 | 65.03 | 10 | 0 | 0 | 0 | 1562.9929
3255 | 2023-05-16 15:00 | 96.5995 | 65.03 | 10 | 0 | 0 | 0 | 1616.2954
3256 | 2023-05-16 16:00 | -32.1149 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 363.7981
3257 | 2023-05-16 17:00 | -66.339 | 66.4 | 20 | 10 | 0 | 10.5 | 1.2196
3258 | 2023-05-16 18:00 | -56.2558 | 66.4 | 20 | 10 | 0 | 20 | 202.8843
3259 | 2023-05-16 19:00 | 106.4915 | 65.03 | 0 | 0 | 10 | 10 | 0
3260 | 2023-05-16 20:00 | 89.7173 | 65.03 | 0.5 | 0 | 9.5 | 0.5 | 77.3737
3261 | 2023-05-16 21:00 | 81.9136 | 65.03 | 20 | 10 | 0 | 10 | 2938.872
3262 | 2023-05-16 22:00 | 91.5043 | 65.03 | 0 | 0 | 10 | 0 | 0
3263 | 2023-05-16 23:00 | 99.4448 | 53.53 | 10 | 0 | 0 | 0 | 1529.7479
3264 | 2023-05-17 00:00 | 80.4777 | 53.53 | 10 | 0 | 0 | 0 | 1340.0766
3265 | 2023-05-17 01:00 | 87.0447 | 53.53 | 10 | 0 | 0 | 0 | 1405.7468
3266 | 2023-05-17 02:00 | 49.856 | 53.53 | 20 | 10 | 0 | 9.5 | 2067.7207
3267 | 2023-05-17 03:00 | 63.608 | 53.53 | 10 | 0 | 0 | 9.5 | 1171.3804
3268 | 2023-05-17 04:00 | 61.6574 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1273.1235
3269 | 2023-05-17 05:00 | 58.4552 | 53.53 | 20 | 10 | 0 | 20 | 2239.7035
3270 | 2023-05-17 06:00 | 73.4795 | 53.53 | 10 | 0 | 0 | 20 | 1270.0953
3271 | 2023-05-17 07:00 | 81.5674 | 53.53 | 10 | 0 | 0 | 20 | 1350.9741
3272 | 2023-05-17 08:00 | 92.602 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 78.816
3273 | 2023-05-17 09:00 | 91.2235 | 65.03 | 10 | 0 | 0 | 10.5 | 1562.5355
3274 | 2023-05-17 10:00 | 82.9653 | 65.03 | 20 | 10 | 0 | 20 | 2959.906
3275 | 2023-05-17 11:00 | 86.6998 | 65.03 | 10 | 0 | 0 | 20 | 1517.2976
3276 | 2023-05-17 12:00 | 102.2532 | 65.03 | 0 | 0 | 10 | 10 | 0
3277 | 2023-05-17 13:00 | 82.1734 | 65.03 | 20 | 10 | 0 | 19.5 | 2944.0683
3278 | 2023-05-17 14:00 | 88.7637 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1618.8815
3279 | 2023-05-17 15:00 | 91.0732 | 65.03 | 10 | 0 | 0 | 20 | 1561.0318
3280 | 2023-05-17 16:00 | 111.079 | 65.03 | 0 | 0 | 10 | 10 | 0
3281 | 2023-05-17 17:00 | 115.3816 | 66.4 | 0 | 0 | 10 | 0 | 0
3282 | 2023-05-17 18:00 | 105.0501 | 66.4 | 10 | 0 | 0 | 0 | 1714.501
3283 | 2023-05-17 19:00 | -62.8208 | 65.03 | 20 | 10 | 0 | 9.5 | 44.1842
3284 | 2023-05-17 20:00 | -68.9006 | 65.03 | 20 | 10 | 0 | 19 | -77.4119
3285 | 2023-05-17 21:00 | 97.737 | 65.03 | 0 | 0 | 10 | 9 | 0
3286 | 2023-05-17 22:00 | 80.5284 | 65.03 | 1 | 0 | 9 | 0 | 145.5584
3287 | 2023-05-17 23:00 | -63.0479 | 53.53 | 20 | 10 | 0 | 9.5 | -190.3576
3288 | 2023-05-18 00:00 | -52.6162 | 53.53 | 20 | 10 | 0 | 19 | 18.2767
3289 | 2023-05-18 01:00 | 77.2611 | 53.53 | 0 | 0 | 10 | 9 | 0
3290 | 2023-05-18 02:00 | 62.3216 | 53.53 | 10 | 0 | 0 | 9 | 1158.5164
3291 | 2023-05-18 03:00 | 66.0674 | 53.53 | 10 | 0 | 0 | 9 | 1195.9737
3292 | 2023-05-18 04:00 | 60.4499 | 53.53 | 20 | 10 | 0 | 18.5 | 2279.5987
3293 | 2023-05-18 05:00 | 68.4181 | 53.53 | 2 | 0 | 8 | 10.5 | 243.8963
3294 | 2023-05-18 06:00 | 59.8869 | 53.53 | 20 | 10 | 0 | 20 | 2268.3374
3295 | 2023-05-18 07:00 | 89.0122 | 53.53 | 10 | 0 | 0 | 20 | 1425.4223
3296 | 2023-05-18 08:00 | 97.445 | 65.03 | 10 | 0 | 0 | 20 | 1624.7504
3297 | 2023-05-18 09:00 | 93.4455 | 65.03 | 10 | 0 | 0 | 20 | 1584.7553
3298 | 2023-05-18 10:00 | 90.7977 | 65.03 | 10 | 0 | 0 | 20 | 1558.2775
3299 | 2023-05-18 11:00 | 95.0611 | 65.03 | 10 | 0 | 0 | 20 | 1600.9109
3300 | 2023-05-18 12:00 | 98.3854 | 65.03 | 10 | 0 | 0 | 20 | 1634.1538
3301 | 2023-05-18 13:00 | 115.3037 | 65.03 | 0 | 0 | 10 | 10 | 0
3302 | 2023-05-18 14:00 | 102.037 | 65.03 | 20 | 10 | 0 | 19.5 | 3341.3402
3303 | 2023-05-18 15:00 | 102.4026 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1762.4481
3304 | 2023-05-18 16:00 | 132.043 | 65.03 | 0 | 0 | 10 | 10 | 0
3305 | 2023-05-18 17:00 | 113.0836 | 66.4 | 10 | 0 | 0 | 10 | 1794.8355
3306 | 2023-05-18 18:00 | 112.8107 | 66.4 | 10 | 0 | 0 | 10 | 1792.1066
3307 | 2023-05-18 19:00 | 114.7774 | 65.03 | 0 | 0 | 10 | 0 | 0
3308 | 2023-05-18 20:00 | 82.369 | 65.03 | 10 | 0 | 0 | 0 | 1473.9901
3309 | 2023-05-18 21:00 | 85.7812 | 65.03 | 10 | 0 | 0 | 0 | 1508.112
3310 | 2023-05-18 22:00 | 85.3762 | 65.03 | 10 | 0 | 0 | 0 | 1504.0622
3311 | 2023-05-18 23:00 | 89.2593 | 53.53 | 10 | 0 | 0 | 0 | 1427.8934
3312 | 2023-05-19 00:00 | 82.6255 | 53.53 | 10 | 0 | 0 | 0 | 1361.5554
3313 | 2023-05-19 01:00 | 84.9568 | 53.53 | 10 | 0 | 0 | 0 | 1384.8678
3314 | 2023-05-19 02:00 | 73.5419 | 53.53 | 10 | 0 | 0 | 0 | 1270.7188
3315 | 2023-05-19 03:00 | 71.2874 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1379.5605
3316 | 2023-05-19 04:00 | 62.7144 | 53.53 | 20 | 10 | 0 | 10.5 | 2324.887
3317 | 2023-05-19 05:00 | 59.3461 | 53.53 | 20 | 10 | 0 | 20 | 2257.5229
3318 | 2023-05-19 06:00 | 74.0425 | 53.53 | 10 | 0 | 0 | 20 | 1275.7246
3319 | 2023-05-19 07:00 | 90.4316 | 53.53 | 10 | 0 | 0 | 20 | 1439.6158
3320 | 2023-05-19 08:00 | 84.3389 | 65.03 | 10 | 0 | 0 | 20 | 1493.6888
3321 | 2023-05-19 09:00 | 91.6566 | 65.03 | 10 | 0 | 0 | 20 | 1566.866
3322 | 2023-05-19 10:00 | 95.171 | 65.03 | 10 | 0 | 0 | 20 | 1602.0101
3323 | 2023-05-19 11:00 | 100.4783 | 65.03 | 10 | 0 | 0 | 20 | 1655.0833
3324 | 2023-05-19 12:00 | 101.7468 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 83.3884
3325 | 2023-05-19 13:00 | 96.1209 | 65.03 | 10 | 0 | 0 | 10.5 | 1611.5091
3326 | 2023-05-19 14:00 | 98.6966 | 65.03 | 10 | 0 | 0 | 10.5 | 1637.2657
3327 | 2023-05-19 15:00 | 94.384 | 65.03 | 10 | 0 | 0 | 10.5 | 1594.1399
3328 | 2023-05-19 16:00 | 89.3225 | 65.03 | 20 | 10 | 0 | 20 | 3087.0501
3329 | 2023-05-19 17:00 | 107.0136 | 66.4 | 10 | 0 | 0 | 20 | 1734.1365
3330 | 2023-05-19 18:00 | 109.0411 | 66.4 | 0 | 0 | 10 | 10 | 0
3331 | 2023-05-19 19:00 | 108.6396 | 65.03 | 0 | 0 | 10 | 0 | 0
3332 | 2023-05-19 20:00 | 78.0978 | 65.03 | 20 | 10 | 0 | 9.5 | 2862.5553
3333 | 2023-05-19 21:00 | 86.0881 | 65.03 | 10 | 0 | 0 | 9.5 | 1511.1806
3334 | 2023-05-19 22:00 | 89.3234 | 65.03 | 0.5 | 0 | 9.5 | 0 | 77.1767
3335 | 2023-05-19 23:00 | 81.8746 | 53.53 | 10 | 0 | 0 | 0 | 1354.0464
3336 | 2023-05-20 00:00 | 74.114 | 53.53 | 10 | 0 | 0 | 0 | 1276.44
3337 | 2023-05-20 01:00 | 79.8397 | 53.53 | 10 | 0 | 0 | 0 | 1333.6971
3338 | 2023-05-20 02:00 | 48.9852 | 53.53 | 20 | 10 | 0 | 9.5 | 2050.3044
3339 | 2023-05-20 03:00 | 46.2383 | 53.53 | 20 | 10 | 0 | 19 | 1995.3659
3340 | 2023-05-20 04:00 | 53.4188 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1182.0655
3341 | 2023-05-20 05:00 | 62.3392 | 53.53 | 10 | 0 | 0 | 20 | 1158.6922
3342 | 2023-05-20 06:00 | 72.3754 | 53.53 | 10 | 0 | 0 | 20 | 1259.0542
3343 | 2023-05-20 07:00 | 82.5096 | 53.53 | 10 | 0 | 0 | 20 | 1360.3959
3344 | 2023-05-20 08:00 | 76.9915 | 53.53 | 10 | 0 | 0 | 20 | 1305.215
3345 | 2023-05-20 09:00 | 84.2149 | 53.53 | 10 | 0 | 0 | 20 | 1377.4491
3346 | 2023-05-20 10:00 | 87.8991 | 53.53 | 10 | 0 | 0 | 20 | 1414.291
3347 | 2023-05-20 11:00 | 87.2664 | 53.53 | 10 | 0 | 0 | 20 | 1407.9636
3348 | 2023-05-20 12:00 | 90.2887 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 71.9093
3349 | 2023-05-20 13:00 | 79.8854 | 53.53 | 20 | 10 | 0 | 20 | 2668.3086
3350 | 2023-05-20 14:00 | 86.3902 | 53.53 | 10 | 0 | 0 | 20 | 1399.2015
3351 | 2023-05-20 15:00 | 89.2581 | 53.53 | 10 | 0 | 0 | 20 | 1427.8811
3352 | 2023-05-20 16:00 | 92.9252 | 53.53 | 10 | 0 | 0 | 20 | 1464.5524
3353 | 2023-05-20 17:00 | 95.5303 | 53.53 | 0 | 0 | 10 | 10 | 0
3354 | 2023-05-20 18:00 | 98.4391 | 53.53 | 0 | 0 | 10 | 0 | 0
3355 | 2023-05-20 19:00 | 87.007 | 53.53 | 10 | 0 | 0 | 0 | 1405.3703
3356 | 2023-05-20 20:00 | 76.646 | 53.53 | 10 | 0 | 0 | 0 | 1301.7604
3357 | 2023-05-20 21:00 | 77.259 | 53.53 | 10 | 0 | 0 | 0 | 1307.8898
3358 | 2023-05-20 22:00 | 74.3103 | 53.53 | 10 | 0 | 0 | 0 | 1278.4027
3359 | 2023-05-20 23:00 | 77.1718 | 53.53 | 10 | 0 | 0 | 0 | 1307.0177
3360 | 2023-05-21 00:00 | 75.4822 | 53.53 | 10 | 0 | 0 | 0 | 1290.1222
3361 | 2023-05-21 01:00 | 63.5921 | 53.53 | 10 | 0 | 0 | 0 | 1171.2208
3362 | 2023-05-21 02:00 | 57.568 | 53.53 | 10 | 0 | 0 | 0 | 1110.9801
3363 | 2023-05-21 03:00 | 49.8213 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1142.304
3364 | 2023-05-21 04:00 | -23.8168 | 53.53 | 20 | 10 | 0 | 10.5 | 594.2644
3365 | 2023-05-21 05:00 | 47.9171 | 53.53 | 20 | 10 | 0 | 20 | 2028.9427
3366 | 2023-05-21 06:00 | 56.1244 | 53.53 | 10 | 0 | 0 | 20 | 1096.5437
3367 | 2023-05-21 07:00 | 73.8623 | 53.53 | 10 | 0 | 0 | 20 | 1273.9228
3368 | 2023-05-21 08:00 | 88.2781 | 53.53 | 0 | 0 | 10 | 10 | 0
3369 | 2023-05-21 09:00 | 86.8512 | 53.53 | 1 | 0 | 9 | 1 | 140.3812
3370 | 2023-05-21 10:00 | 84.056 | 53.53 | 10 | 0 | 0 | 1 | 1375.8599
3371 | 2023-05-21 11:00 | 76.6665 | 53.53 | 20 | 10 | 0 | 10.5 | 2603.9298
3372 | 2023-05-21 12:00 | 76.9484 | 53.53 | 20 | 10 | 0 | 20 | 2609.5676
3373 | 2023-05-21 13:00 | 81.8812 | 53.53 | 10 | 0 | 0 | 20 | 1354.1125
3374 | 2023-05-21 14:00 | 85.8363 | 53.53 | 10 | 0 | 0 | 20 | 1393.6628
3375 | 2023-05-21 15:00 | 81.7285 | 53.53 | 10 | 0 | 0 | 20 | 1352.5846
3376 | 2023-05-21 16:00 | 91.056 | 53.53 | 10 | 0 | 0 | 20 | 1445.8598
3377 | 2023-05-21 17:00 | 98.8895 | 53.53 | 0 | 0 | 10 | 10 | 0
3378 | 2023-05-21 18:00 | 94.6142 | 53.53 | 10 | 0 | 0 | 10 | 1481.4418
3379 | 2023-05-21 19:00 | 98.8972 | 53.53 | 0 | 0 | 10 | 0 | 0
3380 | 2023-05-21 20:00 | 82.651 | 53.53 | 20 | 10 | 0 | 9.5 | 2723.6193
3381 | 2023-05-21 21:00 | 83.4576 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1441.9751
3382 | 2023-05-21 22:00 | 99.8192 | 53.53 | 0 | 0 | 10 | 0 | 0
3383 | 2023-05-21 23:00 | 71.3528 | 53.53 | 20 | 10 | 0 | 9.5 | 2497.6562
3384 | 2023-05-22 00:00 | 83.3532 | 53.53 | 10 | 0 | 0 | 9.5 | 1368.8325
3385 | 2023-05-22 01:00 | 87.3075 | 53.53 | 0.5 | 0 | 9.5 | 0 | 70.4188
3386 | 2023-05-22 02:00 | 63.7232 | 53.53 | 10 | 0 | 0 | 0 | 1172.5325
3387 | 2023-05-22 03:00 | 60.412 | 53.53 | 10 | 0 | 0 | 0 | 1139.4202
3388 | 2023-05-22 04:00 | 54.6052 | 53.53 | 20 | 10 | 0 | 9.5 | 2162.7037
3389 | 2023-05-22 05:00 | 60.3462 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1258.6314
3390 | 2023-05-22 06:00 | -58.1176 | 53.53 | 20 | 10 | 0 | 20 | -91.7522
3391 | 2023-05-22 07:00 | 73.7913 | 53.53 | 10 | 0 | 0 | 20 | 1273.2134
3392 | 2023-05-22 08:00 | 88.5895 | 65.03 | 10 | 0 | 0 | 20 | 1536.1951
3393 | 2023-05-22 09:00 | 87.159 | 65.03 | 10 | 0 | 0 | 20 | 1521.8895
3394 | 2023-05-22 10:00 | 98.6835 | 65.03 | 0 | 0 | 10 | 10 | 0
3395 | 2023-05-22 11:00 | 98.8385 | 65.03 | 0 | 0 | 10 | 0 | 0
3396 | 2023-05-22 12:00 | 87.9606 | 65.03 | 20 | 10 | 0 | 9.5 | 3059.8119
3397 | 2023-05-22 13:00 | 92.0208 | 65.03 | 10 | 0 | 0 | 9.5 | 1570.5083
3398 | 2023-05-22 14:00 | 83.2147 | 65.03 | 20 | 10 | 0 | 19 | 2964.8933
3399 | 2023-05-22 15:00 | 90.4526 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1718.4916
3400 | 2023-05-22 16:00 | 97.0771 | 65.03 | 10 | 0 | 0 | 20 | 1621.0712
3401 | 2023-05-22 17:00 | 115.9182 | 66.4 | 0 | 0 | 10 | 10 | 0
3402 | 2023-05-22 18:00 | 104.0837 | 66.4 | 0 | 0 | 10 | 0 | 0
3403 | 2023-05-22 19:00 | -25.4531 | 65.03 | 20 | 10 | 0 | 9.5 | 791.5376
3404 | 2023-05-22 20:00 | -10.8335 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 599.0141
3405 | 2023-05-22 21:00 | -60.3798 | 65.03 | 20 | 10 | 0 | 20 | 93.0045
3406 | 2023-05-22 22:00 | 94.8298 | 65.03 | 0 | 0 | 10 | 10 | 0
3407 | 2023-05-22 23:00 | 100.1715 | 53.53 | 0 | 0 | 10 | 0 | 0
3408 | 2023-05-23 00:00 | 87.887 | 53.53 | 10 | 0 | 0 | 0 | 1414.1699
3409 | 2023-05-23 01:00 | 83.5976 | 53.53 | 10 | 0 | 0 | 0 | 1371.2756
3410 | 2023-05-23 02:00 | 51.8383 | 53.53 | 20 | 10 | 0 | 9.5 | 2107.3655
3411 | 2023-05-23 03:00 | 52.5265 | 53.53 | 20 | 10 | 0 | 19 | 2121.1303
3412 | 2023-05-23 04:00 | 64.888 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 177.6269
3413 | 2023-05-23 05:00 | 61.352 | 53.53 | 10 | 0 | 0 | 10.5 | 1148.8204
3414 | 2023-05-23 06:00 | 56.84 | 53.53 | 20 | 10 | 0 | 20 | 2207.3993
3415 | 2023-05-23 07:00 | 84.3947 | 53.53 | 10 | 0 | 0 | 20 | 1379.2466
3416 | 2023-05-23 08:00 | 94.7769 | 65.03 | 10 | 0 | 0 | 20 | 1598.0688
3417 | 2023-05-23 09:00 | 102.0867 | 65.03 | 10 | 0 | 0 | 20 | 1671.1671
3418 | 2023-05-23 10:00 | 94.9441 | 65.03 | 10 | 0 | 0 | 20 | 1599.7411
3419 | 2023-05-23 11:00 | 105.0381 | 65.03 | 0 | 0 | 10 | 10 | 0
3420 | 2023-05-23 12:00 | 93.9583 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1673.5614
3421 | 2023-05-23 13:00 | 93.0481 | 65.03 | 20 | 10 | 0 | 20 | 3161.5617
3422 | 2023-05-23 14:00 | 103.3022 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 84.1661
3423 | 2023-05-23 15:00 | 87.5389 | 65.03 | 20 | 10 | 0 | 20 | 3051.3787
3424 | 2023-05-23 16:00 | 127.059 | 65.03 | 0 | 0 | 10 | 10 | 0
3425 | 2023-05-23 17:00 | 111.8773 | 66.4 | 10 | 0 | 0 | 10 | 1782.7727
3426 | 2023-05-23 18:00 | 111.9241 | 66.4 | 0 | 0 | 10 | 0 | 0
3427 | 2023-05-23 19:00 | 113.1637 | 65.03 | 10 | 0 | 0 | 0 | 1781.9367
3428 | 2023-05-23 20:00 | 107.8028 | 65.03 | 10 | 0 | 0 | 0 | 1728.328
3429 | 2023-05-23 21:00 | 95.6082 | 65.03 | 10 | 0 | 0 | 0 | 1606.3818
3430 | 2023-05-23 22:00 | 79.3444 | 65.03 | 10 | 0 | 0 | 0 | 1443.7444
3431 | 2023-05-23 23:00 | 96.987 | 53.53 | 10 | 0 | 0 | 0 | 1505.1698
3432 | 2023-05-24 00:00 | 81.468 | 53.53 | 10 | 0 | 0 | 0 | 1349.9797
3433 | 2023-05-24 01:00 | 84.715 | 53.53 | 10 | 0 | 0 | 0 | 1382.4503
3434 | 2023-05-24 02:00 | 55.9304 | 53.53 | 20 | 10 | 0 | 9.5 | 2189.2081
3435 | 2023-05-24 03:00 | 68.1734 | 53.53 | 1.5 | 0 | 8.5 | 1 | 182.5551
3436 | 2023-05-24 04:00 | 59.4607 | 53.53 | 20 | 10 | 0 | 10.5 | 2259.8139
3437 | 2023-05-24 05:00 | 64.661 | 53.53 | 10 | 0 | 0 | 10.5 | 1181.9098
3438 | 2023-05-24 06:00 | 61.8558 | 53.53 | 20 | 10 | 0 | 20 | 2307.7168
3439 | 2023-05-24 07:00 | 103.4379 | 53.53 | 10 | 0 | 0 | 20 | 1569.6795
3440 | 2023-05-24 08:00 | 114.2095 | 65.03 | 0 | 0 | 10 | 10 | 0
3441 | 2023-05-24 09:00 | 94.2496 | 65.03 | 10 | 0 | 0 | 10 | 1592.796
3442 | 2023-05-24 10:00 | 94.3828 | 65.03 | 10 | 0 | 0 | 10 | 1594.1277
3443 | 2023-05-24 11:00 | 91.2487 | 65.03 | 10 | 0 | 0 | 10 | 1562.7868
3444 | 2023-05-24 12:00 | 103.7352 | 65.03 | 0 | 0 | 10 | 0 | 0
3445 | 2023-05-24 13:00 | 91.5492 | 65.03 | 10 | 0 | 0 | 0 | 1565.7921
3446 | 2023-05-24 14:00 | 90.9298 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1723.7666
3447 | 2023-05-24 15:00 | -31.947 | 65.03 | 20 | 10 | 0 | 10.5 | 661.6605
3448 | 2023-05-24 16:00 | -67.3701 | 65.03 | 20 | 10 | 0 | 20 | -46.801
3449 | 2023-05-24 17:00 | 108.6167 | 66.4 | 0 | 0 | 10 | 10 | 0
3450 | 2023-05-24 18:00 | 99.4549 | 66.4 | 10 | 0 | 0 | 10 | 1658.5487
3451 | 2023-05-24 19:00 | 114.7791 | 65.03 | 0 | 0 | 10 | 0 | 0
3452 | 2023-05-24 20:00 | 108.6503 | 65.03 | 10 | 0 | 0 | 0 | 1736.803
3453 | 2023-05-24 21:00 | -73.7505 | 65.03 | 20 | 10 | 0 | 9.5 | -174.4093
3454 | 2023-05-24 22:00 | -30.1418 | 65.03 | 1.5 | 0 | 8.5 | 1 | 52.3323
3455 | 2023-05-24 23:00 | -26.6653 | 53.53 | 20 | 10 | 0 | 10.5 | 537.2945
3456 | 2023-05-25 00:00 | -43.1839 | 53.53 | 20 | 10 | 0 | 20 | 206.9216
3457 | 2023-05-25 01:00 | 77.7373 | 53.53 | 0 | 0 | 10 | 10 | 0
3458 | 2023-05-25 02:00 | 62.2471 | 53.53 | 11.0526 | 1.0526 | 0 | 11 | 1279.6418
3459 | 2023-05-25 03:00 | 70.4157 | 53.53 | 0 | 0 | 10 | 1 | 0
3460 | 2023-05-25 04:00 | 64.6737 | 53.53 | 10 | 0 | 0 | 1 | 1182.0374
3461 | 2023-05-25 05:00 | 55.2623 | 53.53 | 20 | 10 | 0 | 10.5 | 2175.846
3462 | 2023-05-25 06:00 | 55.7486 | 53.53 | 20 | 10 | 0 | 20 | 2185.5717
3463 | 2023-05-25 07:00 | 75.4176 | 53.53 | 10 | 0 | 0 | 20 | 1289.4756
3464 | 2023-05-25 08:00 | 97.8698 | 65.03 | 10 | 0 | 0 | 20 | 1628.9978
3465 | 2023-05-25 09:00 | 115.3329 | 65.03 | 0 | 0 | 10 | 10 | 0
3466 | 2023-05-25 10:00 | 106.5212 | 65.03 | 1.5 | 0 | 8.5 | 1.5 | 257.3268
3467 | 2023-05-25 11:00 | -14.0363 | 65.03 | 20 | 10 | 0 | 11 | 1019.8731
3468 | 2023-05-25 12:00 | 107.1887 | 65.03 | 0 | 0 | 10 | 1 | 0
3469 | 2023-05-25 13:00 | 102.007 | 65.03 | 10 | 0 | 0 | 1 | 1670.37
3470 | 2023-05-25 14:00 | 84.6238 | 65.03 | 20 | 10 | 0 | 10.5 | 2993.0768
3471 | 2023-05-25 15:00 | 91.7247 | 65.03 | 20 | 10 | 0 | 20 | 3135.093
3472 | 2023-05-25 16:00 | 103.6258 | 65.03 | 10 | 0 | 0 | 20 | 1686.5583
3473 | 2023-05-25 17:00 | 113.387 | 66.4 | 0 | 0 | 10 | 10 | 0
3474 | 2023-05-25 18:00 | 100.7786 | 66.4 | 10 | 0 | 0 | 10 | 1671.7861
3475 | 2023-05-25 19:00 | 113.9254 | 65.03 | 0 | 0 | 10 | 0 | 0
3476 | 2023-05-25 20:00 | 77.0641 | 65.03 | 20 | 10 | 0 | 9.5 | 2841.8829
3477 | 2023-05-25 21:00 | 87.2818 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1603.2818
3478 | 2023-05-25 22:00 | 99.0707 | 65.03 | 0 | 0 | 10 | 0 | 0
3479 | 2023-05-25 23:00 | 84.0366 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1448.0699
3480 | 2023-05-26 00:00 | 80.4229 | 53.53 | 20 | 10 | 0 | 10 | 2679.0573
3481 | 2023-05-26 01:00 | 91.5429 | 53.53 | 0 | 0 | 10 | 0 | 0
3482 | 2023-05-26 02:00 | 72.3901 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1391.7488
3483 | 2023-05-26 03:00 | 75.9342 | 53.53 | 10 | 0 | 0 | 1 | 1294.6421
3484 | 2023-05-26 04:00 | 71.3963 | 53.53 | 20 | 10 | 0 | 10.5 | 2498.5261
3485 | 2023-05-26 05:00 | 73.4787 | 53.53 | 10 | 0 | 0 | 10.5 | 1270.0875
3486 | 2023-05-26 06:00 | 70.0463 | 53.53 | 20 | 10 | 0 | 20 | 2471.5251
3487 | 2023-05-26 07:00 | 85.9712 | 53.53 | 10 | 0 | 0 | 20 | 1395.0124
3488 | 2023-05-26 08:00 | 94.5787 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 79.8044
3489 | 2023-05-26 09:00 | 92.1807 | 65.03 | 10 | 0 | 0 | 10.5 | 1572.1071
3490 | 2023-05-26 10:00 | 86.2756 | 65.03 | 20 | 10 | 0 | 20 | 3026.1123
3491 | 2023-05-26 11:00 | 87.6687 | 65.03 | 10 | 0 | 0 | 20 | 1526.9873
3492 | 2023-05-26 12:00 | 91.8702 | 65.03 | 10 | 0 | 0 | 20 | 1569.002
3493 | 2023-05-26 13:00 | 95.7764 | 65.03 | 10 | 0 | 0 | 20 | 1608.064
3494 | 2023-05-26 14:00 | 107.4161 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 86.223
3495 | 2023-05-26 15:00 | 93.5868 | 65.03 | 20 | 10 | 0 | 20 | 3172.3357
3496 | 2023-05-26 16:00 | 102.68 | 65.03 | 10 | 0 | 0 | 20 | 1677.0999
3497 | 2023-05-26 17:00 | 118.4574 | 66.4 | 0 | 0 | 10 | 10 | 0
3498 | 2023-05-26 18:00 | 107.2213 | 66.4 | 10 | 0 | 0 | 10 | 1736.2135
3499 | 2023-05-26 19:00 | 113.7811 | 65.03 | 0 | 0 | 10 | 0 | 0
3500 | 2023-05-26 20:00 | 87.137 | 65.03 | 20 | 10 | 0 | 9.5 | 3043.3394
3501 | 2023-05-26 21:00 | 101.0688 | 65.03 | 0.5 | 0 | 9.5 | 0 | 83.0494
3502 | 2023-05-26 22:00 | 94.1523 | 65.03 | 10 | 0 | 0 | 0 | 1591.8232
3503 | 2023-05-26 23:00 | 76.3901 | 53.53 | 20 | 10 | 0 | 9.5 | 2598.4016
3504 | 2023-05-27 00:00 | 77.1396 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1375.4692
3505 | 2023-05-27 01:00 | 91.8875 | 53.53 | 0 | 0 | 10 | 0 | 0
3506 | 2023-05-27 02:00 | 54.5754 | 53.53 | 20 | 10 | 0 | 9.5 | 2162.1073
3507 | 2023-05-27 03:00 | 59.4921 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1249.1918
3508 | 2023-05-27 04:00 | 60.3467 | 53.53 | 10 | 0 | 0 | 10.5 | 1138.767
3509 | 2023-05-27 05:00 | 49.2164 | 53.53 | 20 | 10 | 0 | 20 | 2054.9279
3510 | 2023-05-27 06:00 | 60.0376 | 53.53 | 10 | 0 | 0 | 20 | 1135.6762
3511 | 2023-05-27 07:00 | 67.3549 | 53.53 | 10 | 0 | 0 | 20 | 1208.8488
3512 | 2023-05-27 08:00 | 81.6202 | 53.53 | 10 | 0 | 0 | 20 | 1351.5015
3513 | 2023-05-27 09:00 | 95.4202 | 53.53 | 0 | 0 | 10 | 10 | 0
3514 | 2023-05-27 10:00 | 88.7224 | 53.53 | 10 | 0 | 0 | 10 | 1422.5241
3515 | 2023-05-27 11:00 | 83.7159 | 53.53 | 11.5789 | 1.5789 | 0 | 11.5 | 1589.1632
3516 | 2023-05-27 12:00 | 89.4814 | 53.53 | 10 | 0 | 0 | 11.5 | 1430.1136
3517 | 2023-05-27 13:00 | 85.4517 | 53.53 | 10 | 0 | 0 | 11.5 | 1389.8165
3518 | 2023-05-27 14:00 | 85.9928 | 53.53 | 10 | 0 | 0 | 11.5 | 1395.2282
3519 | 2023-05-27 15:00 | 91.3433 | 53.53 | 0 | 0 | 10 | 1.5 | 0
3520 | 2023-05-27 16:00 | -18.7515 | 53.53 | 20 | 10 | 0 | 11 | 695.5694
3521 | 2023-05-27 17:00 | 101.2027 | 53.53 | 0 | 0 | 10 | 1 | 0
3522 | 2023-05-27 18:00 | -76.4559 | 53.53 | 20 | 10 | 0 | 10.5 | -458.519
3523 | 2023-05-27 19:00 | 91.4348 | 53.53 | 0 | 0 | 10 | 0.5 | 0
3524 | 2023-05-27 20:00 | 74.866 | 53.53 | 20 | 10 | 0 | 10 | 2567.9207
3525 | 2023-05-27 21:00 | 95.9166 | 53.53 | 0 | 0 | 10 | 0 | 0
3526 | 2023-05-27 22:00 | 83.9568 | 53.53 | 10 | 0 | 0 | 0 | 1374.8684
3527 | 2023-05-27 23:00 | 67.7054 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1276.1618
3528 | 2023-05-28 00:00 | 66.6472 | 53.53 | 20 | 10 | 0 | 10 | 2403.5438
3529 | 2023-05-28 01:00 | 75.0711 | 53.53 | 0 | 0 | 10 | 0 | 0
3530 | 2023-05-28 02:00 | 70.8325 | 53.53 | 10 | 0 | 0 | 0 | 1243.6245
3531 | 2023-05-28 03:00 | -79.3354 | 53.53 | 20 | 10 | 0 | 9.5 | -516.1072
3532 | 2023-05-28 04:00 | -20.9145 | 53.53 | 20 | 10 | 0 | 19 | 652.311
3533 | 2023-05-28 05:00 | 58.6822 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1240.2397
3534 | 2023-05-28 06:00 | 59.6947 | 53.53 | 10 | 0 | 0 | 20 | 1132.2472
3535 | 2023-05-28 07:00 | 67.6443 | 53.53 | 10 | 0 | 0 | 20 | 1211.7431
3536 | 2023-05-28 08:00 | 94.0182 | 53.53 | 0 | 0 | 10 | 10 | 0
3537 | 2023-05-28 09:00 | 83.5084 | 53.53 | 10 | 0 | 0 | 10 | 1370.3839
3538 | 2023-05-28 10:00 | 93.2868 | 53.53 | 0 | 0 | 10 | 0 | 0
3539 | 2023-05-28 11:00 | 80.4806 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1481.1696
3540 | 2023-05-28 12:00 | -39.5215 | 53.53 | 20 | 10 | 0 | 10.5 | 280.1709
3541 | 2023-05-28 13:00 | -26.3493 | 53.53 | 20 | 10 | 0 | 20 | 543.6145
3542 | 2023-05-28 14:00 | 84.7693 | 53.53 | 10 | 0 | 0 | 20 | 1382.9934
3543 | 2023-05-28 15:00 | 89.1242 | 53.53 | 10 | 0 | 0 | 20 | 1426.5419
3544 | 2023-05-28 16:00 | 83.9781 | 53.53 | 10 | 0 | 0 | 20 | 1375.0808
3545 | 2023-05-28 17:00 | 96.475 | 53.53 | 10 | 0 | 0 | 20 | 1500.0498
3546 | 2023-05-28 18:00 | 116.3667 | 53.53 | 0 | 0 | 10 | 10 | 0
3547 | 2023-05-28 19:00 | 110.144 | 53.53 | 0 | 0 | 10 | 0 | 0
3548 | 2023-05-28 20:00 | 75.7962 | 53.53 | 20 | 10 | 0 | 9.5 | 2586.525
3549 | 2023-05-28 21:00 | 85.5467 | 53.53 | 0.5 | 0 | 9.5 | 0 | 69.5384
3550 | 2023-05-28 22:00 | 75.9051 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1362.4748
3551 | 2023-05-28 23:00 | 68.4205 | 53.53 | 20 | 10 | 0 | 10 | 2439.0107
3552 | 2023-05-29 00:00 | 92.9888 | 53.53 | 0 | 0 | 10 | 0 | 0
3553 | 2023-05-29 01:00 | 73.8922 | 53.53 | 10 | 0 | 0 | 0 | 1274.2224
3554 | 2023-05-29 02:00 | 71.9123 | 53.53 | 10 | 0 | 0 | 0 | 1254.4234
3555 | 2023-05-29 03:00 | 62.073 | 53.53 | 10 | 0 | 0 | 0 | 1156.0296
3556 | 2023-05-29 04:00 | 62.361 | 53.53 | 10 | 0 | 0 | 0 | 1158.91
3557 | 2023-05-29 05:00 | -11.4997 | 53.53 | 20 | 10 | 0 | 9.5 | 840.6058
3558 | 2023-05-29 06:00 | -6.7026 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 517.5657
3559 | 2023-05-29 07:00 | -9.627 | 53.53 | 20 | 10 | 0 | 20 | 878.0599
3560 | 2023-05-29 08:00 | 99.9047 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 82.4674
3561 | 2023-05-29 09:00 | 94.7632 | 65.03 | 10 | 0 | 0 | 10.5 | 1597.9321
3562 | 2023-05-29 10:00 | 86.0494 | 65.03 | 20 | 10 | 0 | 20 | 3021.5871
3563 | 2023-05-29 11:00 | 92.6562 | 65.03 | 10 | 0 | 0 | 20 | 1576.8617
3564 | 2023-05-29 12:00 | 106.7342 | 65.03 | 1 | 0 | 9 | 11 | 171.7642
3565 | 2023-05-29 13:00 | 110.2393 | 65.03 | 0 | 0 | 10 | 1 | 0
3566 | 2023-05-29 14:00 | 99.9012 | 65.03 | 10 | 0 | 0 | 1 | 1649.3119
3567 | 2023-05-29 15:00 | 86.3908 | 65.03 | 20 | 10 | 0 | 10.5 | 3028.4163
3568 | 2023-05-29 16:00 | 97.8624 | 65.03 | 20 | 10 | 0 | 20 | 3257.8486
3569 | 2023-05-29 17:00 | 116.1682 | 66.4 | 0 | 0 | 10 | 10 | 0
3570 | 2023-05-29 18:00 | 114.979 | 66.4 | 0 | 0 | 10 | 0 | 0
3571 | 2023-05-29 19:00 | 115.5364 | 65.03 | 10 | 0 | 0 | 0 | 1805.6641
3572 | 2023-05-29 20:00 | 91.7768 | 65.03 | 10 | 0 | 0 | 0 | 1568.0678
3573 | 2023-05-29 21:00 | 88.3611 | 65.03 | 10 | 0 | 0 | 0 | 1533.9107
3574 | 2023-05-29 22:00 | 84.7277 | 65.03 | 10 | 0 | 0 | 0 | 1497.5771
3575 | 2023-05-29 23:00 | 73.0452 | 53.53 | 20 | 10 | 0 | 9.5 | 2531.504
3576 | 2023-05-30 00:00 | 86.5799 | 53.53 | 0.5 | 0 | 9.5 | 0 | 70.055
3577 | 2023-05-30 01:00 | 85.3334 | 53.53 | 10 | 0 | 0 | 0 | 1388.6338
3578 | 2023-05-30 02:00 | -35.0956 | 53.53 | 20 | 10 | 0 | 9.5 | 368.6885
3579 | 2023-05-30 03:00 | 55.6352 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1206.5622
3580 | 2023-05-30 04:00 | -36.1814 | 53.53 | 20 | 10 | 0 | 20 | 346.9724
3581 | 2023-05-30 05:00 | 85.2028 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 69.3664
3582 | 2023-05-30 06:00 | 64.4937 | 53.53 | 20 | 10 | 0 | 20 | 2360.4732
3583 | 2023-05-30 07:00 | 83.4401 | 53.53 | 10 | 0 | 0 | 20 | 1369.7007
3584 | 2023-05-30 08:00 | 96.3266 | 65.03 | 10 | 0 | 0 | 20 | 1613.5664
3585 | 2023-05-30 09:00 | 114.8953 | 65.03 | 0 | 0 | 10 | 10 | 0
3586 | 2023-05-30 10:00 | 87.2878 | 65.03 | 20 | 10 | 0 | 19.5 | 3046.3567
3587 | 2023-05-30 11:00 | 95.4698 | 65.03 | 10 | 0 | 0 | 19.5 | 1604.9977
3588 | 2023-05-30 12:00 | 88.566 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1616.8003
3589 | 2023-05-30 13:00 | 90.1147 | 65.03 | 10 | 0 | 0 | 20 | 1551.447
3590 | 2023-05-30 14:00 | 93.5291 | 65.03 | 10 | 0 | 0 | 20 | 1585.5913
3591 | 2023-05-30 15:00 | 106.3508 | 65.03 | 10 | 0 | 0 | 20 | 1713.8078
3592 | 2023-05-30 16:00 | 111.8112 | 65.03 | 10 | 0 | 0 | 20 | 1768.4123
3593 | 2023-05-30 17:00 | 112.4958 | 66.4 | 0 | 0 | 10 | 10 | 0
3594 | 2023-05-30 18:00 | 106.2276 | 66.4 | 10 | 0 | 0 | 10 | 1726.2755
3595 | 2023-05-30 19:00 | 136.7081 | 65.03 | 0 | 0 | 10 | 0 | 0
3596 | 2023-05-30 20:00 | 85.8888 | 65.03 | 10 | 0 | 0 | 0 | 1509.1878
3597 | 2023-05-30 21:00 | 84.9617 | 65.03 | 10 | 0 | 0 | 0 | 1499.9167
3598 | 2023-05-30 22:00 | 78.5769 | 65.03 | 20 | 10 | 0 | 9.5 | 2872.1388
3599 | 2023-05-30 23:00 | 96.9028 | 53.53 | 10 | 0 | 0 | 9.5 | 1504.3276
3600 | 2023-05-31 00:00 | 92.3248 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1535.3139
3601 | 2023-05-31 01:00 | 110.5342 | 53.53 | 0 | 0 | 10 | 0 | 0
3602 | 2023-05-31 02:00 | 55.3762 | 53.53 | 20 | 10 | 0 | 9.5 | 2178.1237
3603 | 2023-05-31 03:00 | 77.6172 | 53.53 | 0.5 | 0 | 9.5 | 0 | 65.5736
3604 | 2023-05-31 04:00 | 64.4299 | 53.53 | 20 | 10 | 0 | 9.5 | 2359.1979
3605 | 2023-05-31 05:00 | 70.7377 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1373.4857
3606 | 2023-05-31 06:00 | 54.1477 | 53.53 | 20 | 10 | 0 | 20 | 2153.5549
3607 | 2023-05-31 07:00 | 97.7325 | 53.53 | 10 | 0 | 0 | 20 | 1512.6247
3608 | 2023-05-31 08:00 | 100.5512 | 65.03 | 0 | 0 | 10 | 10 | 0
3609 | 2023-05-31 09:00 | 93.6082 | 65.03 | 10 | 0 | 0 | 10 | 1586.3818
3610 | 2023-05-31 10:00 | 99.2366 | 65.03 | 0 | 0 | 10 | 0 | 0
3611 | 2023-05-31 11:00 | 88.7686 | 65.03 | 20 | 10 | 0 | 9.5 | 3075.9725
3612 | 2023-05-31 12:00 | 89.9093 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1712.4865
3613 | 2023-05-31 13:00 | 90.6533 | 65.03 | 10 | 0 | 0 | 10.5 | 1556.8328
3614 | 2023-05-31 14:00 | 83.2384 | 65.03 | 20 | 10 | 0 | 20 | 2965.3674
3615 | 2023-05-31 15:00 | 101.2739 | 65.03 | 10 | 0 | 0 | 20 | 1663.0385
3616 | 2023-05-31 16:00 | 104.6413 | 65.03 | 10 | 0 | 0 | 20 | 1696.7129
3617 | 2023-05-31 17:00 | 104.1547 | 66.4 | 10 | 0 | 0 | 20 | 1705.5474
3618 | 2023-05-31 18:00 | 111.6511 | 66.4 | 0 | 0 | 10 | 10 | 0
3619 | 2023-05-31 19:00 | 106.984 | 65.03 | 0 | 0 | 10 | 0 | 0
3620 | 2023-05-31 20:00 | 91.4857 | 65.03 | 10 | 0 | 0 | 0 | 1565.1567
3621 | 2023-05-31 21:00 | 84.608 | 65.03 | 10 | 0 | 0 | 0 | 1496.3802
3622 | 2023-05-31 22:00 | 83.0779 | 65.03 | 10 | 0 | 0 | 0 | 1481.0793
3623 | 2023-05-31 23:00 | 93.1761 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1544.2749
3624 | 2023-06-01 00:00 | 83.4238 | 53.53 | 20 | 10 | 0 | 10 | 2739.0767
3625 | 2023-06-01 01:00 | 104.7544 | 53.53 | 0 | 0 | 10 | 0 | 0
3626 | 2023-06-01 02:00 | 64.2481 | 53.53 | 20 | 10 | 0 | 9.5 | 2355.5611
3627 | 2023-06-01 03:00 | 57.8341 | 53.53 | 20 | 10 | 0 | 19 | 2227.2814
3628 | 2023-06-01 04:00 | 75.0223 | 53.53 | 10 | 0 | 0 | 19 | 1285.5233
3629 | 2023-06-01 05:00 | 69.1066 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1355.4569
3630 | 2023-06-01 06:00 | 69.9899 | 53.53 | 10 | 0 | 0 | 20 | 1235.1991
3631 | 2023-06-01 07:00 | 94.6306 | 53.53 | 10 | 0 | 0 | 20 | 1481.6064
3632 | 2023-06-01 08:00 | 89.4519 | 65.03 | 10 | 0 | 0 | 20 | 1544.8192
3633 | 2023-06-01 09:00 | 92.9619 | 65.03 | 10 | 0 | 0 | 20 | 1579.9189
3634 | 2023-06-01 10:00 | 92.6449 | 65.03 | 10 | 0 | 0 | 20 | 1576.7494
3635 | 2023-06-01 11:00 | 85.8718 | 65.03 | 10 | 0 | 0 | 20 | 1509.0178
3636 | 2023-06-01 12:00 | 91.9975 | 65.03 | 10 | 0 | 0 | 20 | 1570.2752
3637 | 2023-06-01 13:00 | 106.228 | 65.03 | 0 | 0 | 10 | 10 | 0
3638 | 2023-06-01 14:00 | 95.7432 | 65.03 | 1 | 0 | 9 | 1 | 160.7732
3639 | 2023-06-01 15:00 | 85.5924 | 65.03 | 20 | 10 | 0 | 10.5 | 3012.4488
3640 | 2023-06-01 16:00 | 84.5742 | 65.03 | 20 | 10 | 0 | 20 | 2992.084
3641 | 2023-06-01 17:00 | 125.093 | 66.4 | 0 | 0 | 10 | 10 | 0
3642 | 2023-06-01 18:00 | 108.23 | 66.4 | 0 | 0 | 10 | 0 | 0
3643 | 2023-06-01 19:00 | 104.4852 | 65.03 | 10 | 0 | 0 | 0 | 1695.1516
3644 | 2023-06-01 20:00 | 86.9256 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1599.5322
3645 | 2023-06-01 21:00 | 79.9479 | 65.03 | 20 | 10 | 0 | 10 | 2899.558
3646 | 2023-06-01 22:00 | 102.2119 | 65.03 | 0 | 0 | 10 | 0 | 0
3647 | 2023-06-01 23:00 | 81.1176 | 53.53 | 20 | 10 | 0 | 9.5 | 2692.9515
3648 | 2023-06-02 00:00 | 96.5771 | 53.53 | 0.5 | 0 | 9.5 | 0 | 75.0535
3649 | 2023-06-02 01:00 | 84.2887 | 53.53 | 10 | 0 | 0 | 0 | 1378.1871
3650 | 2023-06-02 02:00 | 77.2859 | 53.53 | 10 | 0 | 0 | 0 | 1308.1594
3651 | 2023-06-02 03:00 | 65.8996 | 53.53 | 20 | 10 | 0 | 9.5 | 2388.5917
3652 | 2023-06-02 04:00 | 71.1911 | 53.53 | 10 | 0 | 0 | 9.5 | 1247.2115
3653 | 2023-06-02 05:00 | 69.9174 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1364.4189
3654 | 2023-06-02 06:00 | 69.0386 | 53.53 | 20 | 10 | 0 | 20 | 2451.3721
3655 | 2023-06-02 07:00 | 86.6489 | 53.53 | 10 | 0 | 0 | 20 | 1401.7887
3656 | 2023-06-02 08:00 | 92.2115 | 65.03 | 10 | 0 | 0 | 20 | 1572.4153
3657 | 2023-06-02 09:00 | 113.3102 | 65.03 | 0 | 0 | 10 | 10 | 0
3658 | 2023-06-02 10:00 | 87.9431 | 65.03 | 20 | 10 | 0 | 19.5 | 3059.4624
3659 | 2023-06-02 11:00 | 93.9306 | 65.03 | 10 | 0 | 0 | 19.5 | 1589.6063
3660 | 2023-06-02 12:00 | 94.0102 | 65.03 | 10 | 0 | 0 | 19.5 | 1590.402
3661 | 2023-06-02 13:00 | 97.1064 | 65.03 | 1 | 0 | 9 | 10.5 | 162.1364
3662 | 2023-06-02 14:00 | 90.8761 | 65.03 | 10 | 0 | 0 | 10.5 | 1559.0613
3663 | 2023-06-02 15:00 | 96.3739 | 65.03 | 10 | 0 | 0 | 10.5 | 1614.0394
3664 | 2023-06-02 16:00 | 92.6635 | 65.03 | 10 | 0 | 0 | 10.5 | 1576.9352
3665 | 2023-06-02 17:00 | 99.4519 | 66.4 | 0 | 0 | 10 | 0.5 | 0
3666 | 2023-06-02 18:00 | -58.2255 | 66.4 | 20 | 10 | 0 | 10 | 163.4891
3667 | 2023-06-02 19:00 | 101.8684 | 65.03 | 0 | 0 | 10 | 0 | 0
3668 | 2023-06-02 20:00 | 78.7566 | 65.03 | 20 | 10 | 0 | 9.5 | 2875.7326
3669 | 2023-06-02 21:00 | 89.9462 | 65.03 | 10 | 0 | 0 | 9.5 | 1549.7622
3670 | 2023-06-02 22:00 | 92.8388 | 65.03 | 0.5 | 0 | 9.5 | 0 | 78.9344
3671 | 2023-06-02 23:00 | 88.1777 | 53.53 | 10 | 0 | 0 | 0 | 1417.0774
3672 | 2023-06-03 00:00 | 80.5354 | 53.53 | 10 | 0 | 0 | 0 | 1340.6541
3673 | 2023-06-03 01:00 | 64.8989 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1246.6199
3674 | 2023-06-03 02:00 | 47.5177 | 53.53 | 20 | 10 | 0 | 10 | 2020.9541
3675 | 2023-06-03 03:00 | 76.0909 | 53.53 | 0 | 0 | 10 | 0 | 0
3676 | 2023-06-03 04:00 | 49.1583 | 53.53 | 20 | 10 | 0 | 9.5 | 2053.7662
3677 | 2023-06-03 05:00 | 60.9262 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1265.0427
3678 | 2023-06-03 06:00 | 51.2425 | 53.53 | 20 | 10 | 0 | 20 | 2095.4496
3679 | 2023-06-03 07:00 | 76.5031 | 53.53 | 10 | 0 | 0 | 20 | 1300.3305
3680 | 2023-06-03 08:00 | 81.5728 | 53.53 | 10 | 0 | 0 | 20 | 1351.0278
3681 | 2023-06-03 09:00 | 90.4854 | 53.53 | 0 | 0 | 10 | 10 | 0
3682 | 2023-06-03 10:00 | 86.9454 | 53.53 | 10 | 0 | 0 | 10 | 1404.7545
3683 | 2023-06-03 11:00 | 82.7524 | 53.53 | 10 | 0 | 0 | 10 | 1362.8241
3684 | 2023-06-03 12:00 | 79.1421 | 53.53 | 20 | 10 | 0 | 19.5 | 2653.4417
3685 | 2023-06-03 13:00 | 87.9895 | 53.53 | 1 | 0 | 9 | 10.5 | 141.5195
3686 | 2023-06-03 14:00 | 78.2738 | 53.53 | 20 | 10 | 0 | 20 | 2636.0758
3687 | 2023-06-03 15:00 | 89.3191 | 53.53 | 10 | 0 | 0 | 20 | 1428.4907
3688 | 2023-06-03 16:00 | 115.8702 | 53.53 | 0 | 0 | 10 | 10 | 0
3689 | 2023-06-03 17:00 | 113.3828 | 53.53 | 0 | 0 | 10 | 0 | 0
3690 | 2023-06-03 18:00 | 106.9105 | 53.53 | 10 | 0 | 0 | 0 | 1604.4049
3691 | 2023-06-03 19:00 | 100.2644 | 53.53 | 10 | 0 | 0 | 0 | 1537.9443
3692 | 2023-06-03 20:00 | 69.873 | 53.53 | 20 | 10 | 0 | 9.5 | 2468.0605
3693 | 2023-06-03 21:00 | 72.7119 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1328.8625
3694 | 2023-06-03 22:00 | 92.6327 | 53.53 | 0 | 0 | 10 | 0 | 0
3695 | 2023-06-03 23:00 | 70.6245 | 53.53 | 10 | 0 | 0 | 0 | 1241.5453
3696 | 2023-06-04 00:00 | 71.1675 | 53.53 | 10 | 0 | 0 | 0 | 1246.9746
3697 | 2023-06-04 01:00 | 74.6863 | 53.53 | 10 | 0 | 0 | 0 | 1282.1629
3698 | 2023-06-04 02:00 | 49.0772 | 53.53 | 20 | 10 | 0 | 9.5 | 2052.1443
3699 | 2023-06-04 03:00 | 48.2007 | 53.53 | 20 | 10 | 0 | 19 | 2034.6141
3700 | 2023-06-04 04:00 | 55.5226 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 163.5789
3701 | 2023-06-04 05:00 | 50.0314 | 53.53 | 20 | 10 | 0 | 20 | 2071.227
3702 | 2023-06-04 06:00 | 50.9151 | 53.53 | 10 | 0 | 0 | 20 | 1044.4507
3703 | 2023-06-04 07:00 | 70.6753 | 53.53 | 10 | 0 | 0 | 20 | 1242.0528
3704 | 2023-06-04 08:00 | 90.1397 | 53.53 | 10 | 0 | 0 | 20 | 1436.6966
3705 | 2023-06-04 09:00 | 84.2166 | 53.53 | 10 | 0 | 0 | 20 | 1377.466
3706 | 2023-06-04 10:00 | 84.5943 | 53.53 | 10 | 0 | 0 | 20 | 1381.2426
3707 | 2023-06-04 11:00 | 90.8013 | 53.53 | 10 | 0 | 0 | 20 | 1443.3133
3708 | 2023-06-04 12:00 | 84.8554 | 53.53 | 10 | 0 | 0 | 20 | 1383.8539
3709 | 2023-06-04 13:00 | 83.8961 | 53.53 | 10 | 0 | 0 | 20 | 1374.2613
3710 | 2023-06-04 14:00 | 89.6878 | 53.53 | 10 | 0 | 0 | 20 | 1432.1781
3711 | 2023-06-04 15:00 | 91.4474 | 53.53 | 10 | 0 | 0 | 20 | 1449.774
3712 | 2023-06-04 16:00 | 84.8192 | 53.53 | 10 | 0 | 0 | 20 | 1383.4924
3713 | 2023-06-04 17:00 | 101.5102 | 53.53 | 0 | 0 | 10 | 10 | 0
3714 | 2023-06-04 18:00 | 95.6717 | 53.53 | 0 | 0 | 10 | 0 | 0
3715 | 2023-06-04 19:00 | 95.2092 | 53.53 | 10 | 0 | 0 | 0 | 1487.3923
3716 | 2023-06-04 20:00 | 87.3867 | 53.53 | 10 | 0 | 0 | 0 | 1409.1673
3717 | 2023-06-04 21:00 | 84.4683 | 53.53 | 10 | 0 | 0 | 0 | 1379.9834
3718 | 2023-06-04 22:00 | 84.5572 | 53.53 | 10 | 0 | 0 | 0 | 1380.8724
3719 | 2023-06-04 23:00 | 78.096 | 53.53 | 20 | 10 | 0 | 9.5 | 2632.52
3720 | 2023-06-05 00:00 | 84.2472 | 53.53 | 10 | 0 | 0 | 9.5 | 1377.7724
3721 | 2023-06-05 01:00 | 89.7071 | 53.53 | 0.5 | 0 | 9.5 | 0 | 71.6185
3722 | 2023-06-05 02:00 | 71.9942 | 53.53 | 10 | 0 | 0 | 0 | 1255.2417
3723 | 2023-06-05 03:00 | 71.7579 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1384.7612
3724 | 2023-06-05 04:00 | 63.1538 | 53.53 | 20 | 10 | 0 | 10.5 | 2333.6757
3725 | 2023-06-05 05:00 | 76.7992 | 53.53 | 10 | 0 | 0 | 10.5 | 1303.2916
3726 | 2023-06-05 06:00 | 65.6718 | 53.53 | 20 | 10 | 0 | 20 | 2384.0369
3727 | 2023-06-05 07:00 | 89.1209 | 53.53 | 10 | 0 | 0 | 20 | 1426.5087
3728 | 2023-06-05 08:00 | 96.1061 | 65.03 | 10 | 0 | 0 | 20 | 1611.3607
3729 | 2023-06-05 09:00 | 95.8212 | 65.03 | 10 | 0 | 0 | 20 | 1608.5122
3730 | 2023-06-05 10:00 | 88.9467 | 65.03 | 10 | 0 | 0 | 20 | 1539.7672
3731 | 2023-06-05 11:00 | 99.7528 | 65.03 | 0 | 0 | 10 | 10 | 0
3732 | 2023-06-05 12:00 | 127.5997 | 65.03 | 0 | 0 | 10 | 0 | 0
3733 | 2023-06-05 13:00 | 91.2396 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1727.1905
3734 | 2023-06-05 14:00 | 94.4365 | 65.03 | 10 | 0 | 0 | 1 | 1594.6648
3735 | 2023-06-05 15:00 | 90.7661 | 65.03 | 20 | 10 | 0 | 10.5 | 3115.9217
3736 | 2023-06-05 16:00 | 90.4935 | 65.03 | 20 | 10 | 0 | 20 | 3110.4696
3737 | 2023-06-05 17:00 | 123.6324 | 66.4 | 0 | 0 | 10 | 10 | 0
3738 | 2023-06-05 18:00 | 104.3279 | 66.4 | 0 | 0 | 10 | 0 | 0
3739 | 2023-06-05 19:00 | 105.584 | 65.03 | 10 | 0 | 0 | 0 | 1706.1398
3740 | 2023-06-05 20:00 | 79.426 | 65.03 | 10 | 0 | 0 | 0 | 1444.5604
3741 | 2023-06-05 21:00 | 83.8157 | 65.03 | 10 | 0 | 0 | 0 | 1488.4568
3742 | 2023-06-05 22:00 | 78.8729 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1514.7675
3743 | 2023-06-05 23:00 | 89.1157 | 53.53 | 20 | 10 | 0 | 10 | 2852.9137
3744 | 2023-06-06 00:00 | 116.8022 | 53.53 | 0 | 0 | 10 | 0 | 0
3745 | 2023-06-06 01:00 | 81.2941 | 53.53 | 10 | 0 | 0 | 0 | 1348.2408
3746 | 2023-06-06 02:00 | 54.0612 | 53.53 | 20 | 10 | 0 | 9.5 | 2151.8231
3747 | 2023-06-06 03:00 | 71.6474 | 53.53 | 10 | 0 | 0 | 9.5 | 1251.7741
3748 | 2023-06-06 04:00 | 58.9999 | 53.53 | 20 | 10 | 0 | 19 | 2250.5977
3749 | 2023-06-06 05:00 | 75.8156 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 194.0184
3750 | 2023-06-06 06:00 | 61.8701 | 53.53 | 20 | 10 | 0 | 20 | 2308.002
3751 | 2023-06-06 07:00 | 79.5817 | 53.53 | 10 | 0 | 0 | 20 | 1331.117
3752 | 2023-06-06 08:00 | 92.5986 | 65.03 | 10 | 0 | 0 | 20 | 1576.2863
3753 | 2023-06-06 09:00 | 100.2795 | 65.03 | 0 | 0 | 10 | 10 | 0
3754 | 2023-06-06 10:00 | 92.2495 | 65.03 | 10 | 0 | 0 | 10 | 1572.7954
3755 | 2023-06-06 11:00 | 90.4372 | 65.03 | 10 | 0 | 0 | 10 | 1554.6716
3756 | 2023-06-06 12:00 | 92.4507 | 65.03 | 10 | 0 | 0 | 10 | 1574.8067
3757 | 2023-06-06 13:00 | 85.9683 | 65.03 | 20 | 10 | 0 | 19.5 | 3019.965
3758 | 2023-06-06 14:00 | 97.0606 | 65.03 | 1 | 0 | 9 | 10.5 | 162.0906
3759 | 2023-06-06 15:00 | 83.5251 | 65.03 | 20 | 10 | 0 | 20 | 2971.1028
3760 | 2023-06-06 16:00 | 90.7798 | 65.03 | 10 | 0 | 0 | 20 | 1558.0976
3761 | 2023-06-06 17:00 | 115.2946 | 66.4 | 0 | 0 | 10 | 10 | 0
3762 | 2023-06-06 18:00 | 111.2777 | 66.4 | 10 | 0 | 0 | 10 | 1776.7769
3763 | 2023-06-06 19:00 | 113.742 | 65.03 | 0 | 0 | 10 | 0 | 0
3764 | 2023-06-06 20:00 | 88.4152 | 65.03 | 20 | 10 | 0 | 9.5 | 3068.9038
3765 | 2023-06-06 21:00 | 99.4078 | 65.03 | 0.5 | 0 | 9.5 | 0 | 82.2189
3766 | 2023-06-06 22:00 | 96.891 | 65.03 | 10 | 0 | 0 | 0 | 1619.2098
3767 | 2023-06-06 23:00 | 87.4786 | 53.53 | 10 | 0 | 0 | 0 | 1410.0862
3768 | 2023-06-07 00:00 | 91.9192 | 53.53 | 10 | 0 | 0 | 0 | 1454.4917
3769 | 2023-06-07 01:00 | 90.2104 | 53.53 | 10 | 0 | 0 | 0 | 1437.4035
3770 | 2023-06-07 02:00 | 60.8104 | 53.53 | 20 | 10 | 0 | 9.5 | 2286.8071
3771 | 2023-06-07 03:00 | 55.6033 | 53.53 | 20 | 10 | 0 | 19 | 2182.6655
3772 | 2023-06-07 04:00 | 67.2584 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1335.0301
3773 | 2023-06-07 05:00 | 68.3486 | 53.53 | 10 | 0 | 0 | 20 | 1218.7856
3774 | 2023-06-07 06:00 | 73.5733 | 53.53 | 10 | 0 | 0 | 20 | 1271.0325
3775 | 2023-06-07 07:00 | 77.776 | 53.53 | 10 | 0 | 0 | 20 | 1313.0597
3776 | 2023-06-07 08:00 | 87.946 | 65.03 | 10 | 0 | 0 | 20 | 1529.7601
3777 | 2023-06-07 09:00 | 97.5968 | 65.03 | 0 | 0 | 10 | 10 | 0
3778 | 2023-06-07 10:00 | 93.3702 | 65.03 | 10 | 0 | 0 | 10 | 1584.0021
3779 | 2023-06-07 11:00 | 83.097 | 65.03 | 20 | 10 | 0 | 19.5 | 2962.5392
3780 | 2023-06-07 12:00 | 96.876 | 65.03 | 0 | 0 | 10 | 9.5 | 0
3781 | 2023-06-07 13:00 | 83.2397 | 65.03 | 20 | 10 | 0 | 19 | 2965.3937
3782 | 2023-06-07 14:00 | 87.7254 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1688.3495
3783 | 2023-06-07 15:00 | 106.3998 | 65.03 | 10 | 0 | 0 | 20 | 1714.2978
3784 | 2023-06-07 16:00 | 112.1199 | 65.03 | 0 | 0 | 10 | 10 | 0
3785 | 2023-06-07 17:00 | 101.2585 | 66.4 | 10 | 0 | 0 | 10 | 1676.5848
3786 | 2023-06-07 18:00 | 106.546 | 66.4 | 10 | 0 | 0 | 10 | 1729.4601
3787 | 2023-06-07 19:00 | 109.22 | 65.03 | 0 | 0 | 10 | 0 | 0
3788 | 2023-06-07 20:00 | 106.5575 | 65.03 | 10 | 0 | 0 | 0 | 1715.8755
3789 | 2023-06-07 21:00 | 85.4621 | 65.03 | 10 | 0 | 0 | 0 | 1504.9209
3790 | 2023-06-07 22:00 | 85.5657 | 65.03 | 10 | 0 | 0 | 0 | 1505.9574
3791 | 2023-06-07 23:00 | 98.6834 | 53.53 | 10 | 0 | 0 | 0 | 1522.1345
3792 | 2023-06-08 00:00 | 81.2397 | 53.53 | 20 | 10 | 0 | 9.5 | 2695.3931
3793 | 2023-06-08 01:00 | 89.9464 | 53.53 | 0.5 | 0 | 9.5 | 0 | 71.7382
3794 | 2023-06-08 02:00 | 54.9487 | 53.53 | 20 | 10 | 0 | 9.5 | 2169.5739
3795 | 2023-06-08 03:00 | 62.6465 | 53.53 | 10 | 0 | 0 | 9.5 | 1161.7649
3796 | 2023-06-08 04:00 | 54.0938 | 53.53 | 20 | 10 | 0 | 19 | 2152.4753
3797 | 2023-06-08 05:00 | 57.1133 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1222.8998
3798 | 2023-06-08 06:00 | 71.0555 | 53.53 | 10 | 0 | 0 | 20 | 1245.855
3799 | 2023-06-08 07:00 | 83.5268 | 53.53 | 10 | 0 | 0 | 20 | 1370.568
3800 | 2023-06-08 08:00 | 91.616 | 65.03 | 10 | 0 | 0 | 20 | 1566.46
3801 | 2023-06-08 09:00 | 88.8687 | 65.03 | 10 | 0 | 0 | 20 | 1538.987
3802 | 2023-06-08 10:00 | 92.297 | 65.03 | 10 | 0 | 0 | 20 | 1573.2697
3803 | 2023-06-08 11:00 | 96.2618 | 65.03 | 10 | 0 | 0 | 20 | 1612.918
3804 | 2023-06-08 12:00 | 102.4723 | 65.03 | 0 | 0 | 10 | 10 | 0
3805 | 2023-06-08 13:00 | 80.2723 | 65.03 | 20 | 10 | 0 | 19.5 | 2906.0465
3806 | 2023-06-08 14:00 | 88.3775 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1614.8159
3807 | 2023-06-08 15:00 | 95.1205 | 65.03 | 10 | 0 | 0 | 20 | 1601.5046
3808 | 2023-06-08 16:00 | 93.1677 | 65.03 | 10 | 0 | 0 | 20 | 1581.9772
3809 | 2023-06-08 17:00 | 112.1143 | 66.4 | 0 | 0 | 10 | 10 | 0
3810 | 2023-06-08 18:00 | 110.9876 | 66.4 | 0 | 0 | 10 | 0 | 0
3811 | 2023-06-08 19:00 | 106.7132 | 65.03 | 10 | 0 | 0 | 0 | 1717.4324
3812 | 2023-06-08 20:00 | 85.2434 | 65.03 | 20 | 10 | 0 | 9.5 | 3005.4671
3813 | 2023-06-08 21:00 | 87.1232 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1601.6128
3814 | 2023-06-08 22:00 | 99.1847 | 65.03 | 0 | 0 | 10 | 0 | 0
3815 | 2023-06-08 23:00 | 78.9693 | 53.53 | 10 | 0 | 0 | 0 | 1324.9926
3816 | 2023-06-09 00:00 | 83.4317 | 53.53 | 10 | 0 | 0 | 0 | 1369.6167
3817 | 2023-06-09 01:00 | 85.3119 | 53.53 | 10 | 0 | 0 | 0 | 1388.4189
3818 | 2023-06-09 02:00 | 78.8224 | 53.53 | 10 | 0 | 0 | 0 | 1323.5244
3819 | 2023-06-09 03:00 | 61.7445 | 53.53 | 20 | 10 | 0 | 9.5 | 2305.4895
3820 | 2023-06-09 04:00 | 72.2303 | 53.53 | 10 | 0 | 0 | 9.5 | 1257.603
3821 | 2023-06-09 05:00 | 75.077 | 53.53 | 1.5 | 0 | 8.5 | 1 | 192.9105
3822 | 2023-06-09 06:00 | 63.4247 | 53.53 | 20 | 10 | 0 | 10.5 | 2339.0939
3823 | 2023-06-09 07:00 | -65.4092 | 53.53 | 20 | 10 | 0 | 20 | -237.583
3824 | 2023-06-09 08:00 | 91.5483 | 65.03 | 10 | 0 | 0 | 20 | 1565.783
3825 | 2023-06-09 09:00 | 92.0514 | 65.03 | 10 | 0 | 0 | 20 | 1570.8141
3826 | 2023-06-09 10:00 | 101.2009 | 65.03 | 0 | 0 | 10 | 10 | 0
3827 | 2023-06-09 11:00 | 95.6923 | 65.03 | 10 | 0 | 0 | 10 | 1607.2233
3828 | 2023-06-09 12:00 | 95.7268 | 65.03 | 1 | 0 | 9 | 1 | 160.7568
3829 | 2023-06-09 13:00 | 86.7359 | 65.03 | 20 | 10 | 0 | 10.5 | 3035.3182
3830 | 2023-06-09 14:00 | 87.6003 | 65.03 | 20 | 10 | 0 | 20 | 3052.6055
3831 | 2023-06-09 15:00 | 116.4544 | 65.03 | 0 | 0 | 10 | 10 | 0
3832 | 2023-06-09 16:00 | 92.5996 | 65.03 | 20 | 10 | 0 | 19.5 | 3152.5913
3833 | 2023-06-09 17:00 | 103.7134 | 66.4 | 10 | 0 | 0 | 19.5 | 1701.1341
3834 | 2023-06-09 18:00 | 122.304 | 66.4 | 0 | 0 | 10 | 9.5 | 0
3835 | 2023-06-09 19:00 | 111.1038 | 65.03 | 0.5 | 0 | 9.5 | 0 | 88.0669
3836 | 2023-06-09 20:00 | 93.6332 | 65.03 | 10 | 0 | 0 | 0 | 1586.6323
3837 | 2023-06-09 21:00 | 87.8841 | 65.03 | 10 | 0 | 0 | 0 | 1529.141
3838 | 2023-06-09 22:00 | 86.6189 | 65.03 | 10 | 0 | 0 | 0 | 1516.4895
3839 | 2023-06-09 23:00 | 82.6582 | 53.53 | 10 | 0 | 0 | 0 | 1361.8822
3840 | 2023-06-10 00:00 | 67.4098 | 53.53 | 20 | 10 | 0 | 9.5 | 2418.7952
3841 | 2023-06-10 01:00 | 75.2475 | 53.53 | 0.5 | 0 | 9.5 | 0 | 64.3887
3842 | 2023-06-10 02:00 | -28.6289 | 53.53 | 20 | 10 | 0 | 9.5 | 498.0213
3843 | 2023-06-10 03:00 | -28.5484 | 53.53 | 20 | 10 | 0 | 19 | 499.6319
3844 | 2023-06-10 04:00 | 56.5517 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 165.1225
3845 | 2023-06-10 05:00 | 43.3098 | 53.53 | 20 | 10 | 0 | 20 | 1936.7959
3846 | 2023-06-10 06:00 | 55.2033 | 53.53 | 10 | 0 | 0 | 20 | 1087.3326
3847 | 2023-06-10 07:00 | 107.766 | 53.53 | 0 | 0 | 10 | 10 | 0
3848 | 2023-06-10 08:00 | 93.3186 | 53.53 | 0 | 0 | 10 | 0 | 0
3849 | 2023-06-10 09:00 | 80.4999 | 53.53 | 20 | 10 | 0 | 9.5 | 2680.5973
3850 | 2023-06-10 10:00 | 90.749 | 53.53 | 0.5 | 0 | 9.5 | 0 | 72.1395
3851 | 2023-06-10 11:00 | 80.9091 | 53.53 | 10 | 0 | 0 | 0 | 1344.391
3852 | 2023-06-10 12:00 | 77.5537 | 53.53 | 20 | 10 | 0 | 9.5 | 2621.6738
3853 | 2023-06-10 13:00 | 83.4174 | 53.53 | 10 | 0 | 0 | 9.5 | 1369.4743
3854 | 2023-06-10 14:00 | 86.5943 | 53.53 | 1.5 | 0 | 8.5 | 1 | 210.1864
3855 | 2023-06-10 15:00 | 75.155 | 53.53 | 20 | 10 | 0 | 10.5 | 2573.7007
3856 | 2023-06-10 16:00 | 78.6083 | 53.53 | 20 | 10 | 0 | 20 | 2642.7656
3857 | 2023-06-10 17:00 | 100.9759 | 53.53 | 0 | 0 | 10 | 10 | 0
3858 | 2023-06-10 18:00 | 98.017 | 53.53 | 10 | 0 | 0 | 10 | 1515.4702
3859 | 2023-06-10 19:00 | 104.0419 | 53.53 | 0 | 0 | 10 | 0 | 0
3860 | 2023-06-10 20:00 | 73.2636 | 53.53 | 20 | 10 | 0 | 9.5 | 2535.8726
3861 | 2023-06-10 21:00 | 86.8711 | 53.53 | 1 | 0 | 9 | 0.5 | 140.4011
3862 | 2023-06-10 22:00 | 73.4254 | 53.53 | 20 | 10 | 0 | 10 | 2539.1081
3863 | 2023-06-10 23:00 | 91.8215 | 53.53 | 0 | 0 | 10 | 0 | 0
3864 | 2023-06-11 00:00 | 65.8399 | 53.53 | 10 | 0 | 0 | 0 | 1193.6989
3865 | 2023-06-11 01:00 | 68.9116 | 53.53 | 10 | 0 | 0 | 0 | 1224.4159
3866 | 2023-06-11 02:00 | 59.233 | 53.53 | 20 | 10 | 0 | 9.5 | 2255.26
3867 | 2023-06-11 03:00 | 72.0863 | 53.53 | 0.5 | 0 | 9.5 | 0 | 62.8081
3868 | 2023-06-11 04:00 | 58.3764 | 53.53 | 20 | 10 | 0 | 9.5 | 2238.1278
3869 | 2023-06-11 05:00 | 60.4971 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1260.2994
3870 | 2023-06-11 06:00 | 56.0302 | 53.53 | 20 | 10 | 0 | 20 | 2191.2036
3871 | 2023-06-11 07:00 | 69.2727 | 53.53 | 10 | 0 | 0 | 20 | 1228.0267
3872 | 2023-06-11 08:00 | 82.4798 | 53.53 | 10 | 0 | 0 | 20 | 1360.0976
3873 | 2023-06-11 09:00 | 78.278 | 53.53 | 10 | 0 | 0 | 20 | 1318.0801
3874 | 2023-06-11 10:00 | 77.9332 | 53.53 | 10 | 0 | 0 | 20 | 1314.6318
3875 | 2023-06-11 11:00 | 89.1005 | 53.53 | 0 | 0 | 10 | 10 | 0
3876 | 2023-06-11 12:00 | 78.7469 | 53.53 | 20 | 10 | 0 | 19.5 | 2645.5372
3877 | 2023-06-11 13:00 | 88.4136 | 53.53 | 1 | 0 | 9 | 10.5 | 141.9436
3878 | 2023-06-11 14:00 | 77.8155 | 53.53 | 20 | 10 | 0 | 20 | 2626.9095
3879 | 2023-06-11 15:00 | 88.223 | 53.53 | 10 | 0 | 0 | 20 | 1417.53
3880 | 2023-06-11 16:00 | 82.4892 | 53.53 | 10 | 0 | 0 | 20 | 1360.1919
3881 | 2023-06-11 17:00 | 114.0229 | 53.53 | 0 | 0 | 10 | 10 | 0
3882 | 2023-06-11 18:00 | 103.448 | 53.53 | 10 | 0 | 0 | 10 | 1569.78
3883 | 2023-06-11 19:00 | 112.1183 | 53.53 | 0 | 0 | 10 | 0 | 0
3884 | 2023-06-11 20:00 | 75.8274 | 53.53 | 10 | 0 | 0 | 0 | 1293.5742
3885 | 2023-06-11 21:00 | 81.3229 | 53.53 | 10 | 0 | 0 | 0 | 1348.5295
3886 | 2023-06-11 22:00 | 74.5241 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1347.9383
3887 | 2023-06-11 23:00 | 72.981 | 53.53 | 20 | 10 | 0 | 10 | 2530.22
3888 | 2023-06-12 00:00 | 82.0078 | 53.53 | 0 | 0 | 10 | 0 | 0
3889 | 2023-06-12 01:00 | 79.0063 | 53.53 | 10 | 0 | 0 | 0 | 1325.3632
3890 | 2023-06-12 02:00 | 56.2593 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1213.4605
3891 | 2023-06-12 03:00 | 55.258 | 53.53 | 20 | 10 | 0 | 10.5 | 2175.76
3892 | 2023-06-12 04:00 | 51.2891 | 53.53 | 20 | 10 | 0 | 20 | 2096.3814
3893 | 2023-06-12 05:00 | 57.1083 | 53.53 | 10 | 0 | 0 | 20 | 1106.3832
3894 | 2023-06-12 06:00 | 69.0766 | 53.53 | 10 | 0 | 0 | 20 | 1226.0663
3895 | 2023-06-12 07:00 | 74.3749 | 53.53 | 10 | 0 | 0 | 20 | 1279.0486
3896 | 2023-06-12 08:00 | 85.4823 | 65.03 | 10 | 0 | 0 | 20 | 1505.1232
3897 | 2023-06-12 09:00 | 111.6815 | 65.03 | 0 | 0 | 10 | 10 | 0
3898 | 2023-06-12 10:00 | 89.5527 | 65.03 | 20 | 10 | 0 | 19.5 | 3091.6536
3899 | 2023-06-12 11:00 | 96.4259 | 65.03 | 10 | 0 | 0 | 19.5 | 1614.5592
3900 | 2023-06-12 12:00 | 99.2111 | 65.03 | 1.5 | 0 | 8.5 | 11 | 246.3617
3901 | 2023-06-12 13:00 | 99.3955 | 65.03 | 0 | 0 | 10 | 1 | 0
3902 | 2023-06-12 14:00 | 84.7327 | 65.03 | 20 | 10 | 0 | 10.5 | 2995.2531
3903 | 2023-06-12 15:00 | 92.2241 | 65.03 | 10 | 0 | 0 | 10.5 | 1572.5406
3904 | 2023-06-12 16:00 | 84.2835 | 65.03 | 20 | 10 | 0 | 20 | 2986.2706
3905 | 2023-06-12 17:00 | 135.9778 | 66.4 | 0 | 0 | 10 | 10 | 0
3906 | 2023-06-12 18:00 | 99.3917 | 66.4 | 10 | 0 | 0 | 10 | 1657.9169
3907 | 2023-06-12 19:00 | 102.1549 | 65.03 | 0 | 0 | 10 | 0 | 0
3908 | 2023-06-12 20:00 | 82.1945 | 65.03 | 20 | 10 | 0 | 9.5 | 2944.4909
3909 | 2023-06-12 21:00 | 79.855 | 65.03 | 20 | 10 | 0 | 19 | 2897.6998
3910 | 2023-06-12 22:00 | 101.41 | 65.03 | 0 | 0 | 10 | 9 | 0
3911 | 2023-06-12 23:00 | 110.6062 | 53.53 | 1 | 0 | 9 | 0 | 164.1362
3912 | 2023-06-13 00:00 | 80.5731 | 53.53 | 10 | 0 | 0 | 0 | 1341.0312
3913 | 2023-06-13 01:00 | 75.7213 | 53.53 | 10 | 0 | 0 | 0 | 1292.5134
3914 | 2023-06-13 02:00 | 51.6772 | 53.53 | 20 | 10 | 0 | 9.5 | 2104.1448
3915 | 2023-06-13 03:00 | 62.1329 | 53.53 | 10 | 0 | 0 | 9.5 | 1156.6292
3916 | 2023-06-13 04:00 | 61.6347 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1272.8728
3917 | 2023-06-13 05:00 | 59.4612 | 53.53 | 20 | 10 | 0 | 20 | 2259.8235
3918 | 2023-06-13 06:00 | 65.615 | 53.53 | 10 | 0 | 0 | 20 | 1191.4499
3919 | 2023-06-13 07:00 | 87.0449 | 53.53 | 10 | 0 | 0 | 20 | 1405.7494
3920 | 2023-06-13 08:00 | 96.4427 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 80.7364
3921 | 2023-06-13 09:00 | 91.6363 | 65.03 | 10 | 0 | 0 | 10.5 | 1566.6632
3922 | 2023-06-13 10:00 | 86.8627 | 65.03 | 20 | 10 | 0 | 20 | 3037.8531
3923 | 2023-06-13 11:00 | 99.4257 | 65.03 | 10 | 0 | 0 | 20 | 1644.5574
3924 | 2023-06-13 12:00 | 93.9923 | 65.03 | 10 | 0 | 0 | 20 | 1590.2234
3925 | 2023-06-13 13:00 | 101.5332 | 65.03 | 0 | 0 | 10 | 10 | 0
3926 | 2023-06-13 14:00 | 100.5851 | 65.03 | 1 | 0 | 9 | 1 | 165.6151
3927 | 2023-06-13 15:00 | 85.2176 | 65.03 | 20 | 10 | 0 | 10.5 | 3004.9517
3928 | 2023-06-13 16:00 | 85.1567 | 65.03 | 20 | 10 | 0 | 20 | 3003.7339
3929 | 2023-06-13 17:00 | 103.8281 | 66.4 | 0 | 0 | 10 | 10 | 0
3930 | 2023-06-13 18:00 | 102.1088 | 66.4 | 10 | 0 | 0 | 10 | 1685.0877
3931 | 2023-06-13 19:00 | 115.2557 | 65.03 | 0 | 0 | 10 | 0 | 0
3932 | 2023-06-13 20:00 | 91.677 | 65.03 | 10 | 0 | 0 | 0 | 1567.0698
3933 | 2023-06-13 21:00 | 98.664 | 65.03 | 10 | 0 | 0 | 0 | 1636.94
3934 | 2023-06-13 22:00 | 92.056 | 65.03 | 10 | 0 | 0 | 0 | 1570.8603
3935 | 2023-06-13 23:00 | 85.5132 | 53.53 | 20 | 10 | 0 | 9.5 | 2780.8638
3936 | 2023-06-14 00:00 | 94.7286 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.1293
3937 | 2023-06-14 01:00 | 87.6816 | 53.53 | 10 | 0 | 0 | 0 | 1412.1157
3938 | 2023-06-14 02:00 | 64.4143 | 53.53 | 10 | 0 | 0 | 0 | 1179.4432
3939 | 2023-06-14 03:00 | -22.156 | 53.53 | 20 | 10 | 0 | 9.5 | 627.4809
3940 | 2023-06-14 04:00 | 64.7773 | 53.53 | 10 | 0 | 0 | 9.5 | 1183.0726
3941 | 2023-06-14 05:00 | 61.7169 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1273.781
3942 | 2023-06-14 06:00 | 58.3421 | 53.53 | 20 | 10 | 0 | 20 | 2237.4424
3943 | 2023-06-14 07:00 | 89.7683 | 53.53 | 10 | 0 | 0 | 20 | 1432.9826
3944 | 2023-06-14 08:00 | 105.1321 | 65.03 | 0 | 0 | 10 | 10 | 0
3945 | 2023-06-14 09:00 | 93.5218 | 65.03 | 10 | 0 | 0 | 10 | 1585.5176
3946 | 2023-06-14 10:00 | 105.9106 | 65.03 | 0 | 0 | 10 | 0 | 0
3947 | 2023-06-14 11:00 | 82.7426 | 65.03 | 20 | 10 | 0 | 9.5 | 2955.4515
3948 | 2023-06-14 12:00 | 93.4858 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1752.0172
3949 | 2023-06-14 13:00 | 93.5994 | 65.03 | 10 | 0 | 0 | 10.5 | 1586.294
3950 | 2023-06-14 14:00 | 88.9995 | 65.03 | 20 | 10 | 0 | 20 | 3080.5893
3951 | 2023-06-14 15:00 | 120.0111 | 65.03 | 0 | 0 | 10 | 10 | 0
3952 | 2023-06-14 16:00 | 93.4068 | 65.03 | 20 | 10 | 0 | 19.5 | 3168.7352
3953 | 2023-06-14 17:00 | 106.02 | 66.4 | 0.5 | 0 | 9.5 | 10 | 86.21
3954 | 2023-06-14 18:00 | 109.0938 | 66.4 | 0 | 0 | 10 | 0 | 0
3955 | 2023-06-14 19:00 | 97.607 | 65.03 | 10 | 0 | 0 | 0 | 1626.3702
3956 | 2023-06-14 20:00 | 83.8022 | 65.03 | 20 | 10 | 0 | 9.5 | 2976.644
3957 | 2023-06-14 21:00 | 97.4755 | 65.03 | 0.5 | 0 | 9.5 | 0 | 81.2528
3958 | 2023-06-14 22:00 | 84.5995 | 65.03 | 10 | 0 | 0 | 0 | 1496.2952
3959 | 2023-06-14 23:00 | 78.3944 | 53.53 | 20 | 10 | 0 | 9.5 | 2638.4877
3960 | 2023-06-15 00:00 | 95.9285 | 53.53 | 10 | 0 | 0 | 9.5 | 1494.585
3961 | 2023-06-15 01:00 | 96.2714 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.9007
3962 | 2023-06-15 02:00 | 68.0926 | 53.53 | 10 | 0 | 0 | 0 | 1216.2259
3963 | 2023-06-15 03:00 | 60.7077 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1262.6272
3964 | 2023-06-15 04:00 | 62.1653 | 53.53 | 10 | 0 | 0 | 1 | 1156.9527
3965 | 2023-06-15 05:00 | 58.5395 | 53.53 | 20 | 10 | 0 | 10.5 | 2241.3907
3966 | 2023-06-15 06:00 | 57.4478 | 53.53 | 20 | 10 | 0 | 20 | 2219.5565
3967 | 2023-06-15 07:00 | 77.1736 | 53.53 | 10 | 0 | 0 | 20 | 1307.0361
3968 | 2023-06-15 08:00 | 89.6673 | 65.03 | 10 | 0 | 0 | 20 | 1546.9726
3969 | 2023-06-15 09:00 | 87.2268 | 65.03 | 10 | 0 | 0 | 20 | 1522.5685
3970 | 2023-06-15 10:00 | 84.5373 | 65.03 | 10 | 0 | 0 | 20 | 1495.6725
3971 | 2023-06-15 11:00 | 95.5992 | 65.03 | 10 | 0 | 0 | 20 | 1606.2919
3972 | 2023-06-15 12:00 | 95.7212 | 65.03 | 10 | 0 | 0 | 20 | 1607.5117
3973 | 2023-06-15 13:00 | 110.5405 | 65.03 | 0 | 0 | 10 | 10 | 0
3974 | 2023-06-15 14:00 | 89.3563 | 65.03 | 20 | 10 | 0 | 19.5 | 3087.7262
3975 | 2023-06-15 15:00 | 96.2207 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1697.3756
3976 | 2023-06-15 16:00 | 96.3572 | 65.03 | 10 | 0 | 0 | 20 | 1613.8719
3977 | 2023-06-15 17:00 | 107.0652 | 66.4 | 10 | 0 | 0 | 20 | 1734.6521
3978 | 2023-06-15 18:00 | 115.1532 | 66.4 | 0 | 0 | 10 | 10 | 0
3979 | 2023-06-15 19:00 | 115.4442 | 65.03 | 0 | 0 | 10 | 0 | 0
3980 | 2023-06-15 20:00 | 91.4785 | 65.03 | 10 | 0 | 0 | 0 | 1565.0853
3981 | 2023-06-15 21:00 | 87.0527 | 65.03 | 10 | 0 | 0 | 0 | 1520.8268
3982 | 2023-06-15 22:00 | 86.3556 | 65.03 | 10 | 0 | 0 | 0 | 1513.8563
3983 | 2023-06-15 23:00 | 75.4842 | 53.53 | 10 | 0 | 0 | 0 | 1290.1415
3984 | 2023-06-16 00:00 | 78.5291 | 53.53 | 10 | 0 | 0 | 0 | 1320.5912
3985 | 2023-06-16 01:00 | 79.6426 | 53.53 | 10 | 0 | 0 | 0 | 1331.7265
3986 | 2023-06-16 02:00 | 56.7426 | 53.53 | 20 | 10 | 0 | 9.5 | 2205.4522
3987 | 2023-06-16 03:00 | 67.4254 | 53.53 | 11.5789 | 1.5789 | 0 | 11 | 1400.5358
3988 | 2023-06-16 04:00 | 74.6953 | 53.53 | 0 | 0 | 10 | 1 | 0
3989 | 2023-06-16 05:00 | 57.9367 | 53.53 | 20 | 10 | 0 | 10.5 | 2229.3338
3990 | 2023-06-16 06:00 | 66.1171 | 53.53 | 20 | 10 | 0 | 20 | 2392.9423
3991 | 2023-06-16 07:00 | 77.2302 | 53.53 | 10 | 0 | 0 | 20 | 1307.602
3992 | 2023-06-16 08:00 | 91.7129 | 65.03 | 10 | 0 | 0 | 20 | 1567.4287
3993 | 2023-06-16 09:00 | 89.2218 | 65.03 | 10 | 0 | 0 | 20 | 1542.5179
3994 | 2023-06-16 10:00 | 98.8458 | 65.03 | 0 | 0 | 10 | 10 | 0
3995 | 2023-06-16 11:00 | 89.2923 | 65.03 | 20 | 10 | 0 | 19.5 | 3086.4456
3996 | 2023-06-16 12:00 | 102.763 | 65.03 | 0 | 0 | 10 | 9.5 | 0
3997 | 2023-06-16 13:00 | 92.1217 | 65.03 | 10 | 0 | 0 | 9.5 | 1571.5169
3998 | 2023-06-16 14:00 | 89.4716 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1707.6495
3999 | 2023-06-16 15:00 | 86.0635 | 65.03 | 20 | 10 | 0 | 20 | 3021.8702
4000 | 2023-06-16 16:00 | 95.8713 | 65.03 | 10 | 0 | 0 | 20 | 1609.0133
4001 | 2023-06-16 17:00 | 116.6005 | 66.4 | 0 | 0 | 10 | 10 | 0
4002 | 2023-06-16 18:00 | 111.0346 | 66.4 | 10 | 0 | 0 | 10 | 1774.346
4003 | 2023-06-16 19:00 | 132.8349 | 65.03 | 0 | 0 | 10 | 0 | 0
4004 | 2023-06-16 20:00 | 102.2889 | 65.03 | 10 | 0 | 0 | 0 | 1673.1888
4005 | 2023-06-16 21:00 | 86.695 | 65.03 | 10 | 0 | 0 | 0 | 1517.2504
4006 | 2023-06-16 22:00 | 86.6234 | 65.03 | 10 | 0 | 0 | 0 | 1516.5335
4007 | 2023-06-16 23:00 | 87.6813 | 53.53 | 10 | 0 | 0 | 0 | 1412.113
4008 | 2023-06-17 00:00 | 70.341 | 53.53 | 20 | 10 | 0 | 9.5 | 2477.4195
4009 | 2023-06-17 01:00 | 86.371 | 53.53 | 0.5 | 0 | 9.5 | 0 | 69.9505
4010 | 2023-06-17 02:00 | 58.7629 | 53.53 | 20 | 10 | 0 | 9.5 | 2245.8575
4011 | 2023-06-17 03:00 | 57.8977 | 53.53 | 20 | 10 | 0 | 19 | 2228.5535
4012 | 2023-06-17 04:00 | 61.6198 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1272.7081
4013 | 2023-06-17 05:00 | 72.8167 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 63.1734
4014 | 2023-06-17 06:00 | 57.2139 | 53.53 | 20 | 10 | 0 | 20 | 2214.8784
4015 | 2023-06-17 07:00 | 75.0647 | 53.53 | 10 | 0 | 0 | 20 | 1285.9472
4016 | 2023-06-17 08:00 | 100.2088 | 53.53 | 0 | 0 | 10 | 10 | 0
4017 | 2023-06-17 09:00 | 94.3179 | 53.53 | 0 | 0 | 10 | 0 | 0
4018 | 2023-06-17 10:00 | 83.6032 | 53.53 | 10 | 0 | 0 | 0 | 1371.3323
4019 | 2023-06-17 11:00 | 85.9372 | 53.53 | 10 | 0 | 0 | 0 | 1394.6723
4020 | 2023-06-17 12:00 | 87.4075 | 53.53 | 10 | 0 | 0 | 0 | 1409.3746
4021 | 2023-06-17 13:00 | 88.7647 | 53.53 | 10 | 0 | 0 | 0 | 1422.9465
4022 | 2023-06-17 14:00 | 77.5397 | 53.53 | 20 | 10 | 0 | 9.5 | 2621.3949
4023 | 2023-06-17 15:00 | 76.6371 | 53.53 | 20 | 10 | 0 | 19 | 2603.3426
4024 | 2023-06-17 16:00 | 80.0551 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1476.4672
4025 | 2023-06-17 17:00 | 94.6157 | 53.53 | 10 | 0 | 0 | 20 | 1481.4572
4026 | 2023-06-17 18:00 | 96.5073 | 53.53 | 0 | 0 | 10 | 10 | 0
4027 | 2023-06-17 19:00 | 106.142 | 53.53 | 0 | 0 | 10 | 0 | 0
4028 | 2023-06-17 20:00 | 79.6629 | 53.53 | 10 | 0 | 0 | 0 | 1331.9291
4029 | 2023-06-17 21:00 | 82.4155 | 53.53 | 10 | 0 | 0 | 0 | 1359.4552
4030 | 2023-06-17 22:00 | 73.2135 | 53.53 | 20 | 10 | 0 | 9.5 | 2534.8701
4031 | 2023-06-17 23:00 | 72.665 | 53.53 | 20 | 10 | 0 | 19 | 2523.9009
4032 | 2023-06-18 00:00 | 80.7145 | 53.53 | 1 | 0 | 9 | 10 | 134.2445
4033 | 2023-06-18 01:00 | 80.7835 | 53.53 | 0 | 0 | 10 | 0 | 0
4034 | 2023-06-18 02:00 | 51.0141 | 53.53 | 20 | 10 | 0 | 9.5 | 2090.8814
4035 | 2023-06-18 03:00 | 57.1407 | 53.53 | 11.5789 | 1.5789 | 0 | 11 | 1281.4497
4036 | 2023-06-18 04:00 | 79.2514 | 53.53 | 0 | 0 | 10 | 1 | 0
4037 | 2023-06-18 05:00 | 55.7667 | 53.53 | 20 | 10 | 0 | 10.5 | 2185.9334
4038 | 2023-06-18 06:00 | 51.2044 | 53.53 | 20 | 10 | 0 | 20 | 2094.6875
4039 | 2023-06-18 07:00 | 74.6285 | 53.53 | 10 | 0 | 0 | 20 | 1281.5847
4040 | 2023-06-18 08:00 | 86.5993 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 70.0646
4041 | 2023-06-18 09:00 | 84.7899 | 53.53 | 10 | 0 | 0 | 10.5 | 1383.1987
4042 | 2023-06-18 10:00 | 85.6642 | 53.53 | 10 | 0 | 0 | 10.5 | 1391.9425
4043 | 2023-06-18 11:00 | 77.1118 | 53.53 | 20 | 10 | 0 | 20 | 2612.8353
4044 | 2023-06-18 12:00 | 79.6276 | 53.53 | 10 | 0 | 0 | 20 | 1331.5756
4045 | 2023-06-18 13:00 | 84.803 | 53.53 | 10 | 0 | 0 | 20 | 1383.3301
4046 | 2023-06-18 14:00 | 84.689 | 53.53 | 10 | 0 | 0 | 20 | 1382.1902
4047 | 2023-06-18 15:00 | 81.9929 | 53.53 | 10 | 0 | 0 | 20 | 1355.2295
4048 | 2023-06-18 16:00 | 84.6053 | 53.53 | 10 | 0 | 0 | 20 | 1381.3534
4049 | 2023-06-18 17:00 | 101.3601 | 53.53 | 0 | 0 | 10 | 10 | 0
4050 | 2023-06-18 18:00 | 108.5436 | 53.53 | 0 | 0 | 10 | 0 | 0
4051 | 2023-06-18 19:00 | 100.1652 | 53.53 | 10 | 0 | 0 | 0 | 1536.9518
4052 | 2023-06-18 20:00 | 84.0781 | 53.53 | 10 | 0 | 0 | 0 | 1376.0814
4053 | 2023-06-18 21:00 | 77.1491 | 53.53 | 20 | 10 | 0 | 9.5 | 2613.5826
4054 | 2023-06-18 22:00 | 85.5792 | 53.53 | 10 | 0 | 0 | 9.5 | 1391.0923
4055 | 2023-06-18 23:00 | 78.8812 | 53.53 | 20 | 10 | 0 | 19 | 2648.2249
4056 | 2023-06-19 00:00 | 91.3133 | 53.53 | 0 | 0 | 10 | 9 | 0
4057 | 2023-06-19 01:00 | 89.8651 | 53.53 | 1 | 0 | 9 | 0 | 143.3951
4058 | 2023-06-19 02:00 | 68.7278 | 53.53 | 10 | 0 | 0 | 0 | 1222.5777
4059 | 2023-06-19 03:00 | 63.171 | 53.53 | 10 | 0 | 0 | 0 | 1167.0097
4060 | 2023-06-19 04:00 | -11.5561 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 463.9216
4061 | 2023-06-19 05:00 | -49.287 | 53.53 | 20 | 10 | 0 | 10.5 | 84.8602
4062 | 2023-06-19 06:00 | -13.365 | 53.53 | 20 | 10 | 0 | 20 | 803.3008
4063 | 2023-06-19 07:00 | 79.6029 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 66.5664
4064 | 2023-06-19 08:00 | -12.0713 | 65.03 | 20 | 10 | 0 | 20 | 1059.1749
4065 | 2023-06-19 09:00 | 97.2152 | 65.03 | 0 | 0 | 10 | 10 | 0
4066 | 2023-06-19 10:00 | 88.4223 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1615.2873
4067 | 2023-06-19 11:00 | 93.3438 | 65.03 | 10 | 0 | 0 | 10.5 | 1583.7383
4068 | 2023-06-19 12:00 | 93.2032 | 65.03 | 10 | 0 | 0 | 10.5 | 1582.3316
4069 | 2023-06-19 13:00 | 81.7605 | 65.03 | 20 | 10 | 0 | 20 | 2935.8099
4070 | 2023-06-19 14:00 | 92.3044 | 65.03 | 10 | 0 | 0 | 20 | 1573.3443
4071 | 2023-06-19 15:00 | 92.7458 | 65.03 | 10 | 0 | 0 | 20 | 1577.7583
4072 | 2023-06-19 16:00 | 92.7246 | 65.03 | 10 | 0 | 0 | 20 | 1577.5456
4073 | 2023-06-19 17:00 | 122.1294 | 66.4 | 0 | 0 | 10 | 10 | 0
4074 | 2023-06-19 18:00 | 101.2577 | 66.4 | 10 | 0 | 0 | 10 | 1676.5774
4075 | 2023-06-19 19:00 | 103.4193 | 65.03 | 0 | 0 | 10 | 0 | 0
4076 | 2023-06-19 20:00 | 75.3166 | 65.03 | 20 | 10 | 0 | 9.5 | 2806.9321
4077 | 2023-06-19 21:00 | 85.5395 | 65.03 | 10 | 0 | 0 | 9.5 | 1505.6955
4078 | 2023-06-19 22:00 | 86.1003 | 65.03 | 0.5 | 0 | 9.5 | 0 | 75.5652
4079 | 2023-06-19 23:00 | 80.3517 | 53.53 | 20 | 10 | 0 | 9.5 | 2677.6339
4080 | 2023-06-20 00:00 | 93.7527 | 53.53 | 0.5 | 0 | 9.5 | 0 | 73.6413
4081 | 2023-06-20 01:00 | 91.2628 | 53.53 | 10 | 0 | 0 | 0 | 1447.9277
4082 | 2023-06-20 02:00 | 64.4891 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1366.537
4083 | 2023-06-20 03:00 | 61.2677 | 53.53 | 20 | 10 | 0 | 11 | 2295.9532
4084 | 2023-06-20 04:00 | 72.911 | 53.53 | 0 | 0 | 10 | 1 | 0
4085 | 2023-06-20 05:00 | 63.7506 | 53.53 | 20 | 10 | 0 | 10.5 | 2345.6112
4086 | 2023-06-20 06:00 | -54.554 | 53.53 | 20 | 10 | 0 | 20 | -20.4798
4087 | 2023-06-20 07:00 | 73.8377 | 53.53 | 10 | 0 | 0 | 20 | 1273.6769
4088 | 2023-06-20 08:00 | 90.7982 | 65.03 | 10 | 0 | 0 | 20 | 1558.2819
4089 | 2023-06-20 09:00 | 100.25 | 65.03 | 0 | 0 | 10 | 10 | 0
4090 | 2023-06-20 10:00 | 118.3916 | 65.03 | 0 | 0 | 10 | 0 | 0
4091 | 2023-06-20 11:00 | 94.3647 | 65.03 | 10 | 0 | 0 | 0 | 1593.9468
4092 | 2023-06-20 12:00 | 88.7695 | 65.03 | 11.5789 | 1.5789 | 0 | 1.5 | 1780.8359
4093 | 2023-06-20 13:00 | 86.4191 | 65.03 | 20 | 10 | 0 | 11 | 3028.9813
4094 | 2023-06-20 14:00 | 98.4004 | 65.03 | 0 | 0 | 10 | 1 | 0
4095 | 2023-06-20 15:00 | -34.7092 | 65.03 | 20 | 10 | 0 | 10.5 | 606.4154
4096 | 2023-06-20 16:00 | -38.5393 | 65.03 | 20 | 10 | 0 | 20 | 529.8132
4097 | 2023-06-20 17:00 | 115.8489 | 66.4 | 0 | 0 | 10 | 10 | 0
4098 | 2023-06-20 18:00 | 112.3942 | 66.4 | 0 | 0 | 10 | 0 | 0
4099 | 2023-06-20 19:00 | 107.304 | 65.03 | 10 | 0 | 0 | 0 | 1723.3395
4100 | 2023-06-20 20:00 | 93.5156 | 65.03 | 10 | 0 | 0 | 0 | 1585.4559
4101 | 2023-06-20 21:00 | 90.2138 | 65.03 | 10 | 0 | 0 | 0 | 1552.4379
4102 | 2023-06-20 22:00 | 83.6935 | 65.03 | 10 | 0 | 0 | 0 | 1487.2349
4103 | 2023-06-20 23:00 | 102.4522 | 53.53 | 10 | 0 | 0 | 0 | 1559.8222
4104 | 2023-06-21 00:00 | 81.3951 | 53.53 | 20 | 10 | 0 | 9.5 | 2698.5016
4105 | 2023-06-21 01:00 | 90.4492 | 53.53 | 0.5 | 0 | 9.5 | 0 | 71.9896
4106 | 2023-06-21 02:00 | 50.9993 | 53.53 | 20 | 10 | 0 | 9.5 | 2090.587
4107 | 2023-06-21 03:00 | 75.5631 | 53.53 | 10 | 0 | 0 | 9.5 | 1290.931
4108 | 2023-06-21 04:00 | 77.7404 | 53.53 | 1.5 | 0 | 8.5 | 1 | 196.9056
4109 | 2023-06-21 05:00 | 64.1231 | 53.53 | 20 | 10 | 0 | 10.5 | 2353.0613
4110 | 2023-06-21 06:00 | 68.4608 | 53.53 | 20 | 10 | 0 | 20 | 2439.8164
4111 | 2023-06-21 07:00 | 88.4586 | 53.53 | 10 | 0 | 0 | 20 | 1419.8855
4112 | 2023-06-21 08:00 | 89.5138 | 65.03 | 10 | 0 | 0 | 20 | 1545.4376
4113 | 2023-06-21 09:00 | 98.3577 | 65.03 | 0 | 0 | 10 | 10 | 0
4114 | 2023-06-21 10:00 | 88.5132 | 65.03 | 20 | 10 | 0 | 19.5 | 3070.863
4115 | 2023-06-21 11:00 | 89.7253 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1629.0029
4116 | 2023-06-21 12:00 | 103.9547 | 65.03 | 0 | 0 | 10 | 10 | 0
4117 | 2023-06-21 13:00 | 102.3892 | 65.03 | 0 | 0 | 10 | 0 | 0
4118 | 2023-06-21 14:00 | 89.1242 | 65.03 | 20 | 10 | 0 | 9.5 | 3083.0838
4119 | 2023-06-21 15:00 | 88.9598 | 65.03 | 20 | 10 | 0 | 19 | 3079.7963
4120 | 2023-06-21 16:00 | 89.4964 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1707.923
4121 | 2023-06-21 17:00 | 115.0437 | 66.4 | 0 | 0 | 10 | 10 | 0
4122 | 2023-06-21 18:00 | 102.4188 | 66.4 | 10 | 0 | 0 | 10 | 1688.1885
4123 | 2023-06-21 19:00 | 111.722 | 65.03 | 0 | 0 | 10 | 0 | 0
4124 | 2023-06-21 20:00 | 95.1768 | 65.03 | 10 | 0 | 0 | 0 | 1602.0677
4125 | 2023-06-21 21:00 | 88.2451 | 65.03 | 20 | 10 | 0 | 9.5 | 3065.503
4126 | 2023-06-21 22:00 | 97.7468 | 65.03 | 0.5 | 0 | 9.5 | 0 | 81.3884
4127 | 2023-06-21 23:00 | 81.7171 | 53.53 | 10 | 0 | 0 | 0 | 1352.4706
4128 | 2023-06-22 00:00 | 82.3448 | 53.53 | 10 | 0 | 0 | 0 | 1358.7476
4129 | 2023-06-22 01:00 | 77.5456 | 53.53 | 10 | 0 | 0 | 0 | 1310.7562
4130 | 2023-06-22 02:00 | -72.3861 | 53.53 | 20 | 10 | 0 | 9.5 | -377.1212
4131 | 2023-06-22 03:00 | -55.5837 | 53.53 | 20 | 10 | 0 | 19 | -41.073
4132 | 2023-06-22 04:00 | 66.6642 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 180.2913
4133 | 2023-06-22 05:00 | 63.3691 | 53.53 | 10 | 0 | 0 | 10.5 | 1168.9912
4134 | 2023-06-22 06:00 | 57.1278 | 53.53 | 20 | 10 | 0 | 20 | 2213.156
4135 | 2023-06-22 07:00 | 79.7231 | 53.53 | 10 | 0 | 0 | 20 | 1332.5311
4136 | 2023-06-22 08:00 | 106.7523 | 65.03 | 0 | 0 | 10 | 10 | 0
4137 | 2023-06-22 09:00 | 95.4574 | 65.03 | 10 | 0 | 0 | 10 | 1604.8742
4138 | 2023-06-22 10:00 | 87.368 | 65.03 | 20 | 10 | 0 | 19.5 | 3047.9598
4139 | 2023-06-22 11:00 | 96.2964 | 65.03 | 10 | 0 | 0 | 19.5 | 1613.2642
4140 | 2023-06-22 12:00 | 92.8261 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1661.6434
4141 | 2023-06-22 13:00 | 139.3614 | 65.03 | 0 | 0 | 10 | 10 | 0
4142 | 2023-06-22 14:00 | 96.1309 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1696.4301
4143 | 2023-06-22 15:00 | 91.2006 | 65.03 | 20 | 10 | 0 | 20 | 3124.6115
4144 | 2023-06-22 16:00 | 107.1766 | 65.03 | 10 | 0 | 0 | 20 | 1722.0665
4145 | 2023-06-22 17:00 | 98.2888 | 66.4 | 10 | 0 | 0 | 20 | 1646.8876
4146 | 2023-06-22 18:00 | 109.6158 | 66.4 | 0 | 0 | 10 | 10 | 0
4147 | 2023-06-22 19:00 | 129.3752 | 65.03 | 0 | 0 | 10 | 0 | 0
4148 | 2023-06-22 20:00 | 88.0418 | 65.03 | 10 | 0 | 0 | 0 | 1530.7183
4149 | 2023-06-22 21:00 | 78.7615 | 65.03 | 10 | 0 | 0 | 0 | 1437.9146
4150 | 2023-06-22 22:00 | 86.0985 | 65.03 | 10 | 0 | 0 | 0 | 1511.2849
4151 | 2023-06-22 23:00 | 97.5748 | 53.53 | 10 | 0 | 0 | 0 | 1511.0477
4152 | 2023-06-23 00:00 | 86.8841 | 53.53 | 10 | 0 | 0 | 0 | 1404.1409
4153 | 2023-06-23 01:00 | 78.3361 | 53.53 | 10 | 0 | 0 | 0 | 1318.6609
4154 | 2023-06-23 02:00 | 59.2528 | 53.53 | 20 | 10 | 0 | 9.5 | 2255.6565
4155 | 2023-06-23 03:00 | 60.0341 | 53.53 | 20 | 10 | 0 | 19 | 2271.281
4156 | 2023-06-23 04:00 | 66.7595 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1329.5156
4157 | 2023-06-23 05:00 | 76.2484 | 53.53 | 10 | 0 | 0 | 20 | 1297.7837
4158 | 2023-06-23 06:00 | 73.1797 | 53.53 | 10 | 0 | 0 | 20 | 1267.097
4159 | 2023-06-23 07:00 | 87.5634 | 53.53 | 10 | 0 | 0 | 20 | 1410.9338
4160 | 2023-06-23 08:00 | 85.6648 | 65.03 | 10 | 0 | 0 | 20 | 1506.948
4161 | 2023-06-23 09:00 | 85.6835 | 65.03 | 10 | 0 | 0 | 20 | 1507.1348
4162 | 2023-06-23 10:00 | 98.2354 | 65.03 | 0 | 0 | 10 | 10 | 0
4163 | 2023-06-23 11:00 | 85.5954 | 65.03 | 20 | 10 | 0 | 19.5 | 3012.5079
4164 | 2023-06-23 12:00 | 92.2625 | 65.03 | 10 | 0 | 0 | 19.5 | 1572.9252
4165 | 2023-06-23 13:00 | 96.2867 | 65.03 | 0 | 0 | 10 | 9.5 | 0
4166 | 2023-06-23 14:00 | 86.6698 | 65.03 | 20 | 10 | 0 | 19 | 3033.9967
4167 | 2023-06-23 15:00 | 87.2844 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1683.4755
4168 | 2023-06-23 16:00 | 93.2023 | 65.03 | 10 | 0 | 0 | 20 | 1582.3227
4169 | 2023-06-23 17:00 | 112.976 | 66.4 | 0 | 0 | 10 | 10 | 0
4170 | 2023-06-23 18:00 | 118.2734 | 66.4 | 0 | 0 | 10 | 0 | 0
4171 | 2023-06-23 19:00 | -72.9153 | 65.03 | 20 | 10 | 0 | 9.5 | -157.7062
4172 | 2023-06-23 20:00 | -79.2881 | 65.03 | 20 | 10 | 0 | 19 | -285.1628
4173 | 2023-06-23 21:00 | 83.884 | 65.03 | 0 | 0 | 10 | 9 | 0
4174 | 2023-06-23 22:00 | 82.029 | 65.03 | 1 | 0 | 9 | 0 | 147.059
4175 | 2023-06-23 23:00 | 80.3459 | 53.53 | 10 | 0 | 0 | 0 | 1338.759
4176 | 2023-06-24 00:00 | 79.1699 | 53.53 | 10 | 0 | 0 | 0 | 1326.9987
4177 | 2023-06-24 01:00 | 78.5549 | 53.53 | 10 | 0 | 0 | 0 | 1320.8487
4178 | 2023-06-24 02:00 | 44.2135 | 53.53 | 20 | 10 | 0 | 9.5 | 1954.8699
4179 | 2023-06-24 03:00 | 50.6487 | 53.53 | 20 | 10 | 0 | 19 | 2083.5737
4180 | 2023-06-24 04:00 | 66.78 | 53.53 | 0 | 0 | 10 | 9 | 0
4181 | 2023-06-24 05:00 | 56.4995 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1274.0262
4182 | 2023-06-24 06:00 | 47.2409 | 53.53 | 20 | 10 | 0 | 20 | 2015.4175
4183 | 2023-06-24 07:00 | 101.5829 | 53.53 | 0 | 0 | 10 | 10 | 0
4184 | 2023-06-24 08:00 | 85.6822 | 53.53 | 10 | 0 | 0 | 10 | 1392.1218
4185 | 2023-06-24 09:00 | 88.9536 | 53.53 | 10 | 0 | 0 | 10 | 1424.8356
4186 | 2023-06-24 10:00 | 89.0817 | 53.53 | 10 | 0 | 0 | 10 | 1426.1171
4187 | 2023-06-24 11:00 | 83.2879 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1440.1886
4188 | 2023-06-24 12:00 | 80.996 | 53.53 | 20 | 10 | 0 | 20 | 2690.5195
4189 | 2023-06-24 13:00 | 108.1448 | 53.53 | 0 | 0 | 10 | 10 | 0
4190 | 2023-06-24 14:00 | 94.6772 | 53.53 | 10 | 0 | 0 | 10 | 1482.0725
4191 | 2023-06-24 15:00 | 92.8894 | 53.53 | 10 | 0 | 0 | 10 | 1464.1938
4192 | 2023-06-24 16:00 | 90.6166 | 53.53 | 10 | 0 | 0 | 10 | 1441.4659
4193 | 2023-06-24 17:00 | 94.4003 | 53.53 | 10 | 0 | 0 | 10 | 1479.3034
4194 | 2023-06-24 18:00 | 112.5748 | 53.53 | 0 | 0 | 10 | 0 | 0
4195 | 2023-06-24 19:00 | 95.3112 | 53.53 | 10 | 0 | 0 | 0 | 1488.4117
4196 | 2023-06-24 20:00 | 83.1159 | 53.53 | 10 | 0 | 0 | 0 | 1366.4585
4197 | 2023-06-24 21:00 | 71.1862 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1312.8017
4198 | 2023-06-24 22:00 | 69.4514 | 53.53 | 20 | 10 | 0 | 10 | 2459.6289
4199 | 2023-06-24 23:00 | 78.4032 | 53.53 | 0 | 0 | 10 | 0 | 0
4200 | 2023-06-25 00:00 | 70.5104 | 53.53 | 10 | 0 | 0 | 0 | 1240.4039
4201 | 2023-06-25 01:00 | 64.6633 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1368.5535
4202 | 2023-06-25 02:00 | 60.3002 | 53.53 | 20 | 10 | 0 | 11 | 2276.6038
4203 | 2023-06-25 03:00 | 78.1222 | 53.53 | 0 | 0 | 10 | 1 | 0
4204 | 2023-06-25 04:00 | 68.8284 | 53.53 | 10 | 0 | 0 | 1 | 1223.5836
4205 | 2023-06-25 05:00 | 54.041 | 53.53 | 20 | 10 | 0 | 10.5 | 2151.4206
4206 | 2023-06-25 06:00 | 55.9647 | 53.53 | 20 | 10 | 0 | 20 | 2189.8947
4207 | 2023-06-25 07:00 | 83.5269 | 53.53 | 10 | 0 | 0 | 20 | 1370.5686
4208 | 2023-06-25 08:00 | 95.9041 | 53.53 | 0 | 0 | 10 | 10 | 0
4209 | 2023-06-25 09:00 | 83.4501 | 53.53 | 20 | 10 | 0 | 19.5 | 2739.6022
4210 | 2023-06-25 10:00 | 86.156 | 53.53 | 10 | 0 | 0 | 19.5 | 1396.8596
4211 | 2023-06-25 11:00 | 88.2577 | 53.53 | 10 | 0 | 0 | 19.5 | 1417.8771
4212 | 2023-06-25 12:00 | 90.4174 | 53.53 | 10 | 0 | 0 | 19.5 | 1439.4744
4213 | 2023-06-25 13:00 | 84.9199 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1457.3673
4214 | 2023-06-25 14:00 | 85.0137 | 53.53 | 10 | 0 | 0 | 20 | 1385.437
4215 | 2023-06-25 15:00 | 98.7178 | 53.53 | 10 | 0 | 0 | 20 | 1522.4783
4216 | 2023-06-25 16:00 | 96.834 | 53.53 | 10 | 0 | 0 | 20 | 1503.6403
4217 | 2023-06-25 17:00 | 104.748 | 53.53 | 0 | 0 | 10 | 10 | 0
4218 | 2023-06-25 18:00 | 117.7699 | 53.53 | 0 | 0 | 10 | 0 | 0
4219 | 2023-06-25 19:00 | 98.1617 | 53.53 | 10 | 0 | 0 | 0 | 1516.9166
4220 | 2023-06-25 20:00 | 96.5796 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1580.1008
4221 | 2023-06-25 21:00 | 85.317 | 53.53 | 20 | 10 | 0 | 10 | 2776.9401
4222 | 2023-06-25 22:00 | 122.5969 | 53.53 | 0 | 0 | 10 | 0 | 0
4223 | 2023-06-25 23:00 | 68.3796 | 53.53 | 20 | 10 | 0 | 9.5 | 2438.1919
4224 | 2023-06-26 00:00 | 79.2278 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1397.4504
4225 | 2023-06-26 01:00 | 87.2451 | 53.53 | 0 | 0 | 10 | 0 | 0
4226 | 2023-06-26 02:00 | 67.0623 | 53.53 | 20 | 10 | 0 | 9.5 | 2411.847
4227 | 2023-06-26 03:00 | 83.775 | 53.53 | 0.5 | 0 | 9.5 | 0 | 68.6525
4228 | 2023-06-26 04:00 | -74.6399 | 53.53 | 20 | 10 | 0 | 9.5 | -422.1971
4229 | 2023-06-26 05:00 | 71.6958 | 53.53 | 10 | 0 | 0 | 9.5 | 1252.2578
4230 | 2023-06-26 06:00 | 74.3303 | 53.53 | 1.5 | 0 | 8.5 | 1 | 191.7904
4231 | 2023-06-26 07:00 | -10.4642 | 53.53 | 20 | 10 | 0 | 10.5 | 861.3164
4232 | 2023-06-26 08:00 | -36.0163 | 65.03 | 20 | 10 | 0 | 20 | 580.2746
4233 | 2023-06-26 09:00 | 107.036 | 65.03 | 0 | 0 | 10 | 10 | 0
4234 | 2023-06-26 10:00 | 105.0482 | 65.03 | 0 | 0 | 10 | 0 | 0
4235 | 2023-06-26 11:00 | 98.825 | 65.03 | 10 | 0 | 0 | 0 | 1638.5501
4236 | 2023-06-26 12:00 | 95.4789 | 65.03 | 10 | 0 | 0 | 0 | 1605.0887
4237 | 2023-06-26 13:00 | 95.653 | 65.03 | 10 | 0 | 0 | 0 | 1606.8295
4238 | 2023-06-26 14:00 | 93.3147 | 65.03 | 20 | 10 | 0 | 9.5 | 3166.8941
4239 | 2023-06-26 15:00 | 99.1972 | 65.03 | 10 | 0 | 0 | 9.5 | 1642.272
4240 | 2023-06-26 16:00 | 94.1329 | 65.03 | 20 | 10 | 0 | 19 | 3183.2582
4241 | 2023-06-26 17:00 | 103.2798 | 66.4 | 0 | 0 | 10 | 9 | 0
4242 | 2023-06-26 18:00 | 102.1507 | 66.4 | 10 | 0 | 0 | 9 | 1685.5074
4243 | 2023-06-26 19:00 | 103.849 | 65.03 | 1 | 0 | 9 | 0 | 168.879
4244 | 2023-06-26 20:00 | 90.6211 | 65.03 | 10 | 0 | 0 | 0 | 1556.5106
4245 | 2023-06-26 21:00 | 88.697 | 65.03 | 10 | 0 | 0 | 0 | 1537.2695
4246 | 2023-06-26 22:00 | 90.5667 | 65.03 | 10 | 0 | 0 | 0 | 1555.967
4247 | 2023-06-26 23:00 | 87.9512 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1489.2763
4248 | 2023-06-27 00:00 | 79.6096 | 53.53 | 20 | 10 | 0 | 10 | 2662.7922
4249 | 2023-06-27 01:00 | 97.7043 | 53.53 | 0 | 0 | 10 | 0 | 0
4250 | 2023-06-27 02:00 | 61.969 | 53.53 | 10 | 0 | 0 | 0 | 1154.9899
4251 | 2023-06-27 03:00 | 60.8501 | 53.53 | 20 | 10 | 0 | 9.5 | 2287.6015
4252 | 2023-06-27 04:00 | 67.7911 | 53.53 | 1.5 | 0 | 8.5 | 1 | 181.9816
4253 | 2023-06-27 05:00 | 53.3083 | 53.53 | 20 | 10 | 0 | 10.5 | 2136.7662
4254 | 2023-06-27 06:00 | 58.6199 | 53.53 | 20 | 10 | 0 | 20 | 2242.9985
4255 | 2023-06-27 07:00 | 92.4537 | 53.53 | 10 | 0 | 0 | 20 | 1459.837
4256 | 2023-06-27 08:00 | 83.7431 | 65.03 | 10 | 0 | 0 | 20 | 1487.731
4257 | 2023-06-27 09:00 | 103.8563 | 65.03 | 1.5 | 0 | 8.5 | 11.5 | 253.3295
4258 | 2023-06-27 10:00 | 108.2373 | 65.03 | 0 | 0 | 10 | 1.5 | 0
4259 | 2023-06-27 11:00 | 91.2754 | 65.03 | 20 | 10 | 0 | 11 | 3126.1086
4260 | 2023-06-27 12:00 | 96.1856 | 65.03 | 10 | 0 | 0 | 11 | 1612.1556
4261 | 2023-06-27 13:00 | 103.8722 | 65.03 | 0 | 0 | 10 | 1 | 0
4262 | 2023-06-27 14:00 | 90.6315 | 65.03 | 20 | 10 | 0 | 10.5 | 3113.2293
4263 | 2023-06-27 15:00 | 101.3323 | 65.03 | 10 | 0 | 0 | 10.5 | 1663.6235
4264 | 2023-06-27 16:00 | 89.3391 | 65.03 | 20 | 10 | 0 | 20 | 3087.3814
4265 | 2023-06-27 17:00 | 105.5611 | 66.4 | 0 | 0 | 10 | 10 | 0
4266 | 2023-06-27 18:00 | 103.5679 | 66.4 | 10 | 0 | 0 | 10 | 1699.6792
4267 | 2023-06-27 19:00 | 111.6049 | 65.03 | 0 | 0 | 10 | 0 | 0
4268 | 2023-06-27 20:00 | 99.2825 | 65.03 | 10 | 0 | 0 | 0 | 1643.1255
4269 | 2023-06-27 21:00 | 87.5549 | 65.03 | 10 | 0 | 0 | 0 | 1525.849
4270 | 2023-06-27 22:00 | 80.9714 | 65.03 | 10 | 0 | 0 | 0 | 1460.0135
4271 | 2023-06-27 23:00 | 76.9649 | 53.53 | 20 | 10 | 0 | 9.5 | 2609.8977
4272 | 2023-06-28 00:00 | 87.0401 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1479.6852
4273 | 2023-06-28 01:00 | 102.37 | 53.53 | 0 | 0 | 10 | 0 | 0
4274 | 2023-06-28 02:00 | 67.0327 | 53.53 | 10 | 0 | 0 | 0 | 1205.6271
4275 | 2023-06-28 03:00 | 61.1587 | 53.53 | 20 | 10 | 0 | 9.5 | 2293.773
4276 | 2023-06-28 04:00 | 70.3588 | 53.53 | 1.5 | 0 | 8.5 | 1 | 185.8331
4277 | 2023-06-28 05:00 | 62.1651 | 53.53 | 20 | 10 | 0 | 10.5 | 2313.9016
4278 | 2023-06-28 06:00 | 61.2162 | 53.53 | 20 | 10 | 0 | 20 | 2294.9247
4279 | 2023-06-28 07:00 | 77.651 | 53.53 | 1 | 0 | 9 | 11 | 131.181
4280 | 2023-06-28 08:00 | 107.0439 | 65.03 | 0 | 0 | 10 | 1 | 0
4281 | 2023-06-28 09:00 | -68.5676 | 65.03 | 20 | 10 | 0 | 10.5 | -70.7514
4282 | 2023-06-28 10:00 | -40.5925 | 65.03 | 20 | 10 | 0 | 20 | 488.7508
4283 | 2023-06-28 11:00 | 90.6513 | 65.03 | 10 | 0 | 0 | 20 | 1556.8132
4284 | 2023-06-28 12:00 | 91.0026 | 65.03 | 10 | 0 | 0 | 20 | 1560.3264
4285 | 2023-06-28 13:00 | 110.4347 | 65.03 | 0 | 0 | 10 | 10 | 0
4286 | 2023-06-28 14:00 | 89.0772 | 65.03 | 20 | 10 | 0 | 19.5 | 3082.1437
4287 | 2023-06-28 15:00 | 89.2844 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1624.3626
4288 | 2023-06-28 16:00 | 92.9392 | 65.03 | 10 | 0 | 0 | 20 | 1579.6923
4289 | 2023-06-28 17:00 | 112.2031 | 66.4 | 0 | 0 | 10 | 10 | 0
4290 | 2023-06-28 18:00 | 105.7946 | 66.4 | 0 | 0 | 10 | 0 | 0
4291 | 2023-06-28 19:00 | 99.4897 | 65.03 | 10 | 0 | 0 | 0 | 1645.1969
4292 | 2023-06-28 20:00 | 83.1802 | 65.03 | 20 | 10 | 0 | 9.5 | 2964.2039
4293 | 2023-06-28 21:00 | 100.6166 | 65.03 | 0.5 | 0 | 9.5 | 0 | 82.8233
4294 | 2023-06-28 22:00 | 89.4655 | 65.03 | 10 | 0 | 0 | 0 | 1544.9547
4295 | 2023-06-28 23:00 | 87.5211 | 53.53 | 10 | 0 | 0 | 0 | 1410.5106
4296 | 2023-06-29 00:00 | 82.0126 | 53.53 | 10 | 0 | 0 | 0 | 1355.4256
4297 | 2023-06-29 01:00 | 79.4106 | 53.53 | 10 | 0 | 0 | 0 | 1329.4064
4298 | 2023-06-29 02:00 | 80.2514 | 53.53 | 10 | 0 | 0 | 0 | 1337.8138
4299 | 2023-06-29 03:00 | 62.526 | 53.53 | 20 | 10 | 0 | 9.5 | 2321.1194
4300 | 2023-06-29 04:00 | 60.7847 | 53.53 | 20 | 10 | 0 | 19 | 2286.2939
4301 | 2023-06-29 05:00 | 73.6323 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 190.7434
4302 | 2023-06-29 06:00 | 59.0274 | 53.53 | 20 | 10 | 0 | 20 | 2251.1486
4303 | 2023-06-29 07:00 | 79.8131 | 53.53 | 10 | 0 | 0 | 20 | 1333.4312
4304 | 2023-06-29 08:00 | 93.9753 | 65.03 | 10 | 0 | 0 | 20 | 1590.0527
4305 | 2023-06-29 09:00 | 93.9003 | 65.03 | 10 | 0 | 0 | 20 | 1589.3033
4306 | 2023-06-29 10:00 | 95.9232 | 65.03 | 10 | 0 | 0 | 20 | 1609.5322
4307 | 2023-06-29 11:00 | 115.7214 | 65.03 | 0 | 0 | 10 | 10 | 0
4308 | 2023-06-29 12:00 | 96.5518 | 65.03 | 0 | 0 | 10 | 0 | 0
4309 | 2023-06-29 13:00 | 81.1475 | 65.03 | 20 | 10 | 0 | 9.5 | 2923.5499
4310 | 2023-06-29 14:00 | 96.4693 | 65.03 | 1.5 | 0 | 8.5 | 1 | 242.249
4311 | 2023-06-29 15:00 | -43.8255 | 65.03 | 20 | 10 | 0 | 10.5 | 424.0893
4312 | 2023-06-29 16:00 | -19.1092 | 65.03 | 20 | 10 | 0 | 20 | 918.4158
4313 | 2023-06-29 17:00 | 110.8127 | 66.4 | 0 | 0 | 10 | 10 | 0
4314 | 2023-06-29 18:00 | 108.6841 | 66.4 | 0 | 0 | 10 | 0 | 0
4315 | 2023-06-29 19:00 | 108.5068 | 65.03 | 10 | 0 | 0 | 0 | 1735.3681
4316 | 2023-06-29 20:00 | 93.9461 | 65.03 | 10 | 0 | 0 | 0 | 1589.761
4317 | 2023-06-29 21:00 | 85.1461 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1580.8007
4318 | 2023-06-29 22:00 | 82.7117 | 65.03 | 20 | 10 | 0 | 10 | 2954.8343
4319 | 2023-06-29 23:00 | 120.8286 | 53.53 | 0 | 0 | 10 | 0 | 0
4320 | 2023-06-30 00:00 | 79.0667 | 53.53 | 10 | 0 | 0 | 0 | 1325.9674
4321 | 2023-06-30 01:00 | 84.6608 | 53.53 | 10 | 0 | 0 | 0 | 1381.9077
4322 | 2023-06-30 02:00 | 54.8598 | 53.53 | 20 | 10 | 0 | 9.5 | 2167.7955
4323 | 2023-06-30 03:00 | 64.7873 | 53.53 | 1.5 | 0 | 8.5 | 1 | 177.4759
4324 | 2023-06-30 04:00 | -47.5196 | 53.53 | 20 | 10 | 0 | 10.5 | 120.2085
4325 | 2023-06-30 05:00 | -65.9747 | 53.53 | 20 | 10 | 0 | 20 | -248.8931
4326 | 2023-06-30 06:00 | 73.1041 | 53.53 | 10 | 0 | 0 | 20 | 1266.3411
4327 | 2023-06-30 07:00 | 87.7013 | 53.53 | 10 | 0 | 0 | 20 | 1412.3128
4328 | 2023-06-30 08:00 | 98.5464 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 81.7882
4329 | 2023-06-30 09:00 | 83.5934 | 65.03 | 20 | 10 | 0 | 20 | 2972.4682
4330 | 2023-06-30 10:00 | 112.276 | 65.03 | 0 | 0 | 10 | 10 | 0
4331 | 2023-06-30 11:00 | 86.3827 | 65.03 | 20 | 10 | 0 | 19.5 | 3028.255
4332 | 2023-06-30 12:00 | 108.4435 | 65.03 | 0 | 0 | 10 | 9.5 | 0
4333 | 2023-06-30 13:00 | 102.8636 | 65.03 | 10 | 0 | 0 | 9.5 | 1678.9359
4334 | 2023-06-30 14:00 | 98.6259 | 65.03 | 10 | 0 | 0 | 9.5 | 1636.559
4335 | 2023-06-30 15:00 | 88.2423 | 65.03 | 20 | 10 | 0 | 19 | 3065.4454
4336 | 2023-06-30 16:00 | 95.0615 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1769.4321
4337 | 2023-06-30 17:00 | 105.6045 | 66.4 | 10 | 0 | 0 | 20 | 1720.0454
4338 | 2023-06-30 18:00 | 109.1171 | 66.4 | 0 | 0 | 10 | 10 | 0
4339 | 2023-06-30 19:00 | 107.0928 | 65.03 | 0 | 0 | 10 | 0 | 0
4340 | 2023-06-30 20:00 | 77.4606 | 65.03 | 20 | 10 | 0 | 9.5 | 2849.8118
4341 | 2023-06-30 21:00 | 98.9005 | 65.03 | 0.5 | 0 | 9.5 | 0 | 81.9653
4342 | 2023-06-30 22:00 | -55.6422 | 65.03 | 20 | 10 | 0 | 9.5 | 187.7567
4343 | 2023-06-30 23:00 | 80.5143 | 53.53 | 0.5 | 0 | 9.5 | 0 | 67.0222
4344 | 2023-07-01 00:00 | -18.8449 | 53.53 | 20 | 10 | 0 | 9.5 | 693.7019
4345 | 2023-07-01 01:00 | 73.7366 | 53.53 | 0.5 | 0 | 9.5 | 0 | 63.6333
4346 | 2023-07-01 02:00 | 45.0186 | 53.53 | 20 | 10 | 0 | 9.5 | 1970.9715
4347 | 2023-07-01 03:00 | 38.6075 | 53.53 | 20 | 10 | 0 | 19 | 1842.7494
4348 | 2023-07-01 04:00 | 54.1461 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 161.5141
4349 | 2023-07-01 05:00 | -39.6702 | 53.53 | 20 | 10 | 0 | 20 | 277.196
4350 | 2023-07-01 06:00 | 49.445 | 53.53 | 10 | 0 | 0 | 20 | 1029.7502
4351 | 2023-07-01 07:00 | 63.615 | 53.53 | 10 | 0 | 0 | 20 | 1171.4496
4352 | 2023-07-01 08:00 | 81.5743 | 53.53 | 0 | 0 | 10 | 10 | 0
4353 | 2023-07-01 09:00 | 72.0095 | 53.53 | 20 | 10 | 0 | 19.5 | 2510.7906
4354 | 2023-07-01 10:00 | 74.2681 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1345.243
4355 | 2023-07-01 11:00 | 75.857 | 53.53 | 10 | 0 | 0 | 20 | 1293.8703
4356 | 2023-07-01 12:00 | 88.1012 | 53.53 | 0 | 0 | 10 | 10 | 0
4357 | 2023-07-01 13:00 | 78.3214 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1387.9097
4358 | 2023-07-01 14:00 | 77.7552 | 53.53 | 20 | 10 | 0 | 20 | 2625.7038
4359 | 2023-07-01 15:00 | 100.8363 | 53.53 | 0 | 0 | 10 | 10 | 0
4360 | 2023-07-01 16:00 | 83.6866 | 53.53 | 20 | 10 | 0 | 19.5 | 2744.3318
4361 | 2023-07-01 17:00 | 98.5745 | 53.53 | 0 | 0 | 10 | 9.5 | 0
4362 | 2023-07-01 18:00 | 93.2738 | 53.53 | 0.5 | 0 | 9.5 | 0 | 73.4019
4363 | 2023-07-01 19:00 | 91.8028 | 53.53 | 10 | 0 | 0 | 0 | 1453.328
4364 | 2023-07-01 20:00 | 63.8724 | 53.53 | 20 | 10 | 0 | 9.5 | 2348.0478
4365 | 2023-07-01 21:00 | 84.3298 | 53.53 | 0.5 | 0 | 9.5 | 0 | 68.9299
4366 | 2023-07-01 22:00 | 79.4972 | 53.53 | 10 | 0 | 0 | 0 | 1330.2722
4367 | 2023-07-01 23:00 | 69.59 | 53.53 | 10 | 0 | 0 | 0 | 1231.2004
4368 | 2023-07-02 00:00 | 69.89 | 53.53 | 10 | 0 | 0 | 0 | 1234.2
4369 | 2023-07-02 01:00 | -79.7907 | 53.53 | 20 | 10 | 0 | 9.5 | -525.2137
4370 | 2023-07-02 02:00 | -78.8537 | 53.53 | 20 | 10 | 0 | 19 | -506.4746
4371 | 2023-07-02 03:00 | 46.8435 | 53.53 | 10 | 0 | 0 | 19 | 1003.7355
4372 | 2023-07-02 04:00 | 43.6767 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1074.3901
4373 | 2023-07-02 05:00 | 68.4334 | 53.53 | 0 | 0 | 10 | 10 | 0
4374 | 2023-07-02 06:00 | 58.4091 | 53.53 | 20 | 10 | 0 | 19.5 | 2238.7822
4375 | 2023-07-02 07:00 | 58.8092 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1182.5174
4376 | 2023-07-02 08:00 | 71.7733 | 53.53 | 10 | 0 | 0 | 20 | 1253.0333
4377 | 2023-07-02 09:00 | 79.9252 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 66.7276
4378 | 2023-07-02 10:00 | 77.5946 | 53.53 | 10 | 0 | 0 | 10.5 | 1311.2465
4379 | 2023-07-02 11:00 | 72.7014 | 53.53 | 20 | 10 | 0 | 20 | 2524.6274
4380 | 2023-07-02 12:00 | 100.7026 | 53.53 | 0 | 0 | 10 | 10 | 0
4381 | 2023-07-02 13:00 | 83.3558 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1440.9028
4382 | 2023-07-02 14:00 | 84.7255 | 53.53 | 10 | 0 | 0 | 10.5 | 1382.5554
4383 | 2023-07-02 15:00 | 76.2115 | 53.53 | 20 | 10 | 0 | 20 | 2594.8303
4384 | 2023-07-02 16:00 | 86.947 | 53.53 | 10 | 0 | 0 | 20 | 1404.7704
4385 | 2023-07-02 17:00 | 93.2019 | 53.53 | 10 | 0 | 0 | 20 | 1467.3186
4386 | 2023-07-02 18:00 | 93.861 | 53.53 | 0 | 0 | 10 | 10 | 0
4387 | 2023-07-02 19:00 | 100.9277 | 53.53 | 0 | 0 | 10 | 0 | 0
4388 | 2023-07-02 20:00 | 66.2339 | 53.53 | 20 | 10 | 0 | 9.5 | 2395.278
4389 | 2023-07-02 21:00 | 91.2642 | 53.53 | 0.5 | 0 | 9.5 | 0 | 72.3971
4390 | 2023-07-02 22:00 | 77.3043 | 53.53 | 10 | 0 | 0 | 0 | 1308.3434
4391 | 2023-07-02 23:00 | 82.6123 | 53.53 | 10 | 0 | 0 | 0 | 1361.4234
4392 | 2023-07-03 00:00 | 72.0044 | 53.53 | 10 | 0 | 0 | 0 | 1255.3442
4393 | 2023-07-03 01:00 | 72.8506 | 53.53 | 10 | 0 | 0 | 0 | 1263.8062
4394 | 2023-07-03 02:00 | 51.5407 | 53.53 | 20 | 10 | 0 | 9.5 | 2101.4144
4395 | 2023-07-03 03:00 | 60.8478 | 53.53 | 10 | 0 | 0 | 9.5 | 1143.7782
4396 | 2023-07-03 04:00 | 59.3981 | 53.53 | 10 | 0 | 0 | 9.5 | 1129.2811
4397 | 2023-07-03 05:00 | 55.647 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1206.6928
4398 | 2023-07-03 06:00 | 52.3408 | 53.53 | 20 | 10 | 0 | 20 | 2117.4151
4399 | 2023-07-03 07:00 | 70.9952 | 53.53 | 10 | 0 | 0 | 20 | 1245.252
4400 | 2023-07-03 08:00 | 88.5373 | 65.03 | 10 | 0 | 0 | 20 | 1535.6731
4401 | 2023-07-03 09:00 | 85.6393 | 65.03 | 10 | 0 | 0 | 20 | 1506.693
4402 | 2023-07-03 10:00 | 84.2506 | 65.03 | 10 | 0 | 0 | 20 | 1492.806
4403 | 2023-07-03 11:00 | 103.6639 | 65.03 | 0 | 0 | 10 | 10 | 0
4404 | 2023-07-03 12:00 | 88.2884 | 65.03 | 20 | 10 | 0 | 19.5 | 3066.3685
4405 | 2023-07-03 13:00 | 100.4925 | 65.03 | 0 | 0 | 10 | 9.5 | 0
4406 | 2023-07-03 14:00 | 85.2024 | 65.03 | 20 | 10 | 0 | 19 | 3004.6484
4407 | 2023-07-03 15:00 | 90.8032 | 65.03 | 10 | 0 | 0 | 19 | 1558.3321
4408 | 2023-07-03 16:00 | 88.4857 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1696.7522
4409 | 2023-07-03 17:00 | 93.9214 | 66.4 | 10 | 0 | 0 | 20 | 1603.2141
4410 | 2023-07-03 18:00 | 117.2722 | 66.4 | 0 | 0 | 10 | 10 | 0
4411 | 2023-07-03 19:00 | 102.9049 | 65.03 | 0 | 0 | 10 | 0 | 0
4412 | 2023-07-03 20:00 | 90.1728 | 65.03 | 10 | 0 | 0 | 0 | 1552.0275
4413 | 2023-07-03 21:00 | 78.8491 | 65.03 | 10 | 0 | 0 | 0 | 1438.7907
4414 | 2023-07-03 22:00 | 82.692 | 65.03 | 10 | 0 | 0 | 0 | 1477.2205
4415 | 2023-07-03 23:00 | 73.1735 | 53.53 | 20 | 10 | 0 | 9.5 | 2534.0704
4416 | 2023-07-04 00:00 | 90.1206 | 53.53 | 0.5 | 0 | 9.5 | 0 | 71.8253
4417 | 2023-07-04 01:00 | 81.3465 | 53.53 | 10 | 0 | 0 | 0 | 1348.7645
4418 | 2023-07-04 02:00 | 61.8085 | 53.53 | 20 | 10 | 0 | 9.5 | 2306.7699
4419 | 2023-07-04 03:00 | 71.473 | 53.53 | 10 | 0 | 0 | 9.5 | 1250.0301
4420 | 2023-07-04 04:00 | 69.2653 | 53.53 | 10 | 0 | 0 | 9.5 | 1227.9527
4421 | 2023-07-04 05:00 | 65.3508 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1313.9458
4422 | 2023-07-04 06:00 | 50.2178 | 53.53 | 20 | 10 | 0 | 20 | 2074.9551
4423 | 2023-07-04 07:00 | 74.1892 | 53.53 | 10 | 0 | 0 | 20 | 1277.192
4424 | 2023-07-04 08:00 | 82.3972 | 65.03 | 10 | 0 | 0 | 20 | 1474.2717
4425 | 2023-07-04 09:00 | 94.9961 | 65.03 | 0 | 0 | 10 | 10 | 0
4426 | 2023-07-04 10:00 | 90.2115 | 65.03 | 0 | 0 | 10 | 0 | 0
4427 | 2023-07-04 11:00 | 80.3713 | 65.03 | 20 | 10 | 0 | 9.5 | 2908.0259
4428 | 2023-07-04 12:00 | 87.5221 | 65.03 | 10 | 0 | 0 | 9.5 | 1525.5206
4429 | 2023-07-04 13:00 | 79.8672 | 65.03 | 20 | 10 | 0 | 19 | 2897.9438
4430 | 2023-07-04 14:00 | 88.5028 | 65.03 | 1.5 | 0 | 8.5 | 10.5 | 230.2992
4431 | 2023-07-04 15:00 | 79.113 | 65.03 | 20 | 10 | 0 | 20 | 2882.8607
4432 | 2023-07-04 16:00 | 93.1964 | 65.03 | 10 | 0 | 0 | 20 | 1582.2645
4433 | 2023-07-04 17:00 | 106.9 | 66.4 | 10 | 0 | 0 | 20 | 1732.9999
4434 | 2023-07-04 18:00 | 123.2105 | 66.4 | 0 | 0 | 10 | 10 | 0
4435 | 2023-07-04 19:00 | 111.1393 | 65.03 | 0 | 0 | 10 | 0 | 0
4436 | 2023-07-04 20:00 | 80.9194 | 65.03 | 20 | 10 | 0 | 9.5 | 2918.9883
4437 | 2023-07-04 21:00 | 90.8523 | 65.03 | 0.5 | 0 | 9.5 | 0 | 77.9411
4438 | 2023-07-04 22:00 | 75.336 | 65.03 | 10 | 0 | 0 | 0 | 1403.6599
4439 | 2023-07-04 23:00 | 72.6284 | 53.53 | 20 | 10 | 0 | 9.5 | 2523.1689
4440 | 2023-07-05 00:00 | 81.526 | 53.53 | 0.5 | 0 | 9.5 | 0 | 67.528
4441 | 2023-07-05 01:00 | 66.9824 | 53.53 | 10 | 0 | 0 | 0 | 1205.1245
4442 | 2023-07-05 02:00 | 58.6211 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1239.5653
4443 | 2023-07-05 03:00 | 52.3065 | 53.53 | 20 | 10 | 0 | 10.5 | 2116.7303
4444 | 2023-07-05 04:00 | 59.6698 | 53.53 | 10 | 0 | 0 | 10.5 | 1131.9977
4445 | 2023-07-05 05:00 | 51.9918 | 53.53 | 20 | 10 | 0 | 20 | 2110.4369
4446 | 2023-07-05 06:00 | 62.2915 | 53.53 | 10 | 0 | 0 | 20 | 1158.2152
4447 | 2023-07-05 07:00 | 79.0437 | 53.53 | 10 | 0 | 0 | 20 | 1325.7368
4448 | 2023-07-05 08:00 | 101.9515 | 65.03 | 0 | 0 | 10 | 10 | 0
4449 | 2023-07-05 09:00 | 88.9489 | 65.03 | 10 | 0 | 0 | 10 | 1539.7887
4450 | 2023-07-05 10:00 | 83.7499 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1566.1039
4451 | 2023-07-05 11:00 | 87.1136 | 65.03 | 10 | 0 | 0 | 10.5 | 1521.4357
4452 | 2023-07-05 12:00 | 80.6016 | 65.03 | 20 | 10 | 0 | 20 | 2912.6317
4453 | 2023-07-05 13:00 | 92.1377 | 65.03 | 10 | 0 | 0 | 20 | 1571.6767
4454 | 2023-07-05 14:00 | 93.7377 | 65.03 | 10 | 0 | 0 | 20 | 1587.6774
4455 | 2023-07-05 15:00 | 116.3365 | 65.03 | 0 | 0 | 10 | 10 | 0
4456 | 2023-07-05 16:00 | 84.6437 | 65.03 | 20 | 10 | 0 | 19.5 | 2993.4743
4457 | 2023-07-05 17:00 | 101.9684 | 66.4 | 0.5 | 0 | 9.5 | 10 | 84.1842
4458 | 2023-07-05 18:00 | 99.9325 | 66.4 | 10 | 0 | 0 | 10 | 1663.3248
4459 | 2023-07-05 19:00 | 105.5409 | 65.03 | 0 | 0 | 10 | 0 | 0
4460 | 2023-07-05 20:00 | 86.9313 | 65.03 | 10 | 0 | 0 | 0 | 1519.6132
4461 | 2023-07-05 21:00 | 83.5012 | 65.03 | 20 | 10 | 0 | 9.5 | 2970.6237
4462 | 2023-07-05 22:00 | 93.5301 | 65.03 | 0.5 | 0 | 9.5 | 0 | 79.2801
4463 | 2023-07-05 23:00 | 74.674 | 53.53 | 20 | 10 | 0 | 9.5 | 2564.0793
4464 | 2023-07-06 00:00 | 87.5051 | 53.53 | 0.5 | 0 | 9.5 | 0 | 70.5175
4465 | 2023-07-06 01:00 | 83.2816 | 53.53 | 10 | 0 | 0 | 0 | 1368.1157
4466 | 2023-07-06 02:00 | 58.8082 | 53.53 | 20 | 10 | 0 | 9.5 | 2246.7649
4467 | 2023-07-06 03:00 | 56.6444 | 53.53 | 20 | 10 | 0 | 19 | 2203.4886
4468 | 2023-07-06 04:00 | 85.6717 | 53.53 | 0 | 0 | 10 | 9 | 0
4469 | 2023-07-06 05:00 | 53.4639 | 53.53 | 20 | 10 | 0 | 18.5 | 2139.8782
4470 | 2023-07-06 06:00 | 61.2357 | 53.53 | 11.5789 | 1.5789 | 0 | 20 | 1328.8661
4471 | 2023-07-06 07:00 | 73.8599 | 53.53 | 10 | 0 | 0 | 20 | 1273.899
4472 | 2023-07-06 08:00 | 106.6138 | 65.03 | 0 | 0 | 10 | 10 | 0
4473 | 2023-07-06 09:00 | 96.5182 | 65.03 | 1 | 0 | 9 | 1 | 161.5482
4474 | 2023-07-06 10:00 | 84.295 | 65.03 | 20 | 10 | 0 | 10.5 | 2986.4992
4475 | 2023-07-06 11:00 | 93.0541 | 65.03 | 10 | 0 | 0 | 10.5 | 1580.8412
4476 | 2023-07-06 12:00 | 90.9077 | 65.03 | 10 | 0 | 0 | 10.5 | 1559.3769
4477 | 2023-07-06 13:00 | 85.309 | 65.03 | 20 | 10 | 0 | 20 | 3006.7791
4478 | 2023-07-06 14:00 | 95.2831 | 65.03 | 10 | 0 | 0 | 20 | 1603.1315
4479 | 2023-07-06 15:00 | 91.9954 | 65.03 | 10 | 0 | 0 | 20 | 1570.2544
4480 | 2023-07-06 16:00 | 90.5695 | 65.03 | 10 | 0 | 0 | 20 | 1555.9954
4481 | 2023-07-06 17:00 | 103.5859 | 66.4 | 10 | 0 | 0 | 20 | 1699.8588
4482 | 2023-07-06 18:00 | 107.3496 | 66.4 | 0 | 0 | 10 | 10 | 0
4483 | 2023-07-06 19:00 | 105.6793 | 65.03 | 0 | 0 | 10 | 0 | 0
4484 | 2023-07-06 20:00 | 84.3455 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1572.3732
4485 | 2023-07-06 21:00 | 79.5247 | 65.03 | 20 | 10 | 0 | 10 | 2891.0938
4486 | 2023-07-06 22:00 | 100.4528 | 65.03 | 0 | 0 | 10 | 0 | 0
4487 | 2023-07-06 23:00 | 72.1407 | 53.53 | 20 | 10 | 0 | 9.5 | 2513.4146
4488 | 2023-07-07 00:00 | 82.3204 | 53.53 | 0.5 | 0 | 9.5 | 0 | 67.9252
4489 | 2023-07-07 01:00 | 76.6083 | 53.53 | 10 | 0 | 0 | 0 | 1301.3827
4490 | 2023-07-07 02:00 | 76.281 | 53.53 | 10 | 0 | 0 | 0 | 1298.11
4491 | 2023-07-07 03:00 | 52.9629 | 53.53 | 20 | 10 | 0 | 9.5 | 2129.8573
4492 | 2023-07-07 04:00 | 53.9497 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1187.9331
4493 | 2023-07-07 05:00 | 52.5872 | 53.53 | 20 | 10 | 0 | 20 | 2122.3444
4494 | 2023-07-07 06:00 | 61.4459 | 53.53 | 10 | 0 | 0 | 20 | 1149.759
4495 | 2023-07-07 07:00 | 70.4578 | 53.53 | 10 | 0 | 0 | 20 | 1239.8782
4496 | 2023-07-07 08:00 | 85.5551 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 75.2925
4497 | 2023-07-07 09:00 | 77.0056 | 65.03 | 20 | 10 | 0 | 20 | 2840.7113
4498 | 2023-07-07 10:00 | 90.7681 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 77.899
4499 | 2023-07-07 11:00 | 85.4146 | 65.03 | 10 | 0 | 0 | 10.5 | 1504.4462
4500 | 2023-07-07 12:00 | 79.8962 | 65.03 | 20 | 10 | 0 | 20 | 2898.5245
4501 | 2023-07-07 13:00 | 98.5227 | 65.03 | 0 | 0 | 10 | 10 | 0
4502 | 2023-07-07 14:00 | 80.7858 | 65.03 | 20 | 10 | 0 | 19.5 | 2916.3168
4503 | 2023-07-07 15:00 | 95.6504 | 65.03 | 1 | 0 | 9 | 10.5 | 160.6804
4504 | 2023-07-07 16:00 | 84.1566 | 65.03 | 20 | 10 | 0 | 20 | 2983.7317
4505 | 2023-07-07 17:00 | 119.3192 | 66.4 | 0 | 0 | 10 | 10 | 0
4506 | 2023-07-07 18:00 | 110.2022 | 66.4 | 0 | 0 | 10 | 0 | 0
4507 | 2023-07-07 19:00 | 97.3741 | 65.03 | 10 | 0 | 0 | 0 | 1624.041
4508 | 2023-07-07 20:00 | 77.8852 | 65.03 | 20 | 10 | 0 | 9.5 | 2858.3048
4509 | 2023-07-07 21:00 | 88.8784 | 65.03 | 0.5 | 0 | 9.5 | 0 | 76.9542
4510 | 2023-07-07 22:00 | 82.0059 | 65.03 | 10 | 0 | 0 | 0 | 1470.3592
4511 | 2023-07-07 23:00 | 77.66 | 53.53 | 10 | 0 | 0 | 0 | 1311.8996
4512 | 2023-07-08 00:00 | 82.5166 | 53.53 | 10 | 0 | 0 | 0 | 1360.4658
4513 | 2023-07-08 01:00 | 65.8691 | 53.53 | 10 | 0 | 0 | 0 | 1193.9907
4514 | 2023-07-08 02:00 | 51.5925 | 53.53 | 20 | 10 | 0 | 9.5 | 2102.4494
4515 | 2023-07-08 03:00 | 59.1885 | 53.53 | 1.5 | 0 | 8.5 | 1 | 169.0778
4516 | 2023-07-08 04:00 | 57.7666 | 53.53 | 10 | 0 | 0 | 1 | 1112.9658
4517 | 2023-07-08 05:00 | 49.7294 | 53.53 | 20 | 10 | 0 | 10.5 | 2065.1884
4518 | 2023-07-08 06:00 | 48.8228 | 53.53 | 20 | 10 | 0 | 20 | 2047.0551
4519 | 2023-07-08 07:00 | 60.7369 | 53.53 | 10 | 0 | 0 | 20 | 1142.669
4520 | 2023-07-08 08:00 | 74.1089 | 53.53 | 10 | 0 | 0 | 20 | 1276.3888
4521 | 2023-07-08 09:00 | 83.4037 | 53.53 | 1 | 0 | 9 | 11 | 136.9337
4522 | 2023-07-08 10:00 | 79.8853 | 53.53 | 10 | 0 | 0 | 11 | 1334.1529
4523 | 2023-07-08 11:00 | 81.4666 | 53.53 | 10 | 0 | 0 | 11 | 1349.9662
4524 | 2023-07-08 12:00 | 90.0445 | 53.53 | 0 | 0 | 10 | 1 | 0
4525 | 2023-07-08 13:00 | 73.4067 | 53.53 | 20 | 10 | 0 | 10.5 | 2538.7335
4526 | 2023-07-08 14:00 | 79.1883 | 53.53 | 10 | 0 | 0 | 10.5 | 1327.1825
4527 | 2023-07-08 15:00 | 82.3545 | 53.53 | 10 | 0 | 0 | 10.5 | 1358.8447
4528 | 2023-07-08 16:00 | 76.1376 | 53.53 | 20 | 10 | 0 | 20 | 2593.3528
4529 | 2023-07-08 17:00 | 109.3083 | 53.53 | 0 | 0 | 10 | 10 | 0
4530 | 2023-07-08 18:00 | 103.7319 | 53.53 | 0 | 0 | 10 | 0 | 0
4531 | 2023-07-08 19:00 | 98.1718 | 53.53 | 10 | 0 | 0 | 0 | 1517.0181
4532 | 2023-07-08 20:00 | 93.7243 | 53.53 | 10 | 0 | 0 | 0 | 1472.543
4533 | 2023-07-08 21:00 | 66.8443 | 53.53 | 20 | 10 | 0 | 9.5 | 2407.4859
4534 | 2023-07-08 22:00 | 75.8404 | 53.53 | 0.5 | 0 | 9.5 | 0 | 64.6852
4535 | 2023-07-08 23:00 | 73.8025 | 53.53 | 10 | 0 | 0 | 0 | 1273.325
4536 | 2023-07-09 00:00 | 64.8996 | 53.53 | 20 | 10 | 0 | 9.5 | 2368.5928
4537 | 2023-07-09 01:00 | 73.2585 | 53.53 | 0.5 | 0 | 9.5 | 0 | 63.3943
4538 | 2023-07-09 02:00 | 43.8359 | 53.53 | 20 | 10 | 0 | 9.5 | 1947.3188
4539 | 2023-07-09 03:00 | 56.653 | 53.53 | 10 | 0 | 0 | 9.5 | 1101.8301
4540 | 2023-07-09 04:00 | 60.2354 | 53.53 | 1.5 | 0 | 8.5 | 1 | 170.6481
4541 | 2023-07-09 05:00 | 53.0266 | 53.53 | 20 | 10 | 0 | 10.5 | 2131.1312
4542 | 2023-07-09 06:00 | 40.2381 | 53.53 | 20 | 10 | 0 | 20 | 1875.3614
4543 | 2023-07-09 07:00 | 64.6042 | 53.53 | 10 | 0 | 0 | 20 | 1181.3418
4544 | 2023-07-09 08:00 | 85.5135 | 53.53 | 0 | 0 | 10 | 10 | 0
4545 | 2023-07-09 09:00 | 81.0578 | 53.53 | 10 | 0 | 0 | 10 | 1345.878
4546 | 2023-07-09 10:00 | 67.0398 | 53.53 | 20 | 10 | 0 | 19.5 | 2411.3957
4547 | 2023-07-09 11:00 | 92.1949 | 53.53 | 0 | 0 | 10 | 9.5 | 0
4548 | 2023-07-09 12:00 | 81.9445 | 53.53 | 10 | 0 | 0 | 9.5 | 1354.7453
4549 | 2023-07-09 13:00 | 75.4518 | 53.53 | 20 | 10 | 0 | 19 | 2579.6358
4550 | 2023-07-09 14:00 | 89.5937 | 53.53 | 0 | 0 | 10 | 9 | 0
4551 | 2023-07-09 15:00 | 76.2999 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1503.2938
4552 | 2023-07-09 16:00 | 76.2332 | 53.53 | 20 | 10 | 0 | 20 | 2595.2648
4553 | 2023-07-09 17:00 | 98.7357 | 53.53 | 10 | 0 | 0 | 20 | 1522.6574
4554 | 2023-07-09 18:00 | 113.5551 | 53.53 | 0 | 0 | 10 | 10 | 0
4555 | 2023-07-09 19:00 | 111.5871 | 53.53 | 0 | 0 | 10 | 0 | 0
4556 | 2023-07-09 20:00 | 78.7471 | 53.53 | 10 | 0 | 0 | 0 | 1322.7709
4557 | 2023-07-09 21:00 | 79.6182 | 53.53 | 10 | 0 | 0 | 0 | 1331.4824
4558 | 2023-07-09 22:00 | 82.5986 | 53.53 | 10 | 0 | 0 | 0 | 1361.2859
4559 | 2023-07-09 23:00 | 63.0446 | 53.53 | 20 | 10 | 0 | 9.5 | 2331.4915
4560 | 2023-07-10 00:00 | 84.2278 | 53.53 | 0.5 | 0 | 9.5 | 0 | 68.8789
4561 | 2023-07-10 01:00 | 73.9568 | 53.53 | 10 | 0 | 0 | 0 | 1274.8682
4562 | 2023-07-10 02:00 | 61.4047 | 53.53 | 10 | 0 | 0 | 0 | 1149.3472
4563 | 2023-07-10 03:00 | 57.2492 | 53.53 | 20 | 10 | 0 | 9.5 | 2215.5841
4564 | 2023-07-10 04:00 | 62.9547 | 53.53 | 10 | 0 | 0 | 9.5 | 1164.8469
4565 | 2023-07-10 05:00 | 59.8 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1252.5943
4566 | 2023-07-10 06:00 | 43.8423 | 53.53 | 20 | 10 | 0 | 20 | 1947.4456
4567 | 2023-07-10 07:00 | 80.2766 | 53.53 | 10 | 0 | 0 | 20 | 1338.0665
4568 | 2023-07-10 08:00 | 94.2096 | 65.03 | 10 | 0 | 0 | 20 | 1592.3964
4569 | 2023-07-10 09:00 | 92.4768 | 65.03 | 10 | 0 | 0 | 20 | 1575.068
4570 | 2023-07-10 10:00 | 88.1406 | 65.03 | 10 | 0 | 0 | 20 | 1531.7063
4571 | 2023-07-10 11:00 | 104.8144 | 65.03 | 0 | 0 | 10 | 10 | 0
4572 | 2023-07-10 12:00 | 91.3462 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1646.0648
4573 | 2023-07-10 13:00 | 92.4061 | 65.03 | 10 | 0 | 0 | 10.5 | 1574.3611
4574 | 2023-07-10 14:00 | 98.0982 | 65.03 | 10 | 0 | 0 | 10.5 | 1631.2823
4575 | 2023-07-10 15:00 | 91.7712 | 65.03 | 10 | 0 | 0 | 10.5 | 1568.0117
4576 | 2023-07-10 16:00 | 82.9941 | 65.03 | 20 | 10 | 0 | 20 | 2960.4829
4577 | 2023-07-10 17:00 | 90.928 | 66.4 | 10 | 0 | 0 | 20 | 1573.2796
4578 | 2023-07-10 18:00 | 100.5642 | 66.4 | 0 | 0 | 10 | 10 | 0
4579 | 2023-07-10 19:00 | 110.3093 | 65.03 | 0 | 0 | 10 | 0 | 0
4580 | 2023-07-10 20:00 | 81.3855 | 65.03 | 20 | 10 | 0 | 9.5 | 2928.3104
4581 | 2023-07-10 21:00 | 90.6908 | 65.03 | 0.5 | 0 | 9.5 | 0 | 77.8604
4582 | 2023-07-10 22:00 | 85.039 | 65.03 | 10 | 0 | 0 | 0 | 1500.6903
4583 | 2023-07-10 23:00 | 90.6909 | 53.53 | 10 | 0 | 0 | 0 | 1442.2087
4584 | 2023-07-11 00:00 | 76.7794 | 53.53 | 10 | 0 | 0 | 0 | 1303.094
4585 | 2023-07-11 01:00 | 82.6633 | 53.53 | 10 | 0 | 0 | 0 | 1361.9333
4586 | 2023-07-11 02:00 | 62.9955 | 53.53 | 20 | 10 | 0 | 9.5 | 2330.5098
4587 | 2023-07-11 03:00 | 73.125 | 53.53 | 0.5 | 0 | 9.5 | 0 | 63.3275
4588 | 2023-07-11 04:00 | 48.8808 | 53.53 | 20 | 10 | 0 | 9.5 | 2048.2167
4589 | 2023-07-11 05:00 | 55.6862 | 53.53 | 0.5 | 0 | 9.5 | 0 | 54.6081
4590 | 2023-07-11 06:00 | -51.4888 | 53.53 | 20 | 10 | 0 | 9.5 | 40.824
4591 | 2023-07-11 07:00 | -35.9515 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 194.2887
4592 | 2023-07-11 08:00 | -50.2361 | 65.03 | 20 | 10 | 0 | 20 | 295.8786
4593 | 2023-07-11 09:00 | 86.7966 | 65.03 | 10 | 0 | 0 | 20 | 1518.2665
4594 | 2023-07-11 10:00 | 95.2733 | 65.03 | 10 | 0 | 0 | 20 | 1603.033
4595 | 2023-07-11 11:00 | 96.3414 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 80.6857
4596 | 2023-07-11 12:00 | 86.3413 | 65.03 | 20 | 10 | 0 | 20 | 3027.4255
4597 | 2023-07-11 13:00 | 91.5025 | 65.03 | 10 | 0 | 0 | 20 | 1565.3251
4598 | 2023-07-11 14:00 | 99.5228 | 65.03 | 10 | 0 | 0 | 20 | 1645.5282
4599 | 2023-07-11 15:00 | 107.9786 | 65.03 | 0 | 0 | 10 | 10 | 0
4600 | 2023-07-11 16:00 | 95.137 | 65.03 | 20 | 10 | 0 | 19.5 | 3203.3399
4601 | 2023-07-11 17:00 | 104.2315 | 66.4 | 0.5 | 0 | 9.5 | 10 | 85.3158
4602 | 2023-07-11 18:00 | 103.496 | 66.4 | 10 | 0 | 0 | 10 | 1698.9601
4603 | 2023-07-11 19:00 | 108.4486 | 65.03 | 0 | 0 | 10 | 0 | 0
4604 | 2023-07-11 20:00 | 83.0456 | 65.03 | 10 | 0 | 0 | 0 | 1480.7564
4605 | 2023-07-11 21:00 | 85.3618 | 65.03 | 10 | 0 | 0 | 0 | 1503.9185
4606 | 2023-07-11 22:00 | 77.1 | 65.03 | 10 | 0 | 0 | 0 | 1421.2997
4607 | 2023-07-11 23:00 | 90.7902 | 53.53 | 10 | 0 | 0 | 0 | 1443.2024
4608 | 2023-07-12 00:00 | 71.656 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1317.7477
4609 | 2023-07-12 01:00 | 75.8587 | 53.53 | 10 | 0 | 0 | 0.5 | 1293.8874
4610 | 2023-07-12 02:00 | 59.6411 | 53.53 | 20 | 10 | 0 | 10 | 2263.4215
4611 | 2023-07-12 03:00 | 79.3283 | 53.53 | 0 | 0 | 10 | 0 | 0
4612 | 2023-07-12 04:00 | 55.9209 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1209.721
4613 | 2023-07-12 05:00 | 54.3706 | 53.53 | 20 | 10 | 0 | 10.5 | 2158.0114
4614 | 2023-07-12 06:00 | 55.0905 | 53.53 | 20 | 10 | 0 | 20 | 2172.4091
4615 | 2023-07-12 07:00 | 95.0204 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 74.2752
4616 | 2023-07-12 08:00 | 74.6512 | 65.03 | 20 | 10 | 0 | 20 | 2793.6233
4617 | 2023-07-12 09:00 | 82.4036 | 65.03 | 10 | 0 | 0 | 20 | 1474.3356
4618 | 2023-07-12 10:00 | 120.626 | 65.03 | 0 | 0 | 10 | 10 | 0
4619 | 2023-07-12 11:00 | 93.747 | 65.03 | 10 | 0 | 0 | 10 | 1587.7698
4620 | 2023-07-12 12:00 | 81.8392 | 65.03 | 20 | 10 | 0 | 19.5 | 2937.3832
4621 | 2023-07-12 13:00 | 88.5859 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1617.0094
4622 | 2023-07-12 14:00 | 89.4094 | 65.03 | 10 | 0 | 0 | 20 | 1544.3937
4623 | 2023-07-12 15:00 | 96.1224 | 65.03 | 10 | 0 | 0 | 20 | 1611.5237
4624 | 2023-07-12 16:00 | 107.3099 | 65.03 | 10 | 0 | 0 | 20 | 1723.3989
4625 | 2023-07-12 17:00 | 106.9891 | 66.4 | 0 | 0 | 10 | 10 | 0
4626 | 2023-07-12 18:00 | 100.1607 | 66.4 | 10 | 0 | 0 | 10 | 1665.6069
4627 | 2023-07-12 19:00 | 110.5566 | 65.03 | 0 | 0 | 10 | 0 | 0
4628 | 2023-07-12 20:00 | 79.1735 | 65.03 | 10 | 0 | 0 | 0 | 1442.0354
4629 | 2023-07-12 21:00 | 77.2345 | 65.03 | 10 | 0 | 0 | 0 | 1422.6446
4630 | 2023-07-12 22:00 | 73.6433 | 65.03 | 10 | 0 | 0 | 0 | 1386.7329
4631 | 2023-07-12 23:00 | 69.5306 | 53.53 | 10 | 0 | 0 | 0 | 1230.6058
4632 | 2023-07-13 00:00 | 73.0032 | 53.53 | 10 | 0 | 0 | 0 | 1265.3316
4633 | 2023-07-13 01:00 | 71.4568 | 53.53 | 10 | 0 | 0 | 0 | 1249.8682
4634 | 2023-07-13 02:00 | 61.3615 | 53.53 | 10 | 0 | 0 | 0 | 1148.915
4635 | 2023-07-13 03:00 | 51.3433 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1159.1264
4636 | 2023-07-13 04:00 | -44.0492 | 53.53 | 20 | 10 | 0 | 10.5 | 189.6161
4637 | 2023-07-13 05:00 | 52.1764 | 53.53 | 10 | 0 | 0 | 10.5 | 1057.0638
4638 | 2023-07-13 06:00 | -55.136 | 53.53 | 20 | 10 | 0 | 20 | -32.1192
4639 | 2023-07-13 07:00 | 74.746 | 53.53 | 10 | 0 | 0 | 20 | 1282.7595
4640 | 2023-07-13 08:00 | 103.3364 | 65.03 | 0 | 0 | 10 | 10 | 0
4641 | 2023-07-13 09:00 | 84.6954 | 65.03 | 10 | 0 | 0 | 10 | 1497.254
4642 | 2023-07-13 10:00 | 96.4605 | 65.03 | 0 | 0 | 10 | 0 | 0
4643 | 2023-07-13 11:00 | 88.7563 | 65.03 | 10 | 0 | 0 | 0 | 1537.8634
4644 | 2023-07-13 12:00 | 88.583 | 65.03 | 10 | 0 | 0 | 0 | 1536.1303
4645 | 2023-07-13 13:00 | 83.3564 | 65.03 | 20 | 10 | 0 | 9.5 | 2967.7275
4646 | 2023-07-13 14:00 | 88.4613 | 65.03 | 10 | 0 | 0 | 9.5 | 1534.913
4647 | 2023-07-13 15:00 | 83.771 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1644.6427
4648 | 2023-07-13 16:00 | -19.7522 | 65.03 | 20 | 10 | 0 | 20 | 905.5566
4649 | 2023-07-13 17:00 | 102.1878 | 66.4 | 0 | 0 | 10 | 10 | 0
4650 | 2023-07-13 18:00 | 97.729 | 66.4 | 10 | 0 | 0 | 10 | 1641.2899
4651 | 2023-07-13 19:00 | 112.5628 | 65.03 | 0 | 0 | 10 | 0 | 0
4652 | 2023-07-13 20:00 | 87.3136 | 65.03 | 10 | 0 | 0 | 0 | 1523.4361
4653 | 2023-07-13 21:00 | 80.7539 | 65.03 | 10 | 0 | 0 | 0 | 1457.839
4654 | 2023-07-13 22:00 | 85.0137 | 65.03 | 10 | 0 | 0 | 0 | 1500.4367
4655 | 2023-07-13 23:00 | 78.2775 | 53.53 | 10 | 0 | 0 | 0 | 1318.0748
4656 | 2023-07-14 00:00 | 73.1693 | 53.53 | 10 | 0 | 0 | 0 | 1266.9925
4657 | 2023-07-14 01:00 | 79.4327 | 53.53 | 10 | 0 | 0 | 0 | 1329.6266
4658 | 2023-07-14 02:00 | 54.6488 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1195.6609
4659 | 2023-07-14 03:00 | 52.7273 | 53.53 | 20 | 10 | 0 | 10.5 | 2125.1452
4660 | 2023-07-14 04:00 | 49.2626 | 53.53 | 20 | 10 | 0 | 20 | 2055.8518
4661 | 2023-07-14 05:00 | 56.3484 | 53.53 | 10 | 0 | 0 | 20 | 1098.7837
4662 | 2023-07-14 06:00 | 63.5336 | 53.53 | 10 | 0 | 0 | 20 | 1170.6363
4663 | 2023-07-14 07:00 | 74.1954 | 53.53 | 10 | 0 | 0 | 20 | 1277.2541
4664 | 2023-07-14 08:00 | 117.1531 | 65.03 | 0 | 0 | 10 | 10 | 0
4665 | 2023-07-14 09:00 | 96.5071 | 65.03 | 0 | 0 | 10 | 0 | 0
4666 | 2023-07-14 10:00 | -27.4277 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 415.6039
4667 | 2023-07-14 11:00 | -47.5028 | 65.03 | 20 | 10 | 0 | 10.5 | 350.544
4668 | 2023-07-14 12:00 | -63.2306 | 65.03 | 20 | 10 | 0 | 20 | 35.9872
4669 | 2023-07-14 13:00 | 83.6408 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 74.3354
4670 | 2023-07-14 14:00 | 75.4942 | 65.03 | 20 | 10 | 0 | 20 | 2810.4848
4671 | 2023-07-14 15:00 | 85.7666 | 65.03 | 10 | 0 | 0 | 20 | 1507.9661
4672 | 2023-07-14 16:00 | 93.4559 | 65.03 | 10 | 0 | 0 | 20 | 1584.8592
4673 | 2023-07-14 17:00 | 105.0609 | 66.4 | 10 | 0 | 0 | 20 | 1714.6091
4674 | 2023-07-14 18:00 | 106.0521 | 66.4 | 0 | 0 | 10 | 10 | 0
4675 | 2023-07-14 19:00 | 116.0552 | 65.03 | 0 | 0 | 10 | 0 | 0
4676 | 2023-07-14 20:00 | 86.9344 | 65.03 | 10 | 0 | 0 | 0 | 1519.6441
4677 | 2023-07-14 21:00 | 90.6692 | 65.03 | 10 | 0 | 0 | 0 | 1556.9917
4678 | 2023-07-14 22:00 | 77.7576 | 65.03 | 10 | 0 | 0 | 0 | 1427.8762
4679 | 2023-07-14 23:00 | 71.8963 | 53.53 | 20 | 10 | 0 | 9.5 | 2508.5251
4680 | 2023-07-15 00:00 | 86.4716 | 53.53 | 0.5 | 0 | 9.5 | 0 | 70.0008
4681 | 2023-07-15 01:00 | 71.6666 | 53.53 | 10 | 0 | 0 | 0 | 1251.9664
4682 | 2023-07-15 02:00 | 46.635 | 53.53 | 10 | 0 | 0 | 0 | 1001.6505
4683 | 2023-07-15 03:00 | 46.6465 | 53.53 | 10 | 0 | 0 | 0 | 1001.7646
4684 | 2023-07-15 04:00 | 46.4746 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1105.3138
4685 | 2023-07-15 05:00 | 46.1085 | 53.53 | 20 | 10 | 0 | 10.5 | 1992.7704
4686 | 2023-07-15 06:00 | 42.9105 | 53.53 | 20 | 10 | 0 | 20 | 1928.8104
4687 | 2023-07-15 07:00 | 61.837 | 53.53 | 10 | 0 | 0 | 20 | 1153.67
4688 | 2023-07-15 08:00 | 79.4777 | 53.53 | 10 | 0 | 0 | 20 | 1330.0773
4689 | 2023-07-15 09:00 | 76.8244 | 53.53 | 10 | 0 | 0 | 20 | 1303.5442
4690 | 2023-07-15 10:00 | 90.7473 | 53.53 | 0 | 0 | 10 | 10 | 0
4691 | 2023-07-15 11:00 | 83.1959 | 53.53 | 10 | 0 | 0 | 10 | 1367.2591
4692 | 2023-07-15 12:00 | 82.9695 | 53.53 | 10 | 0 | 0 | 10 | 1364.9952
4693 | 2023-07-15 13:00 | 75.9025 | 53.53 | 20 | 10 | 0 | 19.5 | 2588.6491
4694 | 2023-07-15 14:00 | 80.0069 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1405.6513
4695 | 2023-07-15 15:00 | 83.7579 | 53.53 | 10 | 0 | 0 | 20 | 1372.8787
4696 | 2023-07-15 16:00 | 86.8905 | 53.53 | 10 | 0 | 0 | 20 | 1404.2047
4697 | 2023-07-15 17:00 | 95.2039 | 53.53 | 10 | 0 | 0 | 20 | 1487.3394
4698 | 2023-07-15 18:00 | 105.4554 | 53.53 | 0 | 0 | 10 | 10 | 0
4699 | 2023-07-15 19:00 | 95.9583 | 53.53 | 0 | 0 | 10 | 0 | 0
4700 | 2023-07-15 20:00 | 82.6114 | 53.53 | 10 | 0 | 0 | 0 | 1361.4141
4701 | 2023-07-15 21:00 | 72.4816 | 53.53 | 10 | 0 | 0 | 0 | 1260.1161
4702 | 2023-07-15 22:00 | 65.4121 | 53.53 | 20 | 10 | 0 | 9.5 | 2378.8419
4703 | 2023-07-15 23:00 | 72.9942 | 53.53 | 10 | 0 | 0 | 9.5 | 1265.2424
4704 | 2023-07-16 00:00 | 76.9755 | 53.53 | 0.5 | 0 | 9.5 | 0 | 65.2527
4705 | 2023-07-16 01:00 | 75.6082 | 53.53 | 10 | 0 | 0 | 0 | 1291.382
4706 | 2023-07-16 02:00 | 54.274 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1191.5175
4707 | 2023-07-16 03:00 | 48.416 | 53.53 | 20 | 10 | 0 | 10.5 | 2038.9193
4708 | 2023-07-16 04:00 | 45.5242 | 53.53 | 20 | 10 | 0 | 20 | 1981.0848
4709 | 2023-07-16 05:00 | 55.3984 | 53.53 | 10 | 0 | 0 | 20 | 1089.2843
4710 | 2023-07-16 06:00 | 54.3103 | 53.53 | 10 | 0 | 0 | 20 | 1078.4026
4711 | 2023-07-16 07:00 | 67.0265 | 53.53 | 10 | 0 | 0 | 20 | 1205.5645
4712 | 2023-07-16 08:00 | 90.771 | 53.53 | 0 | 0 | 10 | 10 | 0
4713 | 2023-07-16 09:00 | 75.0811 | 53.53 | 20 | 10 | 0 | 19.5 | 2572.2229
4714 | 2023-07-16 10:00 | 76.8835 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1372.7741
4715 | 2023-07-16 11:00 | 96.7441 | 53.53 | 0 | 0 | 10 | 10 | 0
4716 | 2023-07-16 12:00 | 88.3402 | 53.53 | 0 | 0 | 10 | 0 | 0
4717 | 2023-07-16 13:00 | 78.3524 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1457.6476
4718 | 2023-07-16 14:00 | 83.1493 | 53.53 | 10 | 0 | 0 | 1 | 1366.793
4719 | 2023-07-16 15:00 | 82.0866 | 53.53 | 10 | 0 | 0 | 1 | 1356.1663
4720 | 2023-07-16 16:00 | -16.2679 | 53.53 | 20 | 10 | 0 | 10.5 | 745.2427
4721 | 2023-07-16 17:00 | -66.2431 | 53.53 | 20 | 10 | 0 | 20 | -254.2615
4722 | 2023-07-16 18:00 | 95.5199 | 53.53 | 0 | 0 | 10 | 10 | 0
4723 | 2023-07-16 19:00 | 93.3618 | 53.53 | 0 | 0 | 10 | 0 | 0
4724 | 2023-07-16 20:00 | 77.822 | 53.53 | 20 | 10 | 0 | 9.5 | 2627.0399
4725 | 2023-07-16 21:00 | 85.9814 | 53.53 | 0.5 | 0 | 9.5 | 0 | 69.7557
4726 | 2023-07-16 22:00 | 73.5994 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1338.2047
4727 | 2023-07-16 23:00 | 64.1012 | 53.53 | 20 | 10 | 0 | 10 | 2352.6236
4728 | 2023-07-17 00:00 | 81.4574 | 53.53 | 0 | 0 | 10 | 0 | 0
4729 | 2023-07-17 01:00 | 76.5648 | 53.53 | 10 | 0 | 0 | 0 | 1300.9482
4730 | 2023-07-17 02:00 | 57.7548 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1288.5609
4731 | 2023-07-17 03:00 | 56.803 | 53.53 | 20 | 10 | 0 | 11 | 2206.6608
4732 | 2023-07-17 04:00 | 82.879 | 53.53 | 0 | 0 | 10 | 1 | 0
4733 | 2023-07-17 05:00 | 46.6628 | 53.53 | 20 | 10 | 0 | 10.5 | 2003.8553
4734 | 2023-07-17 06:00 | 56.1491 | 53.53 | 20 | 10 | 0 | 20 | 2193.5811
4735 | 2023-07-17 07:00 | 78.8707 | 53.53 | 10 | 0 | 0 | 20 | 1324.0065
4736 | 2023-07-17 08:00 | 83.6756 | 65.03 | 10 | 0 | 0 | 20 | 1487.0557
4737 | 2023-07-17 09:00 | 96.6457 | 65.03 | 0 | 0 | 10 | 10 | 0
4738 | 2023-07-17 10:00 | 95.8062 | 65.03 | 1 | 0 | 9 | 1 | 160.8362
4739 | 2023-07-17 11:00 | 88.5427 | 65.03 | 10 | 0 | 0 | 1 | 1535.727
4740 | 2023-07-17 12:00 | 86.9485 | 65.03 | 20 | 10 | 0 | 10.5 | 3039.5698
4741 | 2023-07-17 13:00 | 88.0726 | 65.03 | 10 | 0 | 0 | 10.5 | 1531.0257
4742 | 2023-07-17 14:00 | 88.1246 | 65.03 | 10 | 0 | 0 | 10.5 | 1531.5463
4743 | 2023-07-17 15:00 | 88.3174 | 65.03 | 10 | 0 | 0 | 10.5 | 1533.4736
4744 | 2023-07-17 16:00 | 87.5273 | 65.03 | 20 | 10 | 0 | 20 | 3051.1467
4745 | 2023-07-17 17:00 | 105.8652 | 66.4 | 0 | 0 | 10 | 10 | 0
4746 | 2023-07-17 18:00 | 110.2366 | 66.4 | 0 | 0 | 10 | 0 | 0
4747 | 2023-07-17 19:00 | 96.1826 | 65.03 | 10 | 0 | 0 | 0 | 1612.1259
4748 | 2023-07-17 20:00 | 77.1394 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1496.5199
4749 | 2023-07-17 21:00 | 73.6938 | 65.03 | 20 | 10 | 0 | 10 | 2774.4753
4750 | 2023-07-17 22:00 | 91.3189 | 65.03 | 0 | 0 | 10 | 0 | 0
4751 | 2023-07-17 23:00 | 80.848 | 53.53 | 10 | 0 | 0 | 0 | 1343.7802
4752 | 2023-07-18 00:00 | 82.9901 | 53.53 | 10 | 0 | 0 | 0 | 1365.201
4753 | 2023-07-18 01:00 | 70.1798 | 53.53 | 10 | 0 | 0 | 0 | 1237.0975
4754 | 2023-07-18 02:00 | 76.6052 | 53.53 | 10 | 0 | 0 | 0 | 1301.352
4755 | 2023-07-18 03:00 | 54.7247 | 53.53 | 20 | 10 | 0 | 9.5 | 2165.0938
4756 | 2023-07-18 04:00 | 60.1922 | 53.53 | 20 | 10 | 0 | 19 | 2274.4444
4757 | 2023-07-18 05:00 | 66.2023 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 179.5985
4758 | 2023-07-18 06:00 | -51.7776 | 53.53 | 20 | 10 | 0 | 20 | 35.0474
4759 | 2023-07-18 07:00 | 75.119 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 64.3245
4760 | 2023-07-18 08:00 | -19.617 | 65.03 | 20 | 10 | 0 | 20 | 908.2603
4761 | 2023-07-18 09:00 | 122.8146 | 65.03 | 0 | 0 | 10 | 10 | 0
4762 | 2023-07-18 10:00 | 91.2619 | 65.03 | 20 | 10 | 0 | 19.5 | 3125.8379
4763 | 2023-07-18 11:00 | 104.3773 | 65.03 | 0 | 0 | 10 | 9.5 | 0
4764 | 2023-07-18 12:00 | 99.7926 | 65.03 | 1.5 | 0 | 8.5 | 1 | 247.2339
4765 | 2023-07-18 13:00 | 91.8165 | 65.03 | 10 | 0 | 0 | 1 | 1568.4651
4766 | 2023-07-18 14:00 | 82.4789 | 65.03 | 20 | 10 | 0 | 10.5 | 2950.1778
4767 | 2023-07-18 15:00 | 98.2552 | 65.03 | 10 | 0 | 0 | 10.5 | 1632.8517
4768 | 2023-07-18 16:00 | 79.848 | 65.03 | 20 | 10 | 0 | 20 | 2897.561
4769 | 2023-07-18 17:00 | 119.3108 | 66.4 | 0 | 0 | 10 | 10 | 0
4770 | 2023-07-18 18:00 | 105.4443 | 66.4 | 0 | 0 | 10 | 0 | 0
4771 | 2023-07-18 19:00 | 90.1871 | 65.03 | 10 | 0 | 0 | 0 | 1552.1708
4772 | 2023-07-18 20:00 | 81.4706 | 65.03 | 20 | 10 | 0 | 9.5 | 2930.0123
4773 | 2023-07-18 21:00 | 89.3171 | 65.03 | 0.5 | 0 | 9.5 | 0 | 77.1735
4774 | 2023-07-18 22:00 | 82.1824 | 65.03 | 10 | 0 | 0 | 0 | 1472.1236
4775 | 2023-07-18 23:00 | 84.8794 | 53.53 | 10 | 0 | 0 | 0 | 1384.0941
4776 | 2023-07-19 00:00 | 73.2711 | 53.53 | 10 | 0 | 0 | 0 | 1268.0108
4777 | 2023-07-19 01:00 | 70.7944 | 53.53 | 10 | 0 | 0 | 0 | 1243.2438
4778 | 2023-07-19 02:00 | 58.3682 | 53.53 | 20 | 10 | 0 | 9.5 | 2237.9633
4779 | 2023-07-19 03:00 | 59.1362 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1245.2577
4780 | 2023-07-19 04:00 | 56.4173 | 53.53 | 20 | 10 | 0 | 20 | 2198.9466
4781 | 2023-07-19 05:00 | 70.0261 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 61.7781
4782 | 2023-07-19 06:00 | 53.27 | 53.53 | 20 | 10 | 0 | 20 | 2136.0003
4783 | 2023-07-19 07:00 | 81.3609 | 53.53 | 10 | 0 | 0 | 20 | 1348.9092
4784 | 2023-07-19 08:00 | 89.4133 | 65.03 | 0 | 0 | 10 | 10 | 0
4785 | 2023-07-19 09:00 | 79.5701 | 65.03 | 20 | 10 | 0 | 19.5 | 2892.0015
4786 | 2023-07-19 10:00 | 80.7284 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1534.2986
4787 | 2023-07-19 11:00 | 88.9878 | 65.03 | 10 | 0 | 0 | 20 | 1540.178
4788 | 2023-07-19 12:00 | 109.1951 | 65.03 | 0 | 0 | 10 | 10 | 0
4789 | 2023-07-19 13:00 | 93.6432 | 65.03 | 1 | 0 | 9 | 1 | 158.6732
4790 | 2023-07-19 14:00 | 78.7957 | 65.03 | 20 | 10 | 0 | 10.5 | 2876.5137
4791 | 2023-07-19 15:00 | 73.7312 | 65.03 | 20 | 10 | 0 | 20 | 2775.2232
4792 | 2023-07-19 16:00 | 95.0476 | 65.03 | 10 | 0 | 0 | 20 | 1600.7761
4793 | 2023-07-19 17:00 | 103.187 | 66.4 | 0 | 0 | 10 | 10 | 0
4794 | 2023-07-19 18:00 | 114.1057 | 66.4 | 0 | 0 | 10 | 0 | 0
4795 | 2023-07-19 19:00 | 98.0935 | 65.03 | 10 | 0 | 0 | 0 | 1631.2351
4796 | 2023-07-19 20:00 | 86.6678 | 65.03 | 10 | 0 | 0 | 0 | 1516.9784
4797 | 2023-07-19 21:00 | 91.1228 | 65.03 | 10 | 0 | 0 | 0 | 1561.5283
4798 | 2023-07-19 22:00 | 80.7578 | 65.03 | 10 | 0 | 0 | 0 | 1457.8783
4799 | 2023-07-19 23:00 | 75.8985 | 53.53 | 20 | 10 | 0 | 9.5 | 2588.5695
4800 | 2023-07-20 00:00 | 79.0885 | 53.53 | 10 | 0 | 0 | 9.5 | 1326.185
4801 | 2023-07-20 01:00 | 83.3184 | 53.53 | 0.5 | 0 | 9.5 | 0 | 68.4242
4802 | 2023-07-20 02:00 | 58.791 | 53.53 | 20 | 10 | 0 | 9.5 | 2246.4206
4803 | 2023-07-20 03:00 | 67.3825 | 53.53 | 1.5 | 0 | 8.5 | 1 | 181.3688
4804 | 2023-07-20 04:00 | 55.6631 | 53.53 | 20 | 10 | 0 | 10.5 | 2183.8627
4805 | 2023-07-20 05:00 | 50.6812 | 53.53 | 20 | 10 | 0 | 20 | 2084.223
4806 | 2023-07-20 06:00 | 79.1377 | 53.53 | 10 | 0 | 0 | 20 | 1326.6771
4807 | 2023-07-20 07:00 | 74.7511 | 53.53 | 10 | 0 | 0 | 20 | 1282.8105
4808 | 2023-07-20 08:00 | 84.9787 | 65.03 | 10 | 0 | 0 | 20 | 1500.087
4809 | 2023-07-20 09:00 | 88.4096 | 65.03 | 10 | 0 | 0 | 20 | 1534.3962
4810 | 2023-07-20 10:00 | 89.4073 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 77.2186
4811 | 2023-07-20 11:00 | 86.1601 | 65.03 | 10 | 0 | 0 | 10.5 | 1511.9007
4812 | 2023-07-20 12:00 | 88.7679 | 65.03 | 10 | 0 | 0 | 10.5 | 1537.9789
4813 | 2023-07-20 13:00 | -69.4321 | 65.03 | 20 | 10 | 0 | 20 | -88.0417
4814 | 2023-07-20 14:00 | 90.2444 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 77.6372
4815 | 2023-07-20 15:00 | 76.2233 | 65.03 | 20 | 10 | 0 | 20 | 2825.0661
4816 | 2023-07-20 16:00 | 107.8521 | 65.03 | 0 | 0 | 10 | 10 | 0
4817 | 2023-07-20 17:00 | 102.8177 | 66.4 | 10 | 0 | 0 | 10 | 1692.1769
4818 | 2023-07-20 18:00 | 108.6553 | 66.4 | 0 | 0 | 10 | 0 | 0
4819 | 2023-07-20 19:00 | 95.4327 | 65.03 | 10 | 0 | 0 | 0 | 1604.6275
4820 | 2023-07-20 20:00 | 80.604 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1532.9897
4821 | 2023-07-20 21:00 | 79.3319 | 65.03 | 20 | 10 | 0 | 10 | 2887.2383
4822 | 2023-07-20 22:00 | 97.7516 | 65.03 | 0 | 0 | 10 | 0 | 0
4823 | 2023-07-20 23:00 | 74.8691 | 53.53 | 20 | 10 | 0 | 9.5 | 2567.9824
4824 | 2023-07-21 00:00 | 85.2824 | 53.53 | 0.5 | 0 | 9.5 | 0 | 69.4062
4825 | 2023-07-21 01:00 | 74.4666 | 53.53 | 10 | 0 | 0 | 0 | 1279.9658
4826 | 2023-07-21 02:00 | 55.724 | 53.53 | 20 | 10 | 0 | 9.5 | 2185.081
4827 | 2023-07-21 03:00 | 57.1229 | 53.53 | 11.5789 | 1.5789 | 0 | 11 | 1281.2438
4828 | 2023-07-21 04:00 | 70.6443 | 53.53 | 0 | 0 | 10 | 1 | 0
4829 | 2023-07-21 05:00 | 48.0795 | 53.53 | 20 | 10 | 0 | 10.5 | 2032.1909
4830 | 2023-07-21 06:00 | 50.7454 | 53.53 | 20 | 10 | 0 | 20 | 2085.5075
4831 | 2023-07-21 07:00 | 67.8372 | 53.53 | 10 | 0 | 0 | 20 | 1213.6722
4832 | 2023-07-21 08:00 | 81.9389 | 65.03 | 10 | 0 | 0 | 20 | 1469.6891
4833 | 2023-07-21 09:00 | 83.4957 | 65.03 | 10 | 0 | 0 | 20 | 1485.2568
4834 | 2023-07-21 10:00 | 79.3008 | 65.03 | 10 | 0 | 0 | 20 | 1443.3083
4835 | 2023-07-21 11:00 | 83.9564 | 65.03 | 10 | 0 | 0 | 20 | 1489.8637
4836 | 2023-07-21 12:00 | 77.5582 | 65.03 | 10 | 0 | 0 | 20 | 1425.8816
4837 | 2023-07-21 13:00 | 82.3191 | 65.03 | 10 | 0 | 0 | 20 | 1473.4908
4838 | 2023-07-21 14:00 | 99.7361 | 65.03 | 0 | 0 | 10 | 10 | 0
4839 | 2023-07-21 15:00 | 92.1161 | 65.03 | 10 | 0 | 0 | 10 | 1571.4609
4840 | 2023-07-21 16:00 | 90.3446 | 65.03 | 10 | 0 | 0 | 10 | 1553.746
4841 | 2023-07-21 17:00 | 97.4033 | 66.4 | 0 | 0 | 10 | 0 | 0
4842 | 2023-07-21 18:00 | 94.6674 | 66.4 | 10 | 0 | 0 | 0 | 1610.6737
4843 | 2023-07-21 19:00 | 96.6615 | 65.03 | 10 | 0 | 0 | 0 | 1616.9151
4844 | 2023-07-21 20:00 | 83.5763 | 65.03 | 20 | 10 | 0 | 9.5 | 2972.1265
4845 | 2023-07-21 21:00 | 91.3363 | 65.03 | 10 | 0 | 0 | 9.5 | 1563.6625
4846 | 2023-07-21 22:00 | 91.6707 | 65.03 | 0.5 | 0 | 9.5 | 0 | 78.3503
4847 | 2023-07-21 23:00 | 84.1049 | 53.53 | 10 | 0 | 0 | 0 | 1376.3488
4848 | 2023-07-22 00:00 | 65.9359 | 53.53 | 10 | 0 | 0 | 0 | 1194.6587
4849 | 2023-07-22 01:00 | 71.0831 | 53.53 | 10 | 0 | 0 | 0 | 1246.1311
4850 | 2023-07-22 02:00 | 48.6008 | 53.53 | 20 | 10 | 0 | 9.5 | 2042.6152
4851 | 2023-07-22 03:00 | 49.434 | 53.53 | 11.5789 | 1.5789 | 0 | 11 | 1192.2149
4852 | 2023-07-22 04:00 | 71.9615 | 53.53 | 0 | 0 | 10 | 1 | 0
4853 | 2023-07-22 05:00 | 40.634 | 53.53 | 20 | 10 | 0 | 10.5 | 1883.2809
4854 | 2023-07-22 06:00 | 49.1988 | 53.53 | 20 | 10 | 0 | 20 | 2054.5752
4855 | 2023-07-22 07:00 | 81.8581 | 53.53 | 0 | 0 | 10 | 10 | 0
4856 | 2023-07-22 08:00 | 72.003 | 53.53 | 10 | 0 | 0 | 10 | 1255.3296
4857 | 2023-07-22 09:00 | 76.5078 | 53.53 | 10 | 0 | 0 | 10 | 1300.3779
4858 | 2023-07-22 10:00 | 77.2294 | 53.53 | 10 | 0 | 0 | 10 | 1307.5937
4859 | 2023-07-22 11:00 | -49.9208 | 53.53 | 20 | 10 | 0 | 19.5 | 72.1847
4860 | 2023-07-22 12:00 | 71.3867 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1314.9123
4861 | 2023-07-22 13:00 | 85.7864 | 53.53 | 10 | 0 | 0 | 20 | 1393.1644
4862 | 2023-07-22 14:00 | 86.4299 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 69.9799
4863 | 2023-07-22 15:00 | 85.0172 | 53.53 | 10 | 0 | 0 | 10.5 | 1385.4723
4864 | 2023-07-22 16:00 | 75.1532 | 53.53 | 20 | 10 | 0 | 20 | 2573.6634
4865 | 2023-07-22 17:00 | 96.5556 | 53.53 | 0 | 0 | 10 | 10 | 0
4866 | 2023-07-22 18:00 | 89.986 | 53.53 | 10 | 0 | 0 | 10 | 1435.16
4867 | 2023-07-22 19:00 | 93.5242 | 53.53 | 10 | 0 | 0 | 10 | 1470.5424
4868 | 2023-07-22 20:00 | 98.5976 | 53.53 | 0 | 0 | 10 | 0 | 0
4869 | 2023-07-22 21:00 | 76.6264 | 53.53 | 10 | 0 | 0 | 0 | 1301.5642
4870 | 2023-07-22 22:00 | 68.4056 | 53.53 | 10 | 0 | 0 | 0 | 1219.356
4871 | 2023-07-22 23:00 | 72.2881 | 53.53 | 10 | 0 | 0 | 0 | 1258.1808
4872 | 2023-07-23 00:00 | 62.5637 | 53.53 | 10 | 0 | 0 | 0 | 1160.9374
4873 | 2023-07-23 01:00 | 63.3454 | 53.53 | 10 | 0 | 0 | 0 | 1168.7539
4874 | 2023-07-23 02:00 | 44.1917 | 53.53 | 20 | 10 | 0 | 9.5 | 1954.4336
4875 | 2023-07-23 03:00 | 47.7785 | 53.53 | 20 | 10 | 0 | 19 | 2026.1705
4876 | 2023-07-23 04:00 | 59.0126 | 53.53 | 10 | 0 | 0 | 19 | 1125.4265
4877 | 2023-07-23 05:00 | 55.6354 | 53.53 | 10 | 0 | 0 | 19 | 1091.654
4878 | 2023-07-23 06:00 | 55.1452 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1201.1473
4879 | 2023-07-23 07:00 | 63.8772 | 53.53 | 10 | 0 | 0 | 20 | 1174.072
4880 | 2023-07-23 08:00 | 77.151 | 53.53 | 10 | 0 | 0 | 20 | 1306.8095
4881 | 2023-07-23 09:00 | 83.0239 | 53.53 | 10 | 0 | 0 | 20 | 1365.5386
4882 | 2023-07-23 10:00 | 76.6034 | 53.53 | 10 | 0 | 0 | 20 | 1301.334
4883 | 2023-07-23 11:00 | 78.8954 | 53.53 | 10 | 0 | 0 | 20 | 1324.2535
4884 | 2023-07-23 12:00 | 84.4376 | 53.53 | 10 | 0 | 0 | 20 | 1379.6764
4885 | 2023-07-23 13:00 | 78.4147 | 53.53 | 10 | 0 | 0 | 20 | 1319.4471
4886 | 2023-07-23 14:00 | 82.6526 | 53.53 | 10 | 0 | 0 | 20 | 1361.8257
4887 | 2023-07-23 15:00 | 96.2121 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 74.8711
4888 | 2023-07-23 16:00 | 79.642 | 53.53 | 20 | 10 | 0 | 20 | 2663.4406
4889 | 2023-07-23 17:00 | 106.5101 | 53.53 | 0 | 0 | 10 | 10 | 0
4890 | 2023-07-23 18:00 | 100.4661 | 53.53 | 0 | 0 | 10 | 0 | 0
4891 | 2023-07-23 19:00 | 86.9964 | 53.53 | 10 | 0 | 0 | 0 | 1405.2644
4892 | 2023-07-23 20:00 | 68.8599 | 53.53 | 20 | 10 | 0 | 9.5 | 2447.7976
4893 | 2023-07-23 21:00 | 70.3668 | 53.53 | 10 | 0 | 0 | 9.5 | 1238.9679
4894 | 2023-07-23 22:00 | 70.2431 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1368.0189
4895 | 2023-07-23 23:00 | 70.2302 | 53.53 | 20 | 10 | 0 | 20 | 2475.2044
4896 | 2023-07-24 00:00 | 83.9605 | 53.53 | 0 | 0 | 10 | 10 | 0
4897 | 2023-07-24 01:00 | 90.3294 | 53.53 | 0 | 0 | 10 | 0 | 0
4898 | 2023-07-24 02:00 | 61.3198 | 53.53 | 10 | 0 | 0 | 0 | 1148.4983
4899 | 2023-07-24 03:00 | 55.7695 | 53.53 | 20 | 10 | 0 | 9.5 | 2185.9907
4900 | 2023-07-24 04:00 | 47.2842 | 53.53 | 20 | 10 | 0 | 19 | 2016.2845
4901 | 2023-07-24 05:00 | 59.4334 | 53.53 | 10 | 0 | 0 | 19 | 1129.6337
4902 | 2023-07-24 06:00 | 59.0923 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1244.7731
4903 | 2023-07-24 07:00 | 80.3086 | 53.53 | 10 | 0 | 0 | 20 | 1338.3862
4904 | 2023-07-24 08:00 | 110.9265 | 65.03 | 0 | 0 | 10 | 10 | 0
4905 | 2023-07-24 09:00 | 100.1706 | 65.03 | 0 | 0 | 10 | 0 | 0
4906 | 2023-07-24 10:00 | 95.5374 | 65.03 | 10 | 0 | 0 | 0 | 1605.6742
4907 | 2023-07-24 11:00 | 82.6307 | 65.03 | 20 | 10 | 0 | 9.5 | 2953.2134
4908 | 2023-07-24 12:00 | 85.3323 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1661.8989
4909 | 2023-07-24 13:00 | 88.197 | 65.03 | 10 | 0 | 0 | 10.5 | 1532.27
4910 | 2023-07-24 14:00 | 83.7096 | 65.03 | 20 | 10 | 0 | 20 | 2974.7926
4911 | 2023-07-24 15:00 | 92.9482 | 65.03 | 10 | 0 | 0 | 20 | 1579.7821
4912 | 2023-07-24 16:00 | 91.7237 | 65.03 | 10 | 0 | 0 | 20 | 1567.5368
4913 | 2023-07-24 17:00 | 96.9346 | 66.4 | 10 | 0 | 0 | 20 | 1633.3455
4914 | 2023-07-24 18:00 | 114.6973 | 66.4 | 0 | 0 | 10 | 10 | 0
4915 | 2023-07-24 19:00 | 104.6775 | 65.03 | 0 | 0 | 10 | 0 | 0
4916 | 2023-07-24 20:00 | 73.7803 | 65.03 | 20 | 10 | 0 | 9.5 | 2776.2067
4917 | 2023-07-24 21:00 | 83.5162 | 65.03 | 10 | 0 | 0 | 9.5 | 1485.4619
4918 | 2023-07-24 22:00 | 86.0989 | 65.03 | 0.5 | 0 | 9.5 | 0 | 75.5644
4919 | 2023-07-24 23:00 | 87.3704 | 53.53 | 10 | 0 | 0 | 0 | 1409.0045
4920 | 2023-07-25 00:00 | 76.4911 | 53.53 | 20 | 10 | 0 | 9.5 | 2600.4229
4921 | 2023-07-25 01:00 | 85.947 | 53.53 | 0.5 | 0 | 9.5 | 0 | 69.7385
4922 | 2023-07-25 02:00 | 60.342 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1258.5855
4923 | 2023-07-25 03:00 | 50.7485 | 53.53 | 20 | 10 | 0 | 10.5 | 2085.5691
4924 | 2023-07-25 04:00 | 50.2499 | 53.53 | 20 | 10 | 0 | 20 | 2075.5981
4925 | 2023-07-25 05:00 | 68.9087 | 53.53 | 10 | 0 | 0 | 20 | 1224.3866
4926 | 2023-07-25 06:00 | 69.6884 | 53.53 | 10 | 0 | 0 | 20 | 1232.184
4927 | 2023-07-25 07:00 | 81.4413 | 53.53 | 10 | 0 | 0 | 20 | 1349.7131
4928 | 2023-07-25 08:00 | 103.0556 | 65.03 | 0 | 0 | 10 | 10 | 0
4929 | 2023-07-25 09:00 | 98.2228 | 65.03 | 0.5 | 0 | 9.5 | 0.5 | 81.6264
4930 | 2023-07-25 10:00 | 94.5892 | 65.03 | 10 | 0 | 0 | 0.5 | 1596.1915
4931 | 2023-07-25 11:00 | 82.9181 | 65.03 | 20 | 10 | 0 | 10 | 2958.9628
4932 | 2023-07-25 12:00 | 105.925 | 65.03 | 0 | 0 | 10 | 0 | 0
4933 | 2023-07-25 13:00 | 93.2622 | 65.03 | 10 | 0 | 0 | 0 | 1582.9221
4934 | 2023-07-25 14:00 | 86.1657 | 65.03 | 20 | 10 | 0 | 9.5 | 3023.9143
4935 | 2023-07-25 15:00 | 84.3567 | 65.03 | 20 | 10 | 0 | 19 | 2987.7346
4936 | 2023-07-25 16:00 | 90.9003 | 65.03 | 10 | 0 | 0 | 19 | 1559.3031
4937 | 2023-07-25 17:00 | 94.0416 | 66.4 | 10 | 0 | 0 | 19 | 1604.416
4938 | 2023-07-25 18:00 | 109.7372 | 66.4 | 0 | 0 | 10 | 9 | 0
4939 | 2023-07-25 19:00 | 97.6785 | 65.03 | 1 | 0 | 9 | 0 | 162.7085
4940 | 2023-07-25 20:00 | 86.8383 | 65.03 | 10 | 0 | 0 | 0 | 1518.6828
4941 | 2023-07-25 21:00 | -7.7705 | 65.03 | 20 | 10 | 0 | 9.5 | 1145.1895
4942 | 2023-07-25 22:00 | 81.9918 | 65.03 | 0.5 | 0 | 9.5 | 0 | 73.5109
4943 | 2023-07-25 23:00 | -62.9181 | 53.53 | 20 | 10 | 0 | 9.5 | -187.7625
4944 | 2023-07-26 00:00 | 77.7179 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1381.5565
4945 | 2023-07-26 01:00 | 97.9644 | 53.53 | 0 | 0 | 10 | 0 | 0
4946 | 2023-07-26 02:00 | 71.7772 | 53.53 | 10 | 0 | 0 | 0 | 1253.0719
4947 | 2023-07-26 03:00 | 61.7034 | 53.53 | 20 | 10 | 0 | 9.5 | 2304.6682
4948 | 2023-07-26 04:00 | 58.7093 | 53.53 | 20 | 10 | 0 | 19 | 2244.7863
4949 | 2023-07-26 05:00 | 66.1038 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1322.268
4950 | 2023-07-26 06:00 | 68.9866 | 53.53 | 10 | 0 | 0 | 20 | 1225.1658
4951 | 2023-07-26 07:00 | 73.3889 | 53.53 | 10 | 0 | 0 | 20 | 1269.1887
4952 | 2023-07-26 08:00 | 88.3242 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 76.6771
4953 | 2023-07-26 09:00 | 78.3714 | 65.03 | 20 | 10 | 0 | 20 | 2868.0271
4954 | 2023-07-26 10:00 | 98.9144 | 65.03 | 0 | 0 | 10 | 10 | 0
4955 | 2023-07-26 11:00 | 110.3486 | 65.03 | 0 | 0 | 10 | 0 | 0
4956 | 2023-07-26 12:00 | 89.5062 | 65.03 | 10 | 0 | 0 | 0 | 1545.362
4957 | 2023-07-26 13:00 | 77.1136 | 65.03 | 20 | 10 | 0 | 9.5 | 2842.8715
4958 | 2023-07-26 14:00 | 93.9087 | 65.03 | 1.5 | 0 | 8.5 | 1 | 238.408
4959 | 2023-07-26 15:00 | 82.9594 | 65.03 | 20 | 10 | 0 | 10.5 | 2959.7879
4960 | 2023-07-26 16:00 | 84.387 | 65.03 | 20 | 10 | 0 | 20 | 2988.3391
4961 | 2023-07-26 17:00 | 109.0683 | 66.4 | 0 | 0 | 10 | 10 | 0
4962 | 2023-07-26 18:00 | 105.8823 | 66.4 | 0 | 0 | 10 | 0 | 0
4963 | 2023-07-26 19:00 | 100.4929 | 65.03 | 10 | 0 | 0 | 0 | 1655.229
4964 | 2023-07-26 20:00 | 79.4716 | 65.03 | 10 | 0 | 0 | 0 | 1445.0161
4965 | 2023-07-26 21:00 | 84.8601 | 65.03 | 10 | 0 | 0 | 0 | 1498.9012
4966 | 2023-07-26 22:00 | 81.0084 | 65.03 | 10 | 0 | 0 | 0 | 1460.3844
4967 | 2023-07-26 23:00 | 71.8217 | 53.53 | 20 | 10 | 0 | 9.5 | 2507.0332
4968 | 2023-07-27 00:00 | 76.5245 | 53.53 | 10 | 0 | 0 | 9.5 | 1300.5447
4969 | 2023-07-27 01:00 | 81.5795 | 53.53 | 0.5 | 0 | 9.5 | 0 | 67.5548
4970 | 2023-07-27 02:00 | 57.5976 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1286.7405
4971 | 2023-07-27 03:00 | 50.258 | 53.53 | 20 | 10 | 0 | 11 | 2075.7609
4972 | 2023-07-27 04:00 | 67.5342 | 53.53 | 0 | 0 | 10 | 1 | 0
4973 | 2023-07-27 05:00 | 44.891 | 53.53 | 20 | 10 | 0 | 10.5 | 1968.4203
4974 | 2023-07-27 06:00 | 55.765 | 53.53 | 20 | 10 | 0 | 20 | 2185.9007
4975 | 2023-07-27 07:00 | 74.6539 | 53.53 | 10 | 0 | 0 | 20 | 1281.8391
4976 | 2023-07-27 08:00 | 90.0347 | 65.03 | 10 | 0 | 0 | 20 | 1550.6472
4977 | 2023-07-27 09:00 | 93.4865 | 65.03 | 10 | 0 | 0 | 20 | 1585.1647
4978 | 2023-07-27 10:00 | 98.9529 | 65.03 | 0 | 0 | 10 | 10 | 0
4979 | 2023-07-27 11:00 | 84.0876 | 65.03 | 20 | 10 | 0 | 19.5 | 2982.3528
4980 | 2023-07-27 12:00 | 93.7085 | 65.03 | 1 | 0 | 9 | 10.5 | 158.7385
4981 | 2023-07-27 13:00 | 90.4109 | 65.03 | 10 | 0 | 0 | 10.5 | 1554.4094
4982 | 2023-07-27 14:00 | 78.8588 | 65.03 | 20 | 10 | 0 | 20 | 2877.7763
4983 | 2023-07-27 15:00 | 108.1121 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 86.5711
4984 | 2023-07-27 16:00 | 80.1345 | 65.03 | 20 | 10 | 0 | 20 | 2903.2901
4985 | 2023-07-27 17:00 | 107.2511 | 66.4 | 0 | 0 | 10 | 10 | 0
4986 | 2023-07-27 18:00 | 107.001 | 66.4 | 0 | 0 | 10 | 0 | 0
4987 | 2023-07-27 19:00 | 106.0535 | 65.03 | 10 | 0 | 0 | 0 | 1710.8346
4988 | 2023-07-27 20:00 | 80.451 | 65.03 | 20 | 10 | 0 | 9.5 | 2909.6208
4989 | 2023-07-27 21:00 | 90.9404 | 65.03 | 0.5 | 0 | 9.5 | 0 | 77.9852
4990 | 2023-07-27 22:00 | 74.5529 | 65.03 | 10 | 0 | 0 | 0 | 1395.8292
4991 | 2023-07-27 23:00 | 78.4094 | 53.53 | 10 | 0 | 0 | 0 | 1319.3943
4992 | 2023-07-28 00:00 | 75.0076 | 53.53 | 10 | 0 | 0 | 0 | 1285.376
4993 | 2023-07-28 01:00 | 74.3014 | 53.53 | 10 | 0 | 0 | 0 | 1278.314
4994 | 2023-07-28 02:00 | 62.3299 | 53.53 | 20 | 10 | 0 | 9.5 | 2317.1975
4995 | 2023-07-28 03:00 | 68.4384 | 53.53 | 1.5 | 0 | 8.5 | 1 | 182.9525
4996 | 2023-07-28 04:00 | 56.452 | 53.53 | 20 | 10 | 0 | 10.5 | 2199.6401
4997 | 2023-07-28 05:00 | 65.4959 | 53.53 | 10 | 0 | 0 | 10.5 | 1190.2587
4998 | 2023-07-28 06:00 | 59.2742 | 53.53 | 20 | 10 | 0 | 20 | 2256.0832
4999 | 2023-07-28 07:00 | 73.0244 | 53.53 | 10 | 0 | 0 | 20 | 1265.5445
5000 | 2023-07-28 08:00 | 87.0366 | 65.03 | 10 | 0 | 0 | 20 | 1520.6663
5001 | 2023-07-28 09:00 | 86.7501 | 65.03 | 10 | 0 | 0 | 20 | 1517.8011
5002 | 2023-07-28 10:00 | 84.1832 | 65.03 | 10 | 0 | 0 | 20 | 1492.1323
5003 | 2023-07-28 11:00 | 92.3276 | 65.03 | 0 | 0 | 10 | 10 | 0
5004 | 2023-07-28 12:00 | 90.7216 | 65.03 | 1 | 0 | 9 | 1 | 155.7516
5005 | 2023-07-28 13:00 | 79.4113 | 65.03 | 20 | 10 | 0 | 10.5 | 2888.8269
5006 | 2023-07-28 14:00 | 79.1306 | 65.03 | 20 | 10 | 0 | 20 | 2883.2121
5007 | 2023-07-28 15:00 | 92.2952 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 78.6626
5008 | 2023-07-28 16:00 | 83.474 | 65.03 | 20 | 10 | 0 | 20 | 2970.0805
5009 | 2023-07-28 17:00 | 106.2694 | 66.4 | 0 | 0 | 10 | 10 | 0
5010 | 2023-07-28 18:00 | 110.4982 | 66.4 | 0 | 0 | 10 | 0 | 0
5011 | 2023-07-28 19:00 | 95.9729 | 65.03 | 10 | 0 | 0 | 0 | 1610.0287
5012 | 2023-07-28 20:00 | 75.2677 | 65.03 | 20 | 10 | 0 | 9.5 | 2805.9544
5013 | 2023-07-28 21:00 | 100.2125 | 65.03 | 0.5 | 0 | 9.5 | 0 | 82.6212
5014 | 2023-07-28 22:00 | 86.6792 | 65.03 | 10 | 0 | 0 | 0 | 1517.0916
5015 | 2023-07-28 23:00 | 75.9437 | 53.53 | 10 | 0 | 0 | 0 | 1294.737
5016 | 2023-07-29 00:00 | 64.7895 | 53.53 | 10 | 0 | 0 | 0 | 1183.1946
5017 | 2023-07-29 01:00 | 67.3487 | 53.53 | 10 | 0 | 0 | 0 | 1208.7871
5018 | 2023-07-29 02:00 | 43.3896 | 53.53 | 20 | 10 | 0 | 9.5 | 1938.3923
5019 | 2023-07-29 03:00 | 58.4849 | 53.53 | 0.5 | 0 | 9.5 | 0 | 56.0074
5020 | 2023-07-29 04:00 | 45.7016 | 53.53 | 10 | 0 | 0 | 0 | 992.3164
5021 | 2023-07-29 05:00 | -63.9254 | 53.53 | 20 | 10 | 0 | 9.5 | -207.9086
5022 | 2023-07-29 06:00 | -24.7271 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 318.3478
5023 | 2023-07-29 07:00 | -26.648 | 53.53 | 20 | 10 | 0 | 20 | 537.6408
5024 | 2023-07-29 08:00 | 77.897 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 65.7135
5025 | 2023-07-29 09:00 | 67.2757 | 53.53 | 20 | 10 | 0 | 20 | 2416.1134
5026 | 2023-07-29 10:00 | 80.0088 | 53.53 | 10 | 0 | 0 | 20 | 1335.3875
5027 | 2023-07-29 11:00 | 79.6544 | 53.53 | 10 | 0 | 0 | 20 | 1331.8442
5028 | 2023-07-29 12:00 | 87.9163 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 70.7232
5029 | 2023-07-29 13:00 | 70.0946 | 53.53 | 20 | 10 | 0 | 20 | 2472.493
5030 | 2023-07-29 14:00 | 91.3239 | 53.53 | 10 | 0 | 0 | 20 | 1448.5394
5031 | 2023-07-29 15:00 | 87.8765 | 53.53 | 10 | 0 | 0 | 20 | 1414.0654
5032 | 2023-07-29 16:00 | 92.2954 | 53.53 | 10 | 0 | 0 | 20 | 1458.254
5033 | 2023-07-29 17:00 | 95.506 | 53.53 | 0 | 0 | 10 | 10 | 0
5034 | 2023-07-29 18:00 | 104.7858 | 53.53 | 0 | 0 | 10 | 0 | 0
5035 | 2023-07-29 19:00 | 86.9771 | 53.53 | 10 | 0 | 0 | 0 | 1405.0712
5036 | 2023-07-29 20:00 | 81.8612 | 53.53 | 10 | 0 | 0 | 0 | 1353.9122
5037 | 2023-07-29 21:00 | 70.7349 | 53.53 | 10 | 0 | 0 | 0 | 1242.6487
5038 | 2023-07-29 22:00 | 66.1312 | 53.53 | 10 | 0 | 0 | 0 | 1196.6117
5039 | 2023-07-29 23:00 | 63.7417 | 53.53 | 20 | 10 | 0 | 9.5 | 2345.4341
5040 | 2023-07-30 00:00 | 70.9398 | 53.53 | 0.5 | 0 | 9.5 | 0 | 62.2349
5041 | 2023-07-30 01:00 | 65.4212 | 53.53 | 10 | 0 | 0 | 0 | 1189.5117
5042 | 2023-07-30 02:00 | 53.8841 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1187.2087
5043 | 2023-07-30 03:00 | 40.4311 | 53.53 | 20 | 10 | 0 | 10.5 | 1879.2211
5044 | 2023-07-30 04:00 | 39.1053 | 53.53 | 20 | 10 | 0 | 20 | 1852.706
5045 | 2023-07-30 05:00 | 63.6335 | 53.53 | 10 | 0 | 0 | 20 | 1171.6346
5046 | 2023-07-30 06:00 | 58.6848 | 53.53 | 10 | 0 | 0 | 20 | 1122.1477
5047 | 2023-07-30 07:00 | 64.1469 | 53.53 | 10 | 0 | 0 | 20 | 1176.7688
5048 | 2023-07-30 08:00 | 80.8758 | 53.53 | 10 | 0 | 0 | 20 | 1344.0582
5049 | 2023-07-30 09:00 | 89.8428 | 53.53 | 0 | 0 | 10 | 10 | 0
5050 | 2023-07-30 10:00 | 84.2486 | 53.53 | 10 | 0 | 0 | 10 | 1377.7856
5051 | 2023-07-30 11:00 | 82.0351 | 53.53 | 10 | 0 | 0 | 10 | 1355.6507
5052 | 2023-07-30 12:00 | 90.622 | 53.53 | 0 | 0 | 10 | 0 | 0
5053 | 2023-07-30 13:00 | 75.9771 | 53.53 | 20 | 10 | 0 | 9.5 | 2590.1411
5054 | 2023-07-30 14:00 | 81.1332 | 53.53 | 10 | 0 | 0 | 9.5 | 1346.6324
5055 | 2023-07-30 15:00 | 80.7648 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1484.3109
5056 | 2023-07-30 16:00 | 78.9341 | 53.53 | 20 | 10 | 0 | 20 | 2649.2811
5057 | 2023-07-30 17:00 | 93.1392 | 53.53 | 10 | 0 | 0 | 20 | 1466.6923
5058 | 2023-07-30 18:00 | 96.4508 | 53.53 | 0 | 0 | 10 | 10 | 0
5059 | 2023-07-30 19:00 | 96.1577 | 53.53 | 0 | 0 | 10 | 0 | 0
5060 | 2023-07-30 20:00 | 69.1516 | 53.53 | 20 | 10 | 0 | 9.5 | 2453.6327
5061 | 2023-07-30 21:00 | 82.6967 | 53.53 | 0.5 | 0 | 9.5 | 0 | 68.1133
5062 | 2023-07-30 22:00 | 69.5504 | 53.53 | 20 | 10 | 0 | 9.5 | 2461.6087
5063 | 2023-07-30 23:00 | 69.314 | 53.53 | 20 | 10 | 0 | 19 | 2456.8797
5064 | 2023-07-31 00:00 | 76.779 | 53.53 | 1 | 0 | 9 | 10 | 130.309
5065 | 2023-07-31 01:00 | 81.7337 | 53.53 | 0 | 0 | 10 | 0 | 0
5066 | 2023-07-31 02:00 | 47.137 | 53.53 | 20 | 10 | 0 | 9.5 | 2013.3402
5067 | 2023-07-31 03:00 | 66.5582 | 53.53 | 10 | 0 | 0 | 9.5 | 1200.8823
5068 | 2023-07-31 04:00 | 54.3033 | 53.53 | 20 | 10 | 0 | 19 | 2156.6656
5069 | 2023-07-31 05:00 | 69.9468 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 185.2152
5070 | 2023-07-31 06:00 | 55.5574 | 53.53 | 20 | 10 | 0 | 20 | 2181.7484
5071 | 2023-07-31 07:00 | 78.5346 | 53.53 | 10 | 0 | 0 | 20 | 1320.6465
5072 | 2023-07-31 08:00 | 108.2882 | 65.03 | 0 | 0 | 10 | 10 | 0
5073 | 2023-07-31 09:00 | 86.9024 | 65.03 | 20 | 10 | 0 | 19.5 | 3038.649
5074 | 2023-07-31 10:00 | 100.1516 | 65.03 | 0 | 0 | 10 | 9.5 | 0
5075 | 2023-07-31 11:00 | 89.1929 | 65.03 | 10 | 0 | 0 | 9.5 | 1542.2287
5076 | 2023-07-31 12:00 | 92.2164 | 65.03 | 10 | 0 | 0 | 9.5 | 1572.4641
5077 | 2023-07-31 13:00 | 89.4285 | 65.03 | 10 | 0 | 0 | 9.5 | 1544.5854
5078 | 2023-07-31 14:00 | 96.1391 | 65.03 | 1.5 | 0 | 8.5 | 1 | 241.7536
5079 | 2023-07-31 15:00 | 84.2511 | 65.03 | 20 | 10 | 0 | 10.5 | 2985.6212
5080 | 2023-07-31 16:00 | 82.5076 | 65.03 | 20 | 10 | 0 | 20 | 2950.7521
5081 | 2023-07-31 17:00 | 99.5398 | 66.4 | 10 | 0 | 0 | 20 | 1659.3979
5082 | 2023-07-31 18:00 | 104.6574 | 66.4 | 0 | 0 | 10 | 10 | 0
5083 | 2023-07-31 19:00 | 102.2958 | 65.03 | 0 | 0 | 10 | 0 | 0
5084 | 2023-07-31 20:00 | 89.8355 | 65.03 | 10 | 0 | 0 | 0 | 1548.6547
5085 | 2023-07-31 21:00 | 95.8753 | 65.03 | 10 | 0 | 0 | 0 | 1609.0528
5086 | 2023-07-31 22:00 | 77.5535 | 65.03 | 10 | 0 | 0 | 0 | 1425.8349
5087 | 2023-07-31 23:00 | 73.9576 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1341.9744
5088 | 2023-08-01 00:00 | 70.1469 | 53.53 | 20 | 10 | 0 | 10 | 2473.5372
5089 | 2023-08-01 01:00 | 99.8682 | 53.53 | 0 | 0 | 10 | 0 | 0
5090 | 2023-08-01 02:00 | 61.291 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1269.0743
5091 | 2023-08-01 03:00 | 62.7687 | 53.53 | 10 | 0 | 0 | 1 | 1162.987
5092 | 2023-08-01 04:00 | 50.6218 | 53.53 | 20 | 10 | 0 | 10.5 | 2083.0356
5093 | 2023-08-01 05:00 | 58.8895 | 53.53 | 20 | 10 | 0 | 20 | 2248.3907
5094 | 2023-08-01 06:00 | 63.0249 | 53.53 | 10 | 0 | 0 | 20 | 1165.5486
5095 | 2023-08-01 07:00 | 77.0727 | 53.53 | 10 | 0 | 0 | 20 | 1306.0271
5096 | 2023-08-01 08:00 | 98.42 | 65.03 | 0 | 0 | 10 | 10 | 0
5097 | 2023-08-01 09:00 | 113.9184 | 65.03 | 0 | 0 | 10 | 0 | 0
5098 | 2023-08-01 10:00 | 82.7152 | 65.03 | 20 | 10 | 0 | 9.5 | 2954.9047
5099 | 2023-08-01 11:00 | 82.2964 | 65.03 | 20 | 10 | 0 | 19 | 2946.5289
5100 | 2023-08-01 12:00 | 83.1106 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1637.3432
5101 | 2023-08-01 13:00 | 104.3754 | 65.03 | 0 | 0 | 10 | 10 | 0
5102 | 2023-08-01 14:00 | 98.0763 | 65.03 | 1 | 0 | 9 | 1 | 163.1063
5103 | 2023-08-01 15:00 | 87.9022 | 65.03 | 20 | 10 | 0 | 10.5 | 3058.6447
5104 | 2023-08-01 16:00 | 89.174 | 65.03 | 20 | 10 | 0 | 20 | 3084.0803
5105 | 2023-08-01 17:00 | 98.4666 | 66.4 | 10 | 0 | 0 | 20 | 1648.6664
5106 | 2023-08-01 18:00 | 111.5496 | 66.4 | 0 | 0 | 10 | 10 | 0
5107 | 2023-08-01 19:00 | 101.2054 | 65.03 | 0 | 0 | 10 | 0 | 0
5108 | 2023-08-01 20:00 | 82.0219 | 65.03 | 10 | 0 | 0 | 0 | 1470.5189
5109 | 2023-08-01 21:00 | 88.9078 | 65.03 | 10 | 0 | 0 | 0 | 1539.3777
5110 | 2023-08-01 22:00 | 82.5274 | 65.03 | 10 | 0 | 0 | 0 | 1475.5737
5111 | 2023-08-01 23:00 | 77.1967 | 53.53 | 20 | 10 | 0 | 9.5 | 2614.5347
5112 | 2023-08-02 00:00 | 78.9777 | 53.53 | 10 | 0 | 0 | 9.5 | 1325.0775
5113 | 2023-08-02 01:00 | 85.6353 | 53.53 | 0.5 | 0 | 9.5 | 0 | 69.5826
5114 | 2023-08-02 02:00 | 74.8676 | 53.53 | 10 | 0 | 0 | 0 | 1283.9764
5115 | 2023-08-02 03:00 | 63.6987 | 53.53 | 10 | 0 | 0 | 0 | 1172.287
5116 | 2023-08-02 04:00 | -66.8933 | 53.53 | 20 | 10 | 0 | 9.5 | -267.267
5117 | 2023-08-02 05:00 | -77.495 | 53.53 | 20 | 10 | 0 | 19 | -479.2994
5118 | 2023-08-02 06:00 | 54.1156 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1189.7667
5119 | 2023-08-02 07:00 | 84.3174 | 53.53 | 10 | 0 | 0 | 20 | 1378.4744
5120 | 2023-08-02 08:00 | 90.2162 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 77.6231
5121 | 2023-08-02 09:00 | 80.2133 | 65.03 | 20 | 10 | 0 | 20 | 2904.8669
5122 | 2023-08-02 10:00 | 86.555 | 65.03 | 10 | 0 | 0 | 20 | 1515.8499
5123 | 2023-08-02 11:00 | 88.2842 | 65.03 | 10 | 0 | 0 | 20 | 1533.1425
5124 | 2023-08-02 12:00 | 85.3486 | 65.03 | 10 | 0 | 0 | 20 | 1503.786
5125 | 2023-08-02 13:00 | 102.8919 | 65.03 | 0 | 0 | 10 | 10 | 0
5126 | 2023-08-02 14:00 | 92.769 | 65.03 | 20 | 10 | 0 | 19.5 | 3155.9803
5127 | 2023-08-02 15:00 | 101.6424 | 65.03 | 1 | 0 | 9 | 10.5 | 166.6724
5128 | 2023-08-02 16:00 | 90.9542 | 65.03 | 20 | 10 | 0 | 20 | 3119.6832
5129 | 2023-08-02 17:00 | 104.5162 | 66.4 | 0 | 0 | 10 | 10 | 0
5130 | 2023-08-02 18:00 | 97.7744 | 66.4 | 10 | 0 | 0 | 10 | 1641.744
5131 | 2023-08-02 19:00 | 103.9879 | 65.03 | 0 | 0 | 10 | 0 | 0
5132 | 2023-08-02 20:00 | 83.9964 | 65.03 | 10 | 0 | 0 | 0 | 1490.264
5133 | 2023-08-02 21:00 | 75.4873 | 65.03 | 10 | 0 | 0 | 0 | 1405.1734
5134 | 2023-08-02 22:00 | 80.1624 | 65.03 | 10 | 0 | 0 | 0 | 1451.9235
5135 | 2023-08-02 23:00 | 76.5876 | 53.53 | 10 | 0 | 0 | 0 | 1301.1755
5136 | 2023-08-03 00:00 | 82.1999 | 53.53 | 10 | 0 | 0 | 0 | 1357.2994
5137 | 2023-08-03 01:00 | 82.6093 | 53.53 | 10 | 0 | 0 | 0 | 1361.3932
5138 | 2023-08-03 02:00 | 54.8974 | 53.53 | 20 | 10 | 0 | 9.5 | 2168.5484
5139 | 2023-08-03 03:00 | 62.6742 | 53.53 | 1.5 | 0 | 8.5 | 1 | 174.3062
5140 | 2023-08-03 04:00 | 57.5693 | 53.53 | 10 | 0 | 0 | 1 | 1110.9934
5141 | 2023-08-03 05:00 | 44.468 | 53.53 | 20 | 10 | 0 | 10.5 | 1959.9598
5142 | 2023-08-03 06:00 | 55.515 | 53.53 | 20 | 10 | 0 | 20 | 2180.8997
5143 | 2023-08-03 07:00 | 88.454 | 53.53 | 10 | 0 | 0 | 20 | 1419.84
5144 | 2023-08-03 08:00 | 78.9929 | 65.03 | 10 | 0 | 0 | 20 | 1440.2286
5145 | 2023-08-03 09:00 | 89.7579 | 65.03 | 10 | 0 | 0 | 20 | 1547.8794
5146 | 2023-08-03 10:00 | 104.1219 | 65.03 | 0 | 0 | 10 | 10 | 0
5147 | 2023-08-03 11:00 | 83.7978 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1566.6079
5148 | 2023-08-03 12:00 | 88.9144 | 65.03 | 10 | 0 | 0 | 10.5 | 1539.4443
5149 | 2023-08-03 13:00 | 80.8043 | 65.03 | 20 | 10 | 0 | 20 | 2916.6869
5150 | 2023-08-03 14:00 | 104.6316 | 65.03 | 0 | 0 | 10 | 10 | 0
5151 | 2023-08-03 15:00 | 88.2811 | 65.03 | 20 | 10 | 0 | 19.5 | 3066.2212
5152 | 2023-08-03 16:00 | 89.2505 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1624.0049
5153 | 2023-08-03 17:00 | 116.4293 | 66.4 | 0 | 0 | 10 | 10 | 0
5154 | 2023-08-03 18:00 | 109.3859 | 66.4 | 0 | 0 | 10 | 0 | 0
5155 | 2023-08-03 19:00 | 98.1228 | 65.03 | 10 | 0 | 0 | 0 | 1631.5284
5156 | 2023-08-03 20:00 | 79.486 | 65.03 | 20 | 10 | 0 | 9.5 | 2890.3196
5157 | 2023-08-03 21:00 | 87.9 | 65.03 | 0.5 | 0 | 9.5 | 0 | 76.465
5158 | 2023-08-03 22:00 | 79.6295 | 65.03 | 10 | 0 | 0 | 0 | 1446.595
5159 | 2023-08-03 23:00 | 67.1444 | 53.53 | 20 | 10 | 0 | 9.5 | 2413.488
5160 | 2023-08-04 00:00 | 78.5022 | 53.53 | 0.5 | 0 | 9.5 | 0 | 66.0161
5161 | 2023-08-04 01:00 | 69.9339 | 53.53 | 10 | 0 | 0 | 0 | 1234.6392
5162 | 2023-08-04 02:00 | 74.498 | 53.53 | 10 | 0 | 0 | 0 | 1280.2799
5163 | 2023-08-04 03:00 | 60.26 | 53.53 | 10 | 0 | 0 | 0 | 1137.9
5164 | 2023-08-04 04:00 | 52.9532 | 53.53 | 20 | 10 | 0 | 9.5 | 2129.6637
5165 | 2023-08-04 05:00 | 54.1712 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1190.382
5166 | 2023-08-04 06:00 | 48.0815 | 53.53 | 20 | 10 | 0 | 20 | 2032.2297
5167 | 2023-08-04 07:00 | 71.8743 | 53.53 | 10 | 0 | 0 | 20 | 1254.043
5168 | 2023-08-04 08:00 | 97.8104 | 65.03 | 0 | 0 | 10 | 10 | 0
5169 | 2023-08-04 09:00 | 112.7316 | 65.03 | 0 | 0 | 10 | 0 | 0
5170 | 2023-08-04 10:00 | 94.9855 | 65.03 | 10 | 0 | 0 | 0 | 1600.1546
5171 | 2023-08-04 11:00 | 88.2174 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1693.7874
5172 | 2023-08-04 12:00 | 85.8597 | 65.03 | 20 | 10 | 0 | 10.5 | 3017.7948
5173 | 2023-08-04 13:00 | 82.6621 | 65.03 | 20 | 10 | 0 | 20 | 2953.8412
5174 | 2023-08-04 14:00 | 110.2754 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.6527
5175 | 2023-08-04 15:00 | 87.522 | 65.03 | 20 | 10 | 0 | 20 | 3051.0405
5176 | 2023-08-04 16:00 | 111.0592 | 65.03 | 0 | 0 | 10 | 10 | 0
5177 | 2023-08-04 17:00 | 116.8734 | 66.4 | 0 | 0 | 10 | 0 | 0
5178 | 2023-08-04 18:00 | 93.7281 | 66.4 | 10 | 0 | 0 | 0 | 1601.2808
5179 | 2023-08-04 19:00 | 99.371 | 65.03 | 10 | 0 | 0 | 0 | 1644.0096
5180 | 2023-08-04 20:00 | 79.352 | 65.03 | 20 | 10 | 0 | 9.5 | 2887.6395
5181 | 2023-08-04 21:00 | 83.3066 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1561.4376
5182 | 2023-08-04 22:00 | 83.45 | 65.03 | 10 | 0 | 0 | 10 | 1484.8002
5183 | 2023-08-04 23:00 | 115.319 | 53.53 | 0 | 0 | 10 | 0 | 0
5184 | 2023-08-05 00:00 | 63.9946 | 53.53 | 20 | 10 | 0 | 9.5 | 2350.4921
5185 | 2023-08-05 01:00 | 72.6759 | 53.53 | 0.5 | 0 | 9.5 | 0 | 63.103
5186 | 2023-08-05 02:00 | 55.9773 | 53.53 | 10 | 0 | 0 | 0 | 1095.0733
5187 | 2023-08-05 03:00 | 50.8865 | 53.53 | 20 | 10 | 0 | 9.5 | 2088.3304
5188 | 2023-08-05 04:00 | 51.7385 | 53.53 | 10 | 0 | 0 | 9.5 | 1052.6847
5189 | 2023-08-05 05:00 | 44.1715 | 53.53 | 20 | 10 | 0 | 19 | 1954.0293
5190 | 2023-08-05 06:00 | 51.7098 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1163.1772
5191 | 2023-08-05 07:00 | 75.0437 | 53.53 | 10 | 0 | 0 | 20 | 1285.7366
5192 | 2023-08-05 08:00 | 83.4801 | 53.53 | 10 | 0 | 0 | 20 | 1370.101
5193 | 2023-08-05 09:00 | 85.5624 | 53.53 | 10 | 0 | 0 | 20 | 1390.9236
5194 | 2023-08-05 10:00 | 94.0915 | 53.53 | 0 | 0 | 10 | 10 | 0
5195 | 2023-08-05 11:00 | 89.0126 | 53.53 | 0 | 0 | 10 | 0 | 0
5196 | 2023-08-05 12:00 | 81.4388 | 53.53 | 10 | 0 | 0 | 0 | 1349.6877
5197 | 2023-08-05 13:00 | 73.4886 | 53.53 | 20 | 10 | 0 | 9.5 | 2540.3724
5198 | 2023-08-05 14:00 | 76.78 | 53.53 | 20 | 10 | 0 | 19 | 2606.2006
5199 | 2023-08-05 15:00 | 79.3042 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1468.1671
5200 | 2023-08-05 16:00 | 82.8644 | 53.53 | 10 | 0 | 0 | 20 | 1363.9438
5201 | 2023-08-05 17:00 | 92.5563 | 53.53 | 0 | 0 | 10 | 10 | 0
5202 | 2023-08-05 18:00 | 89.7793 | 53.53 | 0 | 0 | 10 | 0 | 0
5203 | 2023-08-05 19:00 | 88.4021 | 53.53 | 10 | 0 | 0 | 0 | 1419.3207
5204 | 2023-08-05 20:00 | 66.1322 | 53.53 | 20 | 10 | 0 | 9.5 | 2393.2439
5205 | 2023-08-05 21:00 | 74.1968 | 53.53 | 0.5 | 0 | 9.5 | 0 | 63.8634
5206 | 2023-08-05 22:00 | 66.9847 | 53.53 | 10 | 0 | 0 | 0 | 1205.1474
5207 | 2023-08-05 23:00 | 64.4158 | 53.53 | 10 | 0 | 0 | 0 | 1179.4584
5208 | 2023-08-06 00:00 | 68.1119 | 53.53 | 10 | 0 | 0 | 0 | 1216.4192
5209 | 2023-08-06 01:00 | 62.6433 | 53.53 | 10 | 0 | 0 | 0 | 1161.7332
5210 | 2023-08-06 02:00 | 53.915 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1187.5503
5211 | 2023-08-06 03:00 | 57.1147 | 53.53 | 10 | 0 | 0 | 1 | 1106.4468
5212 | 2023-08-06 04:00 | 47.0993 | 53.53 | 20 | 10 | 0 | 10.5 | 2012.5859
5213 | 2023-08-06 05:00 | 47.8264 | 53.53 | 20 | 10 | 0 | 20 | 2027.1276
5214 | 2023-08-06 06:00 | 55.2722 | 53.53 | 10 | 0 | 0 | 20 | 1088.0215
5215 | 2023-08-06 07:00 | 66.078 | 53.53 | 10 | 0 | 0 | 20 | 1196.0801
5216 | 2023-08-06 08:00 | 75.6661 | 53.53 | 10 | 0 | 0 | 20 | 1291.9613
5217 | 2023-08-06 09:00 | 91.6939 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 72.612
5218 | 2023-08-06 10:00 | 88.4924 | 53.53 | 10 | 0 | 0 | 10.5 | 1420.2243
5219 | 2023-08-06 11:00 | 85.8427 | 53.53 | 10 | 0 | 0 | 10.5 | 1393.7266
5220 | 2023-08-06 12:00 | 88.9003 | 53.53 | 10 | 0 | 0 | 10.5 | 1424.3034
5221 | 2023-08-06 13:00 | 69.7124 | 53.53 | 20 | 10 | 0 | 20 | 2464.8488
5222 | 2023-08-06 14:00 | 93.424 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 73.477
5223 | 2023-08-06 15:00 | 84.0187 | 53.53 | 20 | 10 | 0 | 20 | 2750.9737
5224 | 2023-08-06 16:00 | 89.7541 | 53.53 | 10 | 0 | 0 | 20 | 1432.841
5225 | 2023-08-06 17:00 | 98.9774 | 53.53 | 0 | 0 | 10 | 10 | 0
5226 | 2023-08-06 18:00 | 96.2679 | 53.53 | 0 | 0 | 10 | 0 | 0
5227 | 2023-08-06 19:00 | 93.9165 | 53.53 | 10 | 0 | 0 | 0 | 1474.4646
5228 | 2023-08-06 20:00 | 78.8093 | 53.53 | 10 | 0 | 0 | 0 | 1323.3926
5229 | 2023-08-06 21:00 | 73.6662 | 53.53 | 20 | 10 | 0 | 9.5 | 2543.924
5230 | 2023-08-06 22:00 | 83.3333 | 53.53 | 0.5 | 0 | 9.5 | 0 | 68.4317
5231 | 2023-08-06 23:00 | 61.4309 | 53.53 | 20 | 10 | 0 | 9.5 | 2299.2174
5232 | 2023-08-07 00:00 | 75.1493 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1354.5188
5233 | 2023-08-07 01:00 | 100.068 | 53.53 | 0 | 0 | 10 | 0 | 0
5234 | 2023-08-07 02:00 | 54.6173 | 53.53 | 20 | 10 | 0 | 9.5 | 2162.9463
5235 | 2023-08-07 03:00 | 57.1708 | 53.53 | 10 | 0 | 0 | 9.5 | 1107.0077
5236 | 2023-08-07 04:00 | 53.0828 | 53.53 | 20 | 10 | 0 | 19 | 2132.2557
5237 | 2023-08-07 05:00 | 61.5484 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 172.6176
5238 | 2023-08-07 06:00 | 53.9436 | 53.53 | 20 | 10 | 0 | 20 | 2149.4728
5239 | 2023-08-07 07:00 | 77.5443 | 53.53 | 10 | 0 | 0 | 20 | 1310.7427
5240 | 2023-08-07 08:00 | 96.1489 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 80.5894
5241 | 2023-08-07 09:00 | 84.1704 | 65.03 | 20 | 10 | 0 | 20 | 2984.0086
5242 | 2023-08-07 10:00 | 95.5711 | 65.03 | 10 | 0 | 0 | 20 | 1606.0113
5243 | 2023-08-07 11:00 | 95.8922 | 65.03 | 10 | 0 | 0 | 20 | 1609.2219
5244 | 2023-08-07 12:00 | 98.2058 | 65.03 | 0 | 0 | 10 | 10 | 0
5245 | 2023-08-07 13:00 | 89.9749 | 65.03 | 20 | 10 | 0 | 19.5 | 3100.098
5246 | 2023-08-07 14:00 | 130.0039 | 65.03 | 0 | 0 | 10 | 9.5 | 0
5247 | 2023-08-07 15:00 | 98.2014 | 65.03 | 1.5 | 0 | 8.5 | 1 | 244.8471
5248 | 2023-08-07 16:00 | 91.4576 | 65.03 | 10 | 0 | 0 | 1 | 1564.8758
5249 | 2023-08-07 17:00 | -9.1747 | 66.4 | 20 | 10 | 0 | 10.5 | 1144.5059
5250 | 2023-08-07 18:00 | -13.9196 | 66.4 | 20 | 10 | 0 | 20 | 1049.6086
5251 | 2023-08-07 19:00 | 117.249 | 65.03 | 0 | 0 | 10 | 10 | 0
5252 | 2023-08-07 20:00 | 100.6498 | 65.03 | 0 | 0 | 10 | 0 | 0
5253 | 2023-08-07 21:00 | 97.852 | 65.03 | 10 | 0 | 0 | 0 | 1628.8204
5254 | 2023-08-07 22:00 | 90.5387 | 65.03 | 10 | 0 | 0 | 0 | 1555.6867
5255 | 2023-08-07 23:00 | 71.0514 | 53.53 | 10 | 0 | 0 | 0 | 1245.8139
5256 | 2023-08-08 00:00 | -8.7558 | 53.53 | 20 | 10 | 0 | 9.5 | 895.4846
5257 | 2023-08-08 01:00 | 71.1249 | 53.53 | 0.5 | 0 | 9.5 | 0 | 62.3275
5258 | 2023-08-08 02:00 | -20.7984 | 53.53 | 20 | 10 | 0 | 9.5 | 654.6327
5259 | 2023-08-08 03:00 | 60.7579 | 53.53 | 20 | 10 | 0 | 19 | 2285.7582
5260 | 2023-08-08 04:00 | 63.147 | 53.53 | 10 | 0 | 0 | 19 | 1166.7702
5261 | 2023-08-08 05:00 | 66.6806 | 53.53 | 10 | 0 | 0 | 19 | 1202.1061
5262 | 2023-08-08 06:00 | 62.9192 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1287.0703
5263 | 2023-08-08 07:00 | 83.2207 | 53.53 | 10 | 0 | 0 | 20 | 1367.507
5264 | 2023-08-08 08:00 | 82.5042 | 65.03 | 10 | 0 | 0 | 20 | 1475.3423
5265 | 2023-08-08 09:00 | 88.1232 | 65.03 | 0 | 0 | 10 | 10 | 0
5266 | 2023-08-08 10:00 | 79.805 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1524.5791
5267 | 2023-08-08 11:00 | 77.6047 | 65.03 | 20 | 10 | 0 | 20 | 2852.6947
5268 | 2023-08-08 12:00 | 95.1186 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 80.0743
5269 | 2023-08-08 13:00 | -68.8072 | 65.03 | 20 | 10 | 0 | 20 | -75.5447
5270 | 2023-08-08 14:00 | 96.3783 | 65.03 | 10 | 0 | 0 | 20 | 1614.0833
5271 | 2023-08-08 15:00 | 98.7597 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 81.8949
5272 | 2023-08-08 16:00 | 84.6594 | 65.03 | 20 | 10 | 0 | 20 | 2993.7879
5273 | 2023-08-08 17:00 | 108.7419 | 66.4 | 0 | 0 | 10 | 10 | 0
5274 | 2023-08-08 18:00 | 99.4004 | 66.4 | 0 | 0 | 10 | 0 | 0
5275 | 2023-08-08 19:00 | 93.2679 | 65.03 | 10 | 0 | 0 | 0 | 1582.9787
5276 | 2023-08-08 20:00 | 84.8404 | 65.03 | 10 | 0 | 0 | 0 | 1498.7045
5277 | 2023-08-08 21:00 | 80.6048 | 65.03 | 10 | 0 | 0 | 0 | 1456.3485
5278 | 2023-08-08 22:00 | -22.291 | 65.03 | 20 | 10 | 0 | 9.5 | 854.7793
5279 | 2023-08-08 23:00 | -20.295 | 53.53 | 20 | 10 | 0 | 19 | 664.7009
5280 | 2023-08-09 00:00 | 69.7158 | 53.53 | 1 | 0 | 9 | 10 | 123.2458
5281 | 2023-08-09 01:00 | 81.9413 | 53.53 | 0 | 0 | 10 | 0 | 0
5282 | 2023-08-09 02:00 | 52.4476 | 53.53 | 20 | 10 | 0 | 9.5 | 2119.5527
5283 | 2023-08-09 03:00 | -47.7693 | 53.53 | 20 | 10 | 0 | 19 | 115.2138
5284 | 2023-08-09 04:00 | 61.2398 | 53.53 | 2 | 0 | 8 | 11 | 229.5396
5285 | 2023-08-09 05:00 | 61.9116 | 53.53 | 0 | 0 | 10 | 1 | 0
5286 | 2023-08-09 06:00 | -43.0838 | 53.53 | 20 | 10 | 0 | 10.5 | 208.9236
5287 | 2023-08-09 07:00 | -19.3107 | 53.53 | 20 | 10 | 0 | 20 | 684.3866
5288 | 2023-08-09 08:00 | 96.9162 | 65.03 | 10 | 0 | 0 | 20 | 1619.4624
5289 | 2023-08-09 09:00 | 106.4243 | 65.03 | 0 | 0 | 10 | 10 | 0
5290 | 2023-08-09 10:00 | 92.7731 | 65.03 | 10 | 0 | 0 | 10 | 1578.0308
5291 | 2023-08-09 11:00 | 82.9976 | 65.03 | 20 | 10 | 0 | 19.5 | 2960.5513
5292 | 2023-08-09 12:00 | 91.5741 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1648.464
5293 | 2023-08-09 13:00 | 115.6842 | 65.03 | 0 | 0 | 10 | 10 | 0
5294 | 2023-08-09 14:00 | 89.6784 | 65.03 | 20 | 10 | 0 | 19.5 | 3094.168
5295 | 2023-08-09 15:00 | 102.6598 | 65.03 | 1 | 0 | 9 | 10.5 | 167.6898
5296 | 2023-08-09 16:00 | 83.9192 | 65.03 | 20 | 10 | 0 | 20 | 2978.9842
5297 | 2023-08-09 17:00 | 103.5846 | 66.4 | 10 | 0 | 0 | 20 | 1699.8464
5298 | 2023-08-09 18:00 | 109.0049 | 66.4 | 0 | 0 | 10 | 10 | 0
5299 | 2023-08-09 19:00 | 107.0631 | 65.03 | 0 | 0 | 10 | 0 | 0
5300 | 2023-08-09 20:00 | 78.7633 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1513.6137
5301 | 2023-08-09 21:00 | 78.5079 | 65.03 | 20 | 10 | 0 | 10 | 2870.7586
5302 | 2023-08-09 22:00 | 92.5264 | 65.03 | 0 | 0 | 10 | 0 | 0
5303 | 2023-08-09 23:00 | 89.6408 | 53.53 | 10 | 0 | 0 | 0 | 1431.7083
5304 | 2023-08-10 00:00 | 93.2492 | 53.53 | 10 | 0 | 0 | 0 | 1467.7921
5305 | 2023-08-10 01:00 | 96.8491 | 53.53 | 10 | 0 | 0 | 0 | 1503.7909
5306 | 2023-08-10 02:00 | 59.9286 | 53.53 | 20 | 10 | 0 | 9.5 | 2269.1723
5307 | 2023-08-10 03:00 | 56.6699 | 53.53 | 20 | 10 | 0 | 19 | 2203.999
5308 | 2023-08-10 04:00 | 71.392 | 53.53 | 0 | 0 | 10 | 9 | 0
5309 | 2023-08-10 05:00 | 64.8614 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1370.848
5310 | 2023-08-10 06:00 | 52.5165 | 53.53 | 20 | 10 | 0 | 20 | 2120.93
5311 | 2023-08-10 07:00 | 72.2328 | 53.53 | 10 | 0 | 0 | 20 | 1257.6282
5312 | 2023-08-10 08:00 | 92.8739 | 65.03 | 10 | 0 | 0 | 20 | 1579.0393
5313 | 2023-08-10 09:00 | 87.6035 | 65.03 | 10 | 0 | 0 | 20 | 1526.3348
5314 | 2023-08-10 10:00 | 88.7009 | 65.03 | 10 | 0 | 0 | 20 | 1537.3087
5315 | 2023-08-10 11:00 | 98.3871 | 65.03 | 10 | 0 | 0 | 20 | 1634.1715
5316 | 2023-08-10 12:00 | 95.2914 | 65.03 | 10 | 0 | 0 | 20 | 1603.2137
5317 | 2023-08-10 13:00 | 101.1552 | 65.03 | 0 | 0 | 10 | 10 | 0
5318 | 2023-08-10 14:00 | 77.9033 | 65.03 | 20 | 10 | 0 | 19.5 | 2858.6663
5319 | 2023-08-10 15:00 | 90.8729 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1641.0831
5320 | 2023-08-10 16:00 | 94.6912 | 65.03 | 10 | 0 | 0 | 20 | 1597.2115
5321 | 2023-08-10 17:00 | 94.7124 | 66.4 | 10 | 0 | 0 | 20 | 1611.1238
5322 | 2023-08-10 18:00 | 99.439 | 66.4 | 0 | 0 | 10 | 10 | 0
5323 | 2023-08-10 19:00 | 98.3266 | 65.03 | 10 | 0 | 0 | 10 | 1633.566
5324 | 2023-08-10 20:00 | 84.0616 | 65.03 | 20 | 10 | 0 | 19.5 | 2981.8315
5325 | 2023-08-10 21:00 | 99.6392 | 65.03 | 0.5 | 0 | 9.5 | 10 | 82.3346
5326 | 2023-08-10 22:00 | 104.761 | 65.03 | 0 | 0 | 10 | 0 | 0
5327 | 2023-08-10 23:00 | 73.4799 | 53.53 | 20 | 10 | 0 | 9.5 | 2540.1978
5328 | 2023-08-11 00:00 | 83.1765 | 53.53 | 10 | 0 | 0 | 9.5 | 1367.065
5329 | 2023-08-11 01:00 | 83.4611 | 53.53 | 0.5 | 0 | 9.5 | 0 | 68.4955
5330 | 2023-08-11 02:00 | 61.9813 | 53.53 | 20 | 10 | 0 | 9.5 | 2310.2256
5331 | 2023-08-11 03:00 | 62.0771 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1277.7627
5332 | 2023-08-11 04:00 | 61.2834 | 53.53 | 20 | 10 | 0 | 20 | 2296.2678
5333 | 2023-08-11 05:00 | 75.3756 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 64.4528
5334 | 2023-08-11 06:00 | 68.6983 | 53.53 | 20 | 10 | 0 | 20 | 2444.565
5335 | 2023-08-11 07:00 | 72.0875 | 53.53 | 10 | 0 | 0 | 20 | 1256.1754
5336 | 2023-08-11 08:00 | 95.6388 | 65.03 | 10 | 0 | 0 | 20 | 1606.6876
5337 | 2023-08-11 09:00 | 96.5726 | 65.03 | 1 | 0 | 9 | 11 | 161.6026
5338 | 2023-08-11 10:00 | 91.3758 | 65.03 | 10 | 0 | 0 | 11 | 1564.0577
5339 | 2023-08-11 11:00 | 99.0019 | 65.03 | 0 | 0 | 10 | 1 | 0
5340 | 2023-08-11 12:00 | 90.3494 | 65.03 | 10 | 0 | 0 | 1 | 1553.7941
5341 | 2023-08-11 13:00 | 90.4479 | 65.03 | 10 | 0 | 0 | 1 | 1554.7794
5342 | 2023-08-11 14:00 | 89.8243 | 65.03 | 10 | 0 | 0 | 1 | 1548.5435
5343 | 2023-08-11 15:00 | 77.5437 | 65.03 | 20 | 10 | 0 | 10.5 | 2851.4742
5344 | 2023-08-11 16:00 | 88.3025 | 65.03 | 20 | 10 | 0 | 20 | 3066.6506
5345 | 2023-08-11 17:00 | 99.3569 | 66.4 | 0 | 0 | 10 | 10 | 0
5346 | 2023-08-11 18:00 | 96.4113 | 66.4 | 10 | 0 | 0 | 10 | 1628.1127
5347 | 2023-08-11 19:00 | 117.3376 | 65.03 | 0 | 0 | 10 | 0 | 0
5348 | 2023-08-11 20:00 | 87.9808 | 65.03 | 10 | 0 | 0 | 0 | 1530.1085
5349 | 2023-08-11 21:00 | 83.6756 | 65.03 | 10 | 0 | 0 | 0 | 1487.0557
5350 | 2023-08-11 22:00 | 80.0017 | 65.03 | 10 | 0 | 0 | 0 | 1450.3172
5351 | 2023-08-11 23:00 | 81.2212 | 53.53 | 10 | 0 | 0 | 0 | 1347.5125
5352 | 2023-08-12 00:00 | 79.5582 | 53.53 | 10 | 0 | 0 | 0 | 1330.8819
5353 | 2023-08-12 01:00 | 65.4056 | 53.53 | 10 | 0 | 0 | 0 | 1189.3555
5354 | 2023-08-12 02:00 | 50.8621 | 53.53 | 20 | 10 | 0 | 9.5 | 2087.8424
5355 | 2023-08-12 03:00 | 58.3352 | 53.53 | 0.5 | 0 | 9.5 | 0 | 55.9326
5356 | 2023-08-12 04:00 | 39.8846 | 53.53 | 20 | 10 | 0 | 9.5 | 1868.2913
5357 | 2023-08-12 05:00 | 50.4702 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1149.4763
5358 | 2023-08-12 06:00 | 47.8773 | 53.53 | 20 | 10 | 0 | 20 | 2028.1465
5359 | 2023-08-12 07:00 | 69.9145 | 53.53 | 10 | 0 | 0 | 20 | 1234.4446
5360 | 2023-08-12 08:00 | 77.4055 | 53.53 | 10 | 0 | 0 | 20 | 1309.355
5361 | 2023-08-12 09:00 | 81.9521 | 53.53 | 10 | 0 | 0 | 20 | 1354.8209
5362 | 2023-08-12 10:00 | 100.4194 | 53.53 | 0 | 0 | 10 | 10 | 0
5363 | 2023-08-12 11:00 | 78.5832 | 53.53 | 20 | 10 | 0 | 19.5 | 2642.2639
5364 | 2023-08-12 12:00 | 83.1847 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1439.1024
5365 | 2023-08-12 13:00 | 101.3795 | 53.53 | 0 | 0 | 10 | 10 | 0
5366 | 2023-08-12 14:00 | 77.0955 | 53.53 | 20 | 10 | 0 | 19.5 | 2612.511
5367 | 2023-08-12 15:00 | 98.9878 | 53.53 | 1 | 0 | 9 | 10.5 | 152.5178
5368 | 2023-08-12 16:00 | 80.9383 | 53.53 | 20 | 10 | 0 | 20 | 2689.3652
5369 | 2023-08-12 17:00 | 113.5661 | 53.53 | 0 | 0 | 10 | 10 | 0
5370 | 2023-08-12 18:00 | 102.2083 | 53.53 | 0 | 0 | 10 | 0 | 0
5371 | 2023-08-12 19:00 | 98.3111 | 53.53 | 10 | 0 | 0 | 0 | 1518.4106
5372 | 2023-08-12 20:00 | 75.4109 | 53.53 | 10 | 0 | 0 | 0 | 1289.4089
5373 | 2023-08-12 21:00 | 71.63 | 53.53 | 20 | 10 | 0 | 9.5 | 2503.1999
5374 | 2023-08-12 22:00 | 76.4733 | 53.53 | 10 | 0 | 0 | 9.5 | 1300.0325
5375 | 2023-08-12 23:00 | 78.6215 | 53.53 | 0.5 | 0 | 9.5 | 0 | 66.0758
5376 | 2023-08-13 00:00 | -42.5984 | 53.53 | 20 | 10 | 0 | 9.5 | 218.6322
5377 | 2023-08-13 01:00 | -36.3085 | 53.53 | 20 | 10 | 0 | 19 | 344.4298
5378 | 2023-08-13 02:00 | 49.0864 | 53.53 | 2 | 0 | 8 | 11 | 205.2329
5379 | 2023-08-13 03:00 | 59.5687 | 53.53 | 0 | 0 | 10 | 1 | 0
5380 | 2023-08-13 04:00 | -7.3721 | 53.53 | 20 | 10 | 0 | 10.5 | 923.1573
5381 | 2023-08-13 05:00 | 46.3636 | 53.53 | 10 | 0 | 0 | 10.5 | 998.936
5382 | 2023-08-13 06:00 | -5.4964 | 53.53 | 20 | 10 | 0 | 20 | 960.6713
5383 | 2023-08-13 07:00 | 73.9117 | 53.53 | 10 | 0 | 0 | 20 | 1274.4172
5384 | 2023-08-13 08:00 | 95.4313 | 53.53 | 0 | 0 | 10 | 10 | 0
5385 | 2023-08-13 09:00 | 91.1556 | 53.53 | 0 | 0 | 10 | 0 | 0
5386 | 2023-08-13 10:00 | 73.071 | 53.53 | 20 | 10 | 0 | 9.5 | 2532.0199
5387 | 2023-08-13 11:00 | 78.9942 | 53.53 | 10 | 0 | 0 | 9.5 | 1325.2416
5388 | 2023-08-13 12:00 | 74.8084 | 53.53 | 11.5789 | 1.5789 | 0 | 11 | 1486.0233
5389 | 2023-08-13 13:00 | 78.9704 | 53.53 | 10 | 0 | 0 | 11 | 1325.0036
5390 | 2023-08-13 14:00 | 96.3537 | 53.53 | 0 | 0 | 10 | 1 | 0
5391 | 2023-08-13 15:00 | 72.2135 | 53.53 | 20 | 10 | 0 | 10.5 | 2514.8696
5392 | 2023-08-13 16:00 | 71.2806 | 53.53 | 20 | 10 | 0 | 20 | 2496.2117
5393 | 2023-08-13 17:00 | 90.3963 | 53.53 | 10 | 0 | 0 | 20 | 1439.2626
5394 | 2023-08-13 18:00 | 98.1487 | 53.53 | 0 | 0 | 10 | 10 | 0
5395 | 2023-08-13 19:00 | 101.0157 | 53.53 | 0 | 0 | 10 | 0 | 0
5396 | 2023-08-13 20:00 | 79.4042 | 53.53 | 20 | 10 | 0 | 9.5 | 2658.6837
5397 | 2023-08-13 21:00 | 86.4711 | 53.53 | 0.5 | 0 | 9.5 | 0 | 70.0006
5398 | 2023-08-13 22:00 | 65.6292 | 53.53 | 20 | 10 | 0 | 9.5 | 2383.185
5399 | 2023-08-13 23:00 | 81.6064 | 53.53 | 10 | 0 | 0 | 9.5 | 1351.3638
5400 | 2023-08-14 00:00 | 76.6638 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1370.4614
5401 | 2023-08-14 01:00 | 85.033 | 53.53 | 0 | 0 | 10 | 0 | 0
5402 | 2023-08-14 02:00 | 50.7062 | 53.53 | 20 | 10 | 0 | 9.5 | 2084.7238
5403 | 2023-08-14 03:00 | 58.9355 | 53.53 | 20 | 10 | 0 | 19 | 2249.3102
5404 | 2023-08-14 04:00 | 60.7346 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1262.9251
5405 | 2023-08-14 05:00 | 69.259 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 61.3945
5406 | 2023-08-14 06:00 | 49.4365 | 53.53 | 20 | 10 | 0 | 20 | 2059.3295
5407 | 2023-08-14 07:00 | 79.13 | 53.53 | 10 | 0 | 0 | 20 | 1326.6002
5408 | 2023-08-14 08:00 | 81.9512 | 65.03 | 10 | 0 | 0 | 20 | 1469.8119
5409 | 2023-08-14 09:00 | 92.9921 | 65.03 | 10 | 0 | 0 | 20 | 1580.2209
5410 | 2023-08-14 10:00 | 95.463 | 65.03 | 10 | 0 | 0 | 20 | 1604.9305
5411 | 2023-08-14 11:00 | 100.681 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 82.8555
5412 | 2023-08-14 12:00 | 85.1911 | 65.03 | 20 | 10 | 0 | 20 | 3004.4213
5413 | 2023-08-14 13:00 | 96.916 | 65.03 | 10 | 0 | 0 | 20 | 1619.4601
5414 | 2023-08-14 14:00 | 101.5037 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 83.2668
5415 | 2023-08-14 15:00 | 79.1685 | 65.03 | 20 | 10 | 0 | 20 | 2883.9697
5416 | 2023-08-14 16:00 | 93.9398 | 65.03 | 10 | 0 | 0 | 20 | 1589.6979
5417 | 2023-08-14 17:00 | 112.2273 | 66.4 | 0 | 0 | 10 | 10 | 0
5418 | 2023-08-14 18:00 | 102.0313 | 66.4 | 0 | 0 | 10 | 0 | 0
5419 | 2023-08-14 19:00 | 96.2839 | 65.03 | 10 | 0 | 0 | 0 | 1613.1393
5420 | 2023-08-14 20:00 | 92.0722 | 65.03 | 10 | 0 | 0 | 0 | 1571.0218
5421 | 2023-08-14 21:00 | 76.3428 | 65.03 | 10 | 0 | 0 | 0 | 1413.7278
5422 | 2023-08-14 22:00 | 82.5958 | 65.03 | 10 | 0 | 0 | 0 | 1476.2583
5423 | 2023-08-14 23:00 | 78.5992 | 53.53 | 10 | 0 | 0 | 0 | 1321.2918
5424 | 2023-08-15 00:00 | 84.8844 | 53.53 | 10 | 0 | 0 | 0 | 1384.1436
5425 | 2023-08-15 01:00 | 74.6139 | 53.53 | 10 | 0 | 0 | 0 | 1281.4389
5426 | 2023-08-15 02:00 | 54.2569 | 53.53 | 20 | 10 | 0 | 9.5 | 2155.737
5427 | 2023-08-15 03:00 | 59.6513 | 53.53 | 20 | 10 | 0 | 19 | 2263.6258
5428 | 2023-08-15 04:00 | 67.7095 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1340.0159
5429 | 2023-08-15 05:00 | 83.5539 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 68.5419
5430 | 2023-08-15 06:00 | 49.8033 | 53.53 | 20 | 10 | 0 | 20 | 2066.6655
5431 | 2023-08-15 07:00 | 81.3789 | 53.53 | 10 | 0 | 0 | 20 | 1349.0885
5432 | 2023-08-15 08:00 | 81.9441 | 65.03 | 10 | 0 | 0 | 20 | 1469.7415
5433 | 2023-08-15 09:00 | 97.8358 | 65.03 | 0 | 0 | 10 | 10 | 0
5434 | 2023-08-15 10:00 | 82.7634 | 65.03 | 20 | 10 | 0 | 19.5 | 2955.8677
5435 | 2023-08-15 11:00 | 84.3176 | 65.03 | 10 | 0 | 0 | 19.5 | 1493.4762
5436 | 2023-08-15 12:00 | 84.8474 | 65.03 | 10 | 0 | 0 | 19.5 | 1498.7738
5437 | 2023-08-15 13:00 | 88.3333 | 65.03 | 10 | 0 | 0 | 19.5 | 1533.633
5438 | 2023-08-15 14:00 | 91.4437 | 65.03 | 1.5 | 0 | 8.5 | 11 | 234.7105
5439 | 2023-08-15 15:00 | 92.8025 | 65.03 | 0 | 0 | 10 | 1 | 0
5440 | 2023-08-15 16:00 | 88.8551 | 65.03 | 10 | 0 | 0 | 1 | 1538.8509
5441 | 2023-08-15 17:00 | -66.1504 | 66.4 | 20 | 10 | 0 | 10.5 | 4.9917
5442 | 2023-08-15 18:00 | -66.5636 | 66.4 | 20 | 10 | 0 | 20 | -3.2718
5443 | 2023-08-15 19:00 | 103.5043 | 65.03 | 0 | 0 | 10 | 10 | 0
5444 | 2023-08-15 20:00 | 94.3225 | 65.03 | 0 | 0 | 10 | 0 | 0
5445 | 2023-08-15 21:00 | 79.1159 | 65.03 | 10 | 0 | 0 | 0 | 1441.4592
5446 | 2023-08-15 22:00 | 74.3573 | 65.03 | 10 | 0 | 0 | 0 | 1393.8734
5447 | 2023-08-15 23:00 | 78.6444 | 53.53 | 20 | 10 | 0 | 9.5 | 2643.4882
5448 | 2023-08-16 00:00 | 90.778 | 53.53 | 0.5 | 0 | 9.5 | 0 | 72.154
5449 | 2023-08-16 01:00 | 80.135 | 53.53 | 10 | 0 | 0 | 0 | 1336.6499
5450 | 2023-08-16 02:00 | 57.4448 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1284.9708
5451 | 2023-08-16 03:00 | 53.1533 | 53.53 | 20 | 10 | 0 | 11 | 2133.6665
5452 | 2023-08-16 04:00 | 76.2584 | 53.53 | 0 | 0 | 10 | 1 | 0
5453 | 2023-08-16 05:00 | 52.255 | 53.53 | 20 | 10 | 0 | 10.5 | 2115.7003
5454 | 2023-08-16 06:00 | 54.0091 | 53.53 | 20 | 10 | 0 | 20 | 2150.7823
5455 | 2023-08-16 07:00 | 83.5609 | 53.53 | 10 | 0 | 0 | 20 | 1370.9088
5456 | 2023-08-16 08:00 | 78.2242 | 65.03 | 10 | 0 | 0 | 20 | 1432.5421
5457 | 2023-08-16 09:00 | 100.5424 | 65.03 | 0 | 0 | 10 | 10 | 0
5458 | 2023-08-16 10:00 | 94.0468 | 65.03 | 10 | 0 | 0 | 10 | 1590.7676
5459 | 2023-08-16 11:00 | 96.6399 | 65.03 | 0 | 0 | 10 | 0 | 0
5460 | 2023-08-16 12:00 | 93.455 | 65.03 | 10 | 0 | 0 | 0 | 1584.8502
5461 | 2023-08-16 13:00 | 87.7186 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1688.2742
5462 | 2023-08-16 14:00 | 82.0712 | 65.03 | 20 | 10 | 0 | 10.5 | 2942.024
5463 | 2023-08-16 15:00 | 87.8695 | 65.03 | 10 | 0 | 0 | 10.5 | 1528.9951
5464 | 2023-08-16 16:00 | 82.5569 | 65.03 | 20 | 10 | 0 | 20 | 2951.7373
5465 | 2023-08-16 17:00 | 107.8238 | 66.4 | 10 | 0 | 0 | 20 | 1742.2377
5466 | 2023-08-16 18:00 | 110.7442 | 66.4 | 0 | 0 | 10 | 10 | 0
5467 | 2023-08-16 19:00 | 117.8343 | 65.03 | 0 | 0 | 10 | 0 | 0
5468 | 2023-08-16 20:00 | 86.848 | 65.03 | 10 | 0 | 0 | 0 | 1518.78
5469 | 2023-08-16 21:00 | 91.8898 | 65.03 | 10 | 0 | 0 | 0 | 1569.1976
5470 | 2023-08-16 22:00 | 81.7662 | 65.03 | 10 | 0 | 0 | 0 | 1467.9617
5471 | 2023-08-16 23:00 | 75.5567 | 53.53 | 20 | 10 | 0 | 9.5 | 2581.7338
5472 | 2023-08-17 00:00 | 82.7156 | 53.53 | 0.5 | 0 | 9.5 | 0 | 68.1228
5473 | 2023-08-17 01:00 | 76.1615 | 53.53 | 10 | 0 | 0 | 0 | 1296.9148
5474 | 2023-08-17 02:00 | 61.001 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1265.8685
5475 | 2023-08-17 03:00 | 52.0819 | 53.53 | 20 | 10 | 0 | 10.5 | 2112.2374
5476 | 2023-08-17 04:00 | 53.0883 | 53.53 | 20 | 10 | 0 | 20 | 2132.3654
5477 | 2023-08-17 05:00 | 64.1484 | 53.53 | 10 | 0 | 0 | 20 | 1176.7838
5478 | 2023-08-17 06:00 | 66.5169 | 53.53 | 10 | 0 | 0 | 20 | 1200.4691
5479 | 2023-08-17 07:00 | 72.4986 | 53.53 | 10 | 0 | 0 | 20 | 1260.2863
5480 | 2023-08-17 08:00 | 94.4696 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 79.7498
5481 | 2023-08-17 09:00 | 85.2057 | 65.03 | 20 | 10 | 0 | 20 | 3004.7144
5482 | 2023-08-17 10:00 | 89.0224 | 65.03 | 10 | 0 | 0 | 20 | 1540.524
5483 | 2023-08-17 11:00 | 102.1413 | 65.03 | 0 | 0 | 10 | 10 | 0
5484 | 2023-08-17 12:00 | 95.751 | 65.03 | 10 | 0 | 0 | 10 | 1607.81
5485 | 2023-08-17 13:00 | 95.6402 | 65.03 | 10 | 0 | 0 | 10 | 1606.702
5486 | 2023-08-17 14:00 | 108.2217 | 65.03 | 0 | 0 | 10 | 0 | 0
5487 | 2023-08-17 15:00 | 84.1393 | 65.03 | 20 | 10 | 0 | 9.5 | 2983.3868
5488 | 2023-08-17 16:00 | 82.4974 | 65.03 | 20 | 10 | 0 | 19 | 2950.5482
5489 | 2023-08-17 17:00 | 99.0289 | 66.4 | 1 | 0 | 9 | 10 | 165.4289
5490 | 2023-08-17 18:00 | 102.0606 | 66.4 | 0 | 0 | 10 | 0 | 0
5491 | 2023-08-17 19:00 | 91.2342 | 65.03 | 10 | 0 | 0 | 0 | 1562.6417
5492 | 2023-08-17 20:00 | 82.39 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1551.7896
5493 | 2023-08-17 21:00 | 80.1302 | 65.03 | 20 | 10 | 0 | 10 | 2903.2041
5494 | 2023-08-17 22:00 | 90.5251 | 65.03 | 0 | 0 | 10 | 0 | 0
5495 | 2023-08-17 23:00 | 81.6862 | 53.53 | 10 | 0 | 0 | 0 | 1352.1623
5496 | 2023-08-18 00:00 | 74.7757 | 53.53 | 20 | 10 | 0 | 9.5 | 2566.114
5497 | 2023-08-18 01:00 | 83.7387 | 53.53 | 0.5 | 0 | 9.5 | 0 | 68.6344
5498 | 2023-08-18 02:00 | 64.9563 | 53.53 | 10 | 0 | 0 | 0 | 1184.8625
5499 | 2023-08-18 03:00 | 53.7505 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1185.7313
5500 | 2023-08-18 04:00 | 55.4611 | 53.53 | 10 | 0 | 0 | 1 | 1089.9108
5501 | 2023-08-18 05:00 | -22.0202 | 53.53 | 20 | 10 | 0 | 10.5 | 630.1956
5502 | 2023-08-18 06:00 | 51.9218 | 53.53 | 20 | 10 | 0 | 20 | 2109.0366
5503 | 2023-08-18 07:00 | 73.9064 | 53.53 | 10 | 0 | 0 | 20 | 1274.3636
5504 | 2023-08-18 08:00 | 89.4608 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 77.2454
5505 | 2023-08-18 09:00 | 82.7247 | 65.03 | 10 | 0 | 0 | 10.5 | 1477.5472
5506 | 2023-08-18 10:00 | 85.3293 | 65.03 | 10 | 0 | 0 | 10.5 | 1503.5934
5507 | 2023-08-18 11:00 | 81.2082 | 65.03 | 20 | 10 | 0 | 20 | 2924.7634
5508 | 2023-08-18 12:00 | 90.2152 | 65.03 | 10 | 0 | 0 | 20 | 1552.4517
5509 | 2023-08-18 13:00 | 92.304 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 78.667
5510 | 2023-08-18 14:00 | 92.1057 | 65.03 | 10 | 0 | 0 | 10.5 | 1571.3574
5511 | 2023-08-18 15:00 | 88.9912 | 65.03 | 10 | 0 | 0 | 10.5 | 1540.2119
5512 | 2023-08-18 16:00 | 79.6438 | 65.03 | 20 | 10 | 0 | 20 | 2893.4759
5513 | 2023-08-18 17:00 | 99.6554 | 66.4 | 10 | 0 | 0 | 20 | 1660.5543
5514 | 2023-08-18 18:00 | 101.0228 | 66.4 | 0 | 0 | 10 | 10 | 0
5515 | 2023-08-18 19:00 | 101.0494 | 65.03 | 0 | 0 | 10 | 0 | 0
5516 | 2023-08-18 20:00 | 84.467 | 65.03 | 20 | 10 | 0 | 9.5 | 2989.9408
5517 | 2023-08-18 21:00 | 97.24 | 65.03 | 0.5 | 0 | 9.5 | 0 | 81.135
5518 | 2023-08-18 22:00 | 90.7951 | 65.03 | 10 | 0 | 0 | 0 | 1558.2507
5519 | 2023-08-18 23:00 | 72.4882 | 53.53 | 10 | 0 | 0 | 0 | 1260.1824
5520 | 2023-08-19 00:00 | 76.5411 | 53.53 | 10 | 0 | 0 | 0 | 1300.7107
5521 | 2023-08-19 01:00 | 76.1928 | 53.53 | 10 | 0 | 0 | 0 | 1297.2282
5522 | 2023-08-19 02:00 | 45.5282 | 53.53 | 20 | 10 | 0 | 9.5 | 1981.1648
5523 | 2023-08-19 03:00 | 58.1489 | 53.53 | 1.5 | 0 | 8.5 | 1 | 167.5183
5524 | 2023-08-19 04:00 | 49.724 | 53.53 | 20 | 10 | 0 | 10.5 | 2065.0792
5525 | 2023-08-19 05:00 | 42.2755 | 53.53 | 20 | 10 | 0 | 20 | 1916.11
5526 | 2023-08-19 06:00 | 54.5564 | 53.53 | 10 | 0 | 0 | 20 | 1080.8642
5527 | 2023-08-19 07:00 | 72.5796 | 53.53 | 10 | 0 | 0 | 20 | 1261.0964
5528 | 2023-08-19 08:00 | 79.2477 | 53.53 | 10 | 0 | 0 | 20 | 1327.7774
5529 | 2023-08-19 09:00 | 80.619 | 53.53 | 10 | 0 | 0 | 20 | 1341.4898
5530 | 2023-08-19 10:00 | 76.0472 | 53.53 | 10 | 0 | 0 | 20 | 1295.7722
5531 | 2023-08-19 11:00 | 85.9198 | 53.53 | 0 | 0 | 10 | 10 | 0
5532 | 2023-08-19 12:00 | 80.5745 | 53.53 | 10 | 0 | 0 | 10 | 1341.0454
5533 | 2023-08-19 13:00 | 82.1784 | 53.53 | 10 | 0 | 0 | 10 | 1357.0837
5534 | 2023-08-19 14:00 | 83.7256 | 53.53 | 1 | 0 | 9 | 1 | 137.2556
5535 | 2023-08-19 15:00 | 73.5795 | 53.53 | 20 | 10 | 0 | 10.5 | 2542.1895
5536 | 2023-08-19 16:00 | 75.0156 | 53.53 | 20 | 10 | 0 | 20 | 2570.9111
5537 | 2023-08-19 17:00 | 83.7811 | 53.53 | 10 | 0 | 0 | 20 | 1373.111
5538 | 2023-08-19 18:00 | 100.5138 | 53.53 | 0 | 0 | 10 | 10 | 0
5539 | 2023-08-19 19:00 | 88.2764 | 53.53 | 0 | 0 | 10 | 0 | 0
5540 | 2023-08-19 20:00 | 76.9126 | 53.53 | 10 | 0 | 0 | 0 | 1304.4262
5541 | 2023-08-19 21:00 | 78.8415 | 53.53 | 10 | 0 | 0 | 0 | 1323.7146
5542 | 2023-08-19 22:00 | 80.8499 | 53.53 | 10 | 0 | 0 | 0 | 1343.7987
5543 | 2023-08-19 23:00 | 63.3192 | 53.53 | 20 | 10 | 0 | 9.5 | 2336.9842
5544 | 2023-08-20 00:00 | 70.4143 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1304.6773
5545 | 2023-08-20 01:00 | 87.161 | 53.53 | 0 | 0 | 10 | 0 | 0
5546 | 2023-08-20 02:00 | 67.7098 | 53.53 | 10 | 0 | 0 | 0 | 1212.3976
5547 | 2023-08-20 03:00 | -79.5744 | 53.53 | 20 | 10 | 0 | 9.5 | -520.8888
5548 | 2023-08-20 04:00 | -74.5748 | 53.53 | 20 | 10 | 0 | 19 | -420.8961
5549 | 2023-08-20 05:00 | 44.3904 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1082.2782
5550 | 2023-08-20 06:00 | 56.913 | 53.53 | 10 | 0 | 0 | 20 | 1104.4304
5551 | 2023-08-20 07:00 | 69.7408 | 53.53 | 10 | 0 | 0 | 20 | 1232.708
5552 | 2023-08-20 08:00 | 85.4764 | 53.53 | 0 | 0 | 10 | 10 | 0
5553 | 2023-08-20 09:00 | 76.5753 | 53.53 | 20 | 10 | 0 | 19.5 | 2602.1065
5554 | 2023-08-20 10:00 | 79.6344 | 53.53 | 10 | 0 | 0 | 19.5 | 1331.6438
5555 | 2023-08-20 11:00 | 82.1602 | 53.53 | 10 | 0 | 0 | 19.5 | 1356.9023
5556 | 2023-08-20 12:00 | 82.8153 | 53.53 | 10 | 0 | 0 | 19.5 | 1363.4534
5557 | 2023-08-20 13:00 | 84.8895 | 53.53 | 0 | 0 | 10 | 9.5 | 0
5558 | 2023-08-20 14:00 | 76.9108 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1441.7141
5559 | 2023-08-20 15:00 | 72.6064 | 53.53 | 20 | 10 | 0 | 20 | 2522.7271
5560 | 2023-08-20 16:00 | 96.6017 | 53.53 | 10 | 0 | 0 | 20 | 1501.3169
5561 | 2023-08-20 17:00 | 123.653 | 53.53 | 0 | 0 | 10 | 10 | 0
5562 | 2023-08-20 18:00 | 99.4896 | 53.53 | 0 | 0 | 10 | 0 | 0
5563 | 2023-08-20 19:00 | 87.7033 | 53.53 | 10 | 0 | 0 | 0 | 1412.3334
5564 | 2023-08-20 20:00 | 70.7228 | 53.53 | 20 | 10 | 0 | 9.5 | 2485.0556
5565 | 2023-08-20 21:00 | 80.0237 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1405.8286
5566 | 2023-08-20 22:00 | 88.2811 | 53.53 | 0 | 0 | 10 | 0 | 0
5567 | 2023-08-20 23:00 | 63.2729 | 53.53 | 20 | 10 | 0 | 9.5 | 2336.0579
5568 | 2023-08-21 00:00 | 77.983 | 53.53 | 10 | 0 | 0 | 9.5 | 1315.1299
5569 | 2023-08-21 01:00 | 80.4118 | 53.53 | 0.5 | 0 | 9.5 | 0 | 66.9709
5570 | 2023-08-21 02:00 | 66.3013 | 53.53 | 10 | 0 | 0 | 0 | 1198.3125
5571 | 2023-08-21 03:00 | 56.4497 | 53.53 | 20 | 10 | 0 | 9.5 | 2199.5934
5572 | 2023-08-21 04:00 | 49.5367 | 53.53 | 20 | 10 | 0 | 19 | 2061.3347
5573 | 2023-08-21 05:00 | 64.0197 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1299.2333
5574 | 2023-08-21 06:00 | 68.9322 | 53.53 | 10 | 0 | 0 | 20 | 1224.6215
5575 | 2023-08-21 07:00 | 78.2865 | 53.53 | 10 | 0 | 0 | 20 | 1318.1648
5576 | 2023-08-21 08:00 | 92.1301 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 78.58
5577 | 2023-08-21 09:00 | 85.5813 | 65.03 | 10 | 0 | 0 | 10.5 | 1506.113
5578 | 2023-08-21 10:00 | 83.2958 | 65.03 | 20 | 10 | 0 | 20 | 2966.516
5579 | 2023-08-21 11:00 | 97.9134 | 65.03 | 1 | 0 | 9 | 11 | 162.9434
5580 | 2023-08-21 12:00 | 91.9802 | 65.03 | 10 | 0 | 0 | 11 | 1570.1019
5581 | 2023-08-21 13:00 | 92.8604 | 65.03 | 10 | 0 | 0 | 11 | 1578.9036
5582 | 2023-08-21 14:00 | 103.131 | 65.03 | 0 | 0 | 10 | 1 | 0
5583 | 2023-08-21 15:00 | 82.1165 | 65.03 | 20 | 10 | 0 | 10.5 | 2942.9309
5584 | 2023-08-21 16:00 | 85.0828 | 65.03 | 20 | 10 | 0 | 20 | 3002.2553
5585 | 2023-08-21 17:00 | 105.1113 | 66.4 | 0 | 0 | 10 | 10 | 0
5586 | 2023-08-21 18:00 | 100.0048 | 66.4 | 10 | 0 | 0 | 10 | 1664.0482
5587 | 2023-08-21 19:00 | 110.5192 | 65.03 | 0 | 0 | 10 | 0 | 0
5588 | 2023-08-21 20:00 | 82.5316 | 65.03 | 10 | 0 | 0 | 0 | 1475.6159
5589 | 2023-08-21 21:00 | 77.4603 | 65.03 | 10 | 0 | 0 | 0 | 1424.903
5590 | 2023-08-21 22:00 | 84.3965 | 65.03 | 10 | 0 | 0 | 0 | 1494.2649
5591 | 2023-08-21 23:00 | 80.2091 | 53.53 | 10 | 0 | 0 | 0 | 1337.3905
5592 | 2023-08-22 00:00 | 86.9899 | 53.53 | 10 | 0 | 0 | 0 | 1405.1994
5593 | 2023-08-22 01:00 | 82.0278 | 53.53 | 10 | 0 | 0 | 0 | 1355.5778
5594 | 2023-08-22 02:00 | 62.6076 | 53.53 | 10 | 0 | 0 | 0 | 1161.3757
5595 | 2023-08-22 03:00 | 61.4197 | 53.53 | 10 | 0 | 0 | 0 | 1149.4969
5596 | 2023-08-22 04:00 | 57.5258 | 53.53 | 20 | 10 | 0 | 9.5 | 2221.1151
5597 | 2023-08-22 05:00 | 54.0645 | 53.53 | 20 | 10 | 0 | 19 | 2151.891
5598 | 2023-08-22 06:00 | 61.1612 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1267.6398
5599 | 2023-08-22 07:00 | 76.5207 | 53.53 | 10 | 0 | 0 | 20 | 1300.5066
5600 | 2023-08-22 08:00 | 105.4037 | 65.03 | 0 | 0 | 10 | 10 | 0
5601 | 2023-08-22 09:00 | 101.2931 | 65.03 | 0 | 0 | 10 | 0 | 0
5602 | 2023-08-22 10:00 | 94.1251 | 65.03 | 10 | 0 | 0 | 0 | 1591.5506
5603 | 2023-08-22 11:00 | 91.9042 | 65.03 | 10 | 0 | 0 | 0 | 1569.3423
5604 | 2023-08-22 12:00 | 88.2472 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1694.1169
5605 | 2023-08-22 13:00 | 81.0233 | 65.03 | 20 | 10 | 0 | 10.5 | 2921.0659
5606 | 2023-08-22 14:00 | 87.3285 | 65.03 | 20 | 10 | 0 | 20 | 3047.1694
5607 | 2023-08-22 15:00 | 89.6705 | 65.03 | 10 | 0 | 0 | 20 | 1547.0049
5608 | 2023-08-22 16:00 | 90.6798 | 65.03 | 10 | 0 | 0 | 20 | 1557.0984
5609 | 2023-08-22 17:00 | 107.6799 | 66.4 | 0 | 0 | 10 | 10 | 0
5610 | 2023-08-22 18:00 | 111.8577 | 66.4 | 0 | 0 | 10 | 0 | 0
5611 | 2023-08-22 19:00 | 99.2107 | 65.03 | 10 | 0 | 0 | 0 | 1642.4067
5612 | 2023-08-22 20:00 | 79.2661 | 65.03 | 20 | 10 | 0 | 9.5 | 2885.9213
5613 | 2023-08-22 21:00 | 97.5323 | 65.03 | 0.5 | 0 | 9.5 | 0 | 81.2812
5614 | 2023-08-22 22:00 | 90.4041 | 65.03 | 10 | 0 | 0 | 0 | 1554.3406
5615 | 2023-08-22 23:00 | 76.1328 | 53.53 | 10 | 0 | 0 | 0 | 1296.6279
5616 | 2023-08-23 00:00 | 78.107 | 53.53 | 10 | 0 | 0 | 0 | 1316.3702
5617 | 2023-08-23 01:00 | 78.1397 | 53.53 | 10 | 0 | 0 | 0 | 1316.697
5618 | 2023-08-23 02:00 | 59.1362 | 53.53 | 20 | 10 | 0 | 9.5 | 2253.3247
5619 | 2023-08-23 03:00 | 62.7071 | 53.53 | 20 | 10 | 0 | 19 | 2324.742
5620 | 2023-08-23 04:00 | 87.3818 | 53.53 | 0 | 0 | 10 | 9 | 0
5621 | 2023-08-23 05:00 | 60.3628 | 53.53 | 20 | 10 | 0 | 18.5 | 2277.8554
5622 | 2023-08-23 06:00 | 64.3961 | 53.53 | 11.5789 | 1.5789 | 0 | 20 | 1365.4604
5623 | 2023-08-23 07:00 | 68.9717 | 53.53 | 10 | 0 | 0 | 20 | 1225.0172
5624 | 2023-08-23 08:00 | 85.5137 | 65.03 | 10 | 0 | 0 | 20 | 1505.437
5625 | 2023-08-23 09:00 | 100.0426 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 82.5363
5626 | 2023-08-23 10:00 | 92.1053 | 65.03 | 10 | 0 | 0 | 10.5 | 1571.3531
5627 | 2023-08-23 11:00 | 70.5985 | 65.03 | 20 | 10 | 0 | 20 | 2712.5707
5628 | 2023-08-23 12:00 | 94.5008 | 65.03 | 10 | 0 | 0 | 20 | 1595.3084
5629 | 2023-08-23 13:00 | 108.3465 | 65.03 | 0 | 0 | 10 | 10 | 0
5630 | 2023-08-23 14:00 | 77.6355 | 65.03 | 20 | 10 | 0 | 19.5 | 2853.309
5631 | 2023-08-23 15:00 | 103.3348 | 65.03 | 1 | 0 | 9 | 10.5 | 168.3648
5632 | 2023-08-23 16:00 | 74.7823 | 65.03 | 20 | 10 | 0 | 20 | 2796.2451
5633 | 2023-08-23 17:00 | 112.0229 | 66.4 | 0 | 0 | 10 | 10 | 0
5634 | 2023-08-23 18:00 | 103.8335 | 66.4 | 0 | 0 | 10 | 0 | 0
5635 | 2023-08-23 19:00 | 91.2511 | 65.03 | 10 | 0 | 0 | 0 | 1562.8113
5636 | 2023-08-23 20:00 | 87.4786 | 65.03 | 10 | 0 | 0 | 0 | 1525.0859
5637 | 2023-08-23 21:00 | 94.2069 | 65.03 | 10 | 0 | 0 | 0 | 1592.3695
5638 | 2023-08-23 22:00 | 86.782 | 65.03 | 10 | 0 | 0 | 0 | 1518.12
5639 | 2023-08-23 23:00 | 83.6928 | 53.53 | 10 | 0 | 0 | 0 | 1372.2282
5640 | 2023-08-24 00:00 | -32.8542 | 53.53 | 20 | 10 | 0 | 9.5 | 413.5152
5641 | 2023-08-24 01:00 | -27.1874 | 53.53 | 20 | 10 | 0 | 19 | 526.8512
5642 | 2023-08-24 02:00 | 64.6651 | 53.53 | 10 | 0 | 0 | 19 | 1181.9507
5643 | 2023-08-24 03:00 | 76.1567 | 53.53 | 0 | 0 | 10 | 9 | 0
5644 | 2023-08-24 04:00 | 68.9825 | 53.53 | 2 | 0 | 8 | 1 | 245.025
5645 | 2023-08-24 05:00 | 47.6686 | 53.53 | 20 | 10 | 0 | 10.5 | 2023.9718
5646 | 2023-08-24 06:00 | 49.7679 | 53.53 | 20 | 10 | 0 | 20 | 2065.9588
5647 | 2023-08-24 07:00 | 73.2947 | 53.53 | 10 | 0 | 0 | 20 | 1268.2467
5648 | 2023-08-24 08:00 | 79.4005 | 65.03 | 10 | 0 | 0 | 20 | 1444.3053
5649 | 2023-08-24 09:00 | 89.2319 | 65.03 | 10 | 0 | 0 | 20 | 1542.6194
5650 | 2023-08-24 10:00 | 92.0301 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 78.5301
5651 | 2023-08-24 11:00 | 80.1761 | 65.03 | 20 | 10 | 0 | 20 | 2904.1213
5652 | 2023-08-24 12:00 | 95.4622 | 65.03 | 0 | 0 | 10 | 10 | 0
5653 | 2023-08-24 13:00 | 93.8387 | 65.03 | 1 | 0 | 9 | 1 | 158.8687
5654 | 2023-08-24 14:00 | 85.1074 | 65.03 | 20 | 10 | 0 | 10.5 | 3002.7472
5655 | 2023-08-24 15:00 | 87.6373 | 65.03 | 10 | 0 | 0 | 10.5 | 1526.6731
5656 | 2023-08-24 16:00 | 77.8268 | 65.03 | 20 | 10 | 0 | 20 | 2857.1357
5657 | 2023-08-24 17:00 | 101.5265 | 66.4 | 10 | 0 | 0 | 20 | 1679.2651
5658 | 2023-08-24 18:00 | 103.9538 | 66.4 | 0 | 0 | 10 | 10 | 0
5659 | 2023-08-24 19:00 | 105.1965 | 65.03 | 0 | 0 | 10 | 0 | 0
5660 | 2023-08-24 20:00 | 86.9077 | 65.03 | 10 | 0 | 0 | 0 | 1519.3767
5661 | 2023-08-24 21:00 | 85.7989 | 65.03 | 10 | 0 | 0 | 0 | 1508.289
5662 | 2023-08-24 22:00 | 81.9923 | 65.03 | 10 | 0 | 0 | 0 | 1470.223
5663 | 2023-08-24 23:00 | 81.1396 | 53.53 | 10 | 0 | 0 | 0 | 1346.6961
5664 | 2023-08-25 00:00 | 87.6654 | 53.53 | 10 | 0 | 0 | 0 | 1411.9535
5665 | 2023-08-25 01:00 | 78.1922 | 53.53 | 10 | 0 | 0 | 0 | 1317.2223
5666 | 2023-08-25 02:00 | 61.3974 | 53.53 | 10 | 0 | 0 | 0 | 1149.2743
5667 | 2023-08-25 03:00 | 57.5403 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1227.6191
5668 | 2023-08-25 04:00 | 54.4892 | 53.53 | 20 | 10 | 0 | 10.5 | 2160.3837
5669 | 2023-08-25 05:00 | 63.1442 | 53.53 | 10 | 0 | 0 | 10.5 | 1166.7422
5670 | 2023-08-25 06:00 | 55.0624 | 53.53 | 20 | 10 | 0 | 20 | 2171.8488
5671 | 2023-08-25 07:00 | 81.9688 | 53.53 | 10 | 0 | 0 | 20 | 1354.9883
5672 | 2023-08-25 08:00 | 89.1111 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 77.0706
5673 | 2023-08-25 09:00 | 86.7196 | 65.03 | 10 | 0 | 0 | 10.5 | 1517.4963
5674 | 2023-08-25 10:00 | 86.5545 | 65.03 | 10 | 0 | 0 | 10.5 | 1515.8449
5675 | 2023-08-25 11:00 | 85.3636 | 65.03 | 10 | 0 | 0 | 10.5 | 1503.9365
5676 | 2023-08-25 12:00 | 79.1568 | 65.03 | 20 | 10 | 0 | 20 | 2883.7357
5677 | 2023-08-25 13:00 | 91.9415 | 65.03 | 10 | 0 | 0 | 20 | 1569.7145
5678 | 2023-08-25 14:00 | 90.6966 | 65.03 | 10 | 0 | 0 | 20 | 1557.2664
5679 | 2023-08-25 15:00 | 96.1567 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 80.5933
5680 | 2023-08-25 16:00 | 85.2139 | 65.03 | 20 | 10 | 0 | 20 | 3004.8779
5681 | 2023-08-25 17:00 | 123.0438 | 66.4 | 0 | 0 | 10 | 10 | 0
5682 | 2023-08-25 18:00 | 101.2065 | 66.4 | 0 | 0 | 10 | 0 | 0
5683 | 2023-08-25 19:00 | 98.1258 | 65.03 | 10 | 0 | 0 | 0 | 1631.5583
5684 | 2023-08-25 20:00 | 77.4539 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1499.8303
5685 | 2023-08-25 21:00 | 73.7587 | 65.03 | 20 | 10 | 0 | 10 | 2775.7739
5686 | 2023-08-25 22:00 | 98.4918 | 65.03 | 0 | 0 | 10 | 0 | 0
5687 | 2023-08-25 23:00 | 91.6185 | 53.53 | 10 | 0 | 0 | 0 | 1451.4852
5688 | 2023-08-26 00:00 | 75.8354 | 53.53 | 10 | 0 | 0 | 0 | 1293.6543
5689 | 2023-08-26 01:00 | 65.0052 | 53.53 | 10 | 0 | 0 | 0 | 1185.352
5690 | 2023-08-26 02:00 | 68.9437 | 53.53 | 10 | 0 | 0 | 0 | 1224.7374
5691 | 2023-08-26 03:00 | 48.3948 | 53.53 | 20 | 10 | 0 | 9.5 | 2038.4963
5692 | 2023-08-26 04:00 | 48.9599 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1078.8409
5693 | 2023-08-26 05:00 | 64.375 | 53.53 | 0 | 0 | 10 | 0 | 0
5694 | 2023-08-26 06:00 | -31.0492 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 248.4725
5695 | 2023-08-26 07:00 | -57.9547 | 53.53 | 20 | 10 | 0 | 10.5 | -88.4941
5696 | 2023-08-26 08:00 | -34.3825 | 53.53 | 20 | 10 | 0 | 20 | 382.9498
5697 | 2023-08-26 09:00 | 78.0911 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 65.8105
5698 | 2023-08-26 10:00 | 76.7062 | 53.53 | 10 | 0 | 0 | 10.5 | 1302.3624
5699 | 2023-08-26 11:00 | 70.2631 | 53.53 | 20 | 10 | 0 | 20 | 2475.861
5700 | 2023-08-26 12:00 | 78.8938 | 53.53 | 10 | 0 | 0 | 20 | 1324.2377
5701 | 2023-08-26 13:00 | 91.1408 | 53.53 | 0 | 0 | 10 | 10 | 0
5702 | 2023-08-26 14:00 | 85.8183 | 53.53 | 10 | 0 | 0 | 10 | 1393.4827
5703 | 2023-08-26 15:00 | 81.0511 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1416.643
5704 | 2023-08-26 16:00 | 74.4469 | 53.53 | 20 | 10 | 0 | 20 | 2559.5386
5705 | 2023-08-26 17:00 | 97.6591 | 53.53 | 10 | 0 | 0 | 20 | 1511.891
5706 | 2023-08-26 18:00 | 104.7748 | 53.53 | 0 | 0 | 10 | 10 | 0
5707 | 2023-08-26 19:00 | 99.3467 | 53.53 | 0 | 0 | 10 | 0 | 0
5708 | 2023-08-26 20:00 | 77.1806 | 53.53 | 10 | 0 | 0 | 0 | 1307.1062
5709 | 2023-08-26 21:00 | 70.582 | 53.53 | 20 | 10 | 0 | 9.5 | 2482.2392
5710 | 2023-08-26 22:00 | 83.3266 | 53.53 | 0.5 | 0 | 9.5 | 0 | 68.4283
5711 | 2023-08-26 23:00 | 55.6682 | 53.53 | 20 | 10 | 0 | 9.5 | 2183.9638
5712 | 2023-08-27 00:00 | 73.941 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1341.8004
5713 | 2023-08-27 01:00 | 99.9517 | 53.53 | 0 | 0 | 10 | 0 | 0
5714 | 2023-08-27 02:00 | 41.799 | 53.53 | 20 | 10 | 0 | 9.5 | 1906.5803
5715 | 2023-08-27 03:00 | 49.152 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1134.9066
5716 | 2023-08-27 04:00 | 50.839 | 53.53 | 10 | 0 | 0 | 10.5 | 1043.6904
5717 | 2023-08-27 05:00 | 47.6589 | 53.53 | 20 | 10 | 0 | 20 | 2023.7781
5718 | 2023-08-27 06:00 | 60.015 | 53.53 | 10 | 0 | 0 | 20 | 1135.4504
5719 | 2023-08-27 07:00 | 74.7051 | 53.53 | 10 | 0 | 0 | 20 | 1282.351
5720 | 2023-08-27 08:00 | 82.0671 | 53.53 | 10 | 0 | 0 | 20 | 1355.9706
5721 | 2023-08-27 09:00 | 87.6535 | 53.53 | 1 | 0 | 9 | 11 | 141.1835
5722 | 2023-08-27 10:00 | 81.0243 | 53.53 | 10 | 0 | 0 | 11 | 1345.5425
5723 | 2023-08-27 11:00 | 120.7975 | 53.53 | 0 | 0 | 10 | 1 | 0
5724 | 2023-08-27 12:00 | 82.0596 | 53.53 | 10 | 0 | 0 | 1 | 1355.8957
5725 | 2023-08-27 13:00 | 82.4067 | 53.53 | 10 | 0 | 0 | 1 | 1359.3667
5726 | 2023-08-27 14:00 | 70.8636 | 53.53 | 20 | 10 | 0 | 10.5 | 2487.8725
5727 | 2023-08-27 15:00 | 77.1373 | 53.53 | 20 | 10 | 0 | 20 | 2613.3468
5728 | 2023-08-27 16:00 | 91.1703 | 53.53 | 0 | 0 | 10 | 10 | 0
5729 | 2023-08-27 17:00 | 87.6456 | 53.53 | 10 | 0 | 0 | 10 | 1411.7563
5730 | 2023-08-27 18:00 | 83.9852 | 53.53 | 10 | 0 | 0 | 10 | 1375.1517
5731 | 2023-08-27 19:00 | 96.1419 | 53.53 | 0 | 0 | 10 | 0 | 0
5732 | 2023-08-27 20:00 | 88.6149 | 53.53 | 10 | 0 | 0 | 0 | 1421.4486
5733 | 2023-08-27 21:00 | 76.2182 | 53.53 | 10 | 0 | 0 | 0 | 1297.4819
5734 | 2023-08-27 22:00 | 73.5003 | 53.53 | 20 | 10 | 0 | 9.5 | 2540.6061
5735 | 2023-08-27 23:00 | 60.2136 | 53.53 | 20 | 10 | 0 | 19 | 2274.8723
5736 | 2023-08-28 00:00 | 82.5311 | 53.53 | 1 | 0 | 9 | 10 | 136.0611
5737 | 2023-08-28 01:00 | 84.384 | 53.53 | 0 | 0 | 10 | 0 | 0
5738 | 2023-08-28 02:00 | 48.5471 | 53.53 | 20 | 10 | 0 | 9.5 | 2041.5414
5739 | 2023-08-28 03:00 | 69.0346 | 53.53 | 10 | 0 | 0 | 9.5 | 1225.6463
5740 | 2023-08-28 04:00 | 65.3541 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1313.9826
5741 | 2023-08-28 05:00 | 69.0113 | 53.53 | 10 | 0 | 0 | 10.5 | 1225.4128
5742 | 2023-08-28 06:00 | 63.6812 | 53.53 | 20 | 10 | 0 | 20 | 2344.2235
5743 | 2023-08-28 07:00 | 84.3147 | 53.53 | 10 | 0 | 0 | 20 | 1378.4467
5744 | 2023-08-28 08:00 | 93.1253 | 65.03 | 0 | 0 | 10 | 10 | 0
5745 | 2023-08-28 09:00 | 96.3391 | 65.03 | 0 | 0 | 10 | 0 | 0
5746 | 2023-08-28 10:00 | 78.3853 | 65.03 | 20 | 10 | 0 | 9.5 | 2868.3052
5747 | 2023-08-28 11:00 | 79.8339 | 65.03 | 20 | 10 | 0 | 19 | 2897.2789
5748 | 2023-08-28 12:00 | 83.9452 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1646.5678
5749 | 2023-08-28 13:00 | 87.9434 | 65.03 | 10 | 0 | 0 | 20 | 1529.7337
5750 | 2023-08-28 14:00 | 91.9856 | 65.03 | 10 | 0 | 0 | 20 | 1570.1559
5751 | 2023-08-28 15:00 | 91.456 | 65.03 | 10 | 0 | 0 | 20 | 1564.8596
5752 | 2023-08-28 16:00 | 98.8514 | 65.03 | 10 | 0 | 0 | 20 | 1638.8142
5753 | 2023-08-28 17:00 | 114.1821 | 66.4 | 0 | 0 | 10 | 10 | 0
5754 | 2023-08-28 18:00 | 98.1416 | 66.4 | 10 | 0 | 0 | 10 | 1645.4155
5755 | 2023-08-28 19:00 | 105.7532 | 65.03 | 0 | 0 | 10 | 0 | 0
5756 | 2023-08-28 20:00 | 78.2838 | 65.03 | 20 | 10 | 0 | 9.5 | 2866.2765
5757 | 2023-08-28 21:00 | 82.5256 | 65.03 | 10 | 0 | 0 | 9.5 | 1475.5558
5758 | 2023-08-28 22:00 | 86.4321 | 65.03 | 1 | 0 | 9 | 0.5 | 151.4621
5759 | 2023-08-28 23:00 | 62.8896 | 53.53 | 20 | 10 | 0 | 10 | 2328.393
5760 | 2023-08-29 00:00 | 105.4327 | 53.53 | 0 | 0 | 10 | 0 | 0
5761 | 2023-08-29 01:00 | 83.5286 | 53.53 | 10 | 0 | 0 | 0 | 1370.5863
5762 | 2023-08-29 02:00 | 54.807 | 53.53 | 20 | 10 | 0 | 9.5 | 2166.7399
5763 | 2023-08-29 03:00 | 78.4695 | 53.53 | 0.5 | 0 | 9.5 | 0 | 65.9997
5764 | 2023-08-29 04:00 | 56.4238 | 53.53 | 20 | 10 | 0 | 9.5 | 2199.0754
5765 | 2023-08-29 05:00 | 59.9122 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1253.8351
5766 | 2023-08-29 06:00 | 55.4993 | 53.53 | 20 | 10 | 0 | 20 | 2180.5868
5767 | 2023-08-29 07:00 | 94.9353 | 53.53 | 10 | 0 | 0 | 20 | 1484.6528
5768 | 2023-08-29 08:00 | 88.1232 | 65.03 | 10 | 0 | 0 | 20 | 1531.5319
5769 | 2023-08-29 09:00 | 90.045 | 65.03 | 10 | 0 | 0 | 20 | 1550.7496
5770 | 2023-08-29 10:00 | 99.7722 | 65.03 | 0 | 0 | 10 | 10 | 0
5771 | 2023-08-29 11:00 | 93.6956 | 65.03 | 10 | 0 | 0 | 10 | 1587.256
5772 | 2023-08-29 12:00 | 88.494 | 65.03 | 20 | 10 | 0 | 19.5 | 3070.48
5773 | 2023-08-29 13:00 | 98.7811 | 65.03 | 10 | 0 | 0 | 19.5 | 1638.1108
5774 | 2023-08-29 14:00 | 117.4379 | 65.03 | 0 | 0 | 10 | 9.5 | 0
5775 | 2023-08-29 15:00 | 91.3959 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1728.918
5776 | 2023-08-29 16:00 | 89.7895 | 65.03 | 20 | 10 | 0 | 20 | 3096.3905
5777 | 2023-08-29 17:00 | 105.2113 | 66.4 | 0 | 0 | 10 | 10 | 0
5778 | 2023-08-29 18:00 | 115.9385 | 66.4 | 0 | 0 | 10 | 0 | 0
5779 | 2023-08-29 19:00 | 99.7851 | 65.03 | 10 | 0 | 0 | 0 | 1648.1509
5780 | 2023-08-29 20:00 | 81.8957 | 65.03 | 10 | 0 | 0 | 0 | 1469.2569
5781 | 2023-08-29 21:00 | 74.661 | 65.03 | 10 | 0 | 0 | 0 | 1396.9095
5782 | 2023-08-29 22:00 | 76.4248 | 65.03 | 10 | 0 | 0 | 0 | 1414.5483
5783 | 2023-08-29 23:00 | 75.3014 | 53.53 | 20 | 10 | 0 | 9.5 | 2576.6281
5784 | 2023-08-30 00:00 | 78.4823 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1389.6029
5785 | 2023-08-30 01:00 | 96.4024 | 53.53 | 0 | 0 | 10 | 0 | 0
5786 | 2023-08-30 02:00 | 63.2595 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1290.8312
5787 | 2023-08-30 03:00 | 52.9138 | 53.53 | 20 | 10 | 0 | 10.5 | 2128.8753
5788 | 2023-08-30 04:00 | -23.472 | 53.53 | 20 | 10 | 0 | 20 | 601.1593
5789 | 2023-08-30 05:00 | 71.6602 | 53.53 | 10 | 0 | 0 | 20 | 1251.902
5790 | 2023-08-30 06:00 | 68.9512 | 53.53 | 10 | 0 | 0 | 20 | 1224.8123
5791 | 2023-08-30 07:00 | 79.1103 | 53.53 | 10 | 0 | 0 | 20 | 1326.4032
5792 | 2023-08-30 08:00 | 85.7902 | 65.03 | 10 | 0 | 0 | 20 | 1508.2023
5793 | 2023-08-30 09:00 | 98.9336 | 65.03 | 0 | 0 | 10 | 10 | 0
5794 | 2023-08-30 10:00 | 82.4559 | 65.03 | 20 | 10 | 0 | 19.5 | 2949.7175
5795 | 2023-08-30 11:00 | 92.0184 | 65.03 | 10 | 0 | 0 | 19.5 | 1570.4842
5796 | 2023-08-30 12:00 | 113.334 | 65.03 | 0 | 0 | 10 | 9.5 | 0
5797 | 2023-08-30 13:00 | 90.4869 | 65.03 | 10 | 0 | 0 | 9.5 | 1555.1691
5798 | 2023-08-30 14:00 | 83.7084 | 65.03 | 20 | 10 | 0 | 19 | 2974.7685
5799 | 2023-08-30 15:00 | 92.1735 | 65.03 | 10 | 0 | 0 | 19 | 1572.0354
5800 | 2023-08-30 16:00 | 85.6105 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1664.9737
5801 | 2023-08-30 17:00 | 95.3535 | 66.4 | 10 | 0 | 0 | 20 | 1617.535
5802 | 2023-08-30 18:00 | 109.7498 | 66.4 | 0 | 0 | 10 | 10 | 0
5803 | 2023-08-30 19:00 | 113.8591 | 65.03 | 0 | 0 | 10 | 0 | 0
5804 | 2023-08-30 20:00 | 81.6719 | 65.03 | 10 | 0 | 0 | 0 | 1467.0195
5805 | 2023-08-30 21:00 | 81.2233 | 65.03 | 10 | 0 | 0 | 0 | 1462.5326
5806 | 2023-08-30 22:00 | 77.6335 | 65.03 | 10 | 0 | 0 | 0 | 1426.6355
5807 | 2023-08-30 23:00 | 77.7987 | 53.53 | 10 | 0 | 0 | 0 | 1313.287
5808 | 2023-08-31 00:00 | 75.0171 | 53.53 | 10 | 0 | 0 | 0 | 1285.4714
5809 | 2023-08-31 01:00 | -10.5528 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 475.0109
5810 | 2023-08-31 02:00 | -50.6224 | 53.53 | 20 | 10 | 0 | 10.5 | 58.1524
5811 | 2023-08-31 03:00 | -54.9857 | 53.53 | 20 | 10 | 0 | 20 | -29.1138
5812 | 2023-08-31 04:00 | 63.5819 | 53.53 | 10 | 0 | 0 | 20 | 1171.119
5813 | 2023-08-31 05:00 | 66.4847 | 53.53 | 10 | 0 | 0 | 20 | 1200.1473
5814 | 2023-08-31 06:00 | 65.4046 | 53.53 | 10 | 0 | 0 | 20 | 1189.3458
5815 | 2023-08-31 07:00 | 75.9843 | 53.53 | 10 | 0 | 0 | 20 | 1295.1428
5816 | 2023-08-31 08:00 | 91.0283 | 65.03 | 10 | 0 | 0 | 20 | 1560.5835
5817 | 2023-08-31 09:00 | 86.9599 | 65.03 | 10 | 0 | 0 | 20 | 1519.8985
5818 | 2023-08-31 10:00 | 92.4129 | 65.03 | 0 | 0 | 10 | 10 | 0
5819 | 2023-08-31 11:00 | 91.5969 | 65.03 | 1 | 0 | 9 | 1 | 156.6269
5820 | 2023-08-31 12:00 | 86.187 | 65.03 | 10 | 0 | 0 | 1 | 1512.1696
5821 | 2023-08-31 13:00 | 80.6766 | 65.03 | 20 | 10 | 0 | 10.5 | 2914.1321
5822 | 2023-08-31 14:00 | 90.0195 | 65.03 | 10 | 0 | 0 | 10.5 | 1550.495
5823 | 2023-08-31 15:00 | 87.4123 | 65.03 | 10 | 0 | 0 | 10.5 | 1524.4228
5824 | 2023-08-31 16:00 | 78.0773 | 65.03 | 20 | 10 | 0 | 20 | 2862.1467
5825 | 2023-08-31 17:00 | 108.011 | 66.4 | 10 | 0 | 0 | 20 | 1744.11
5826 | 2023-08-31 18:00 | 112.2957 | 66.4 | 0 | 0 | 10 | 10 | 0
5827 | 2023-08-31 19:00 | 132.2755 | 65.03 | 0 | 0 | 10 | 0 | 0
5828 | 2023-08-31 20:00 | 81.1299 | 65.03 | 10 | 0 | 0 | 0 | 1461.5995
5829 | 2023-08-31 21:00 | 80.1676 | 65.03 | 10 | 0 | 0 | 0 | 1451.9755
5830 | 2023-08-31 22:00 | 76.8207 | 65.03 | 10 | 0 | 0 | 0 | 1418.5067
5831 | 2023-08-31 23:00 | 80.5131 | 53.53 | 20 | 10 | 0 | 9.5 | 2680.8626
5832 | 2023-09-01 00:00 | 95.4627 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.4963
5833 | 2023-09-01 01:00 | 88.4975 | 53.53 | 10 | 0 | 0 | 0 | 1420.2747
5834 | 2023-09-01 02:00 | 72.6202 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1327.8965
5835 | 2023-09-01 03:00 | 62.7067 | 53.53 | 20 | 10 | 0 | 10 | 2324.7339
5836 | 2023-09-01 04:00 | 81.9076 | 53.53 | 0 | 0 | 10 | 0 | 0
5837 | 2023-09-01 05:00 | -23.4624 | 53.53 | 20 | 10 | 0 | 9.5 | 601.3527
5838 | 2023-09-01 06:00 | -13.0064 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 447.8929
5839 | 2023-09-01 07:00 | -25.0892 | 53.53 | 20 | 10 | 0 | 20 | 568.816
5840 | 2023-09-01 08:00 | 99.8909 | 65.03 | 10 | 0 | 0 | 20 | 1649.209
5841 | 2023-09-01 09:00 | 101.8869 | 65.03 | 10 | 0 | 0 | 20 | 1669.1691
5842 | 2023-09-01 10:00 | 103.8138 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 84.4219
5843 | 2023-09-01 11:00 | -60.9659 | 65.03 | 20 | 10 | 0 | 20 | 81.2813
5844 | 2023-09-01 12:00 | 117.396 | 65.03 | 10 | 0 | 0 | 20 | 1824.26
5845 | 2023-09-01 13:00 | 110.0444 | 65.03 | 10 | 0 | 0 | 20 | 1750.7441
5846 | 2023-09-01 14:00 | 112.2639 | 65.03 | 10 | 0 | 0 | 20 | 1772.939
5847 | 2023-09-01 15:00 | 117.4773 | 65.03 | 10 | 0 | 0 | 20 | 1825.0727
5848 | 2023-09-01 16:00 | 108.558 | 65.03 | 10 | 0 | 0 | 20 | 1735.8798
5849 | 2023-09-01 17:00 | 118.6245 | 66.4 | 10 | 0 | 0 | 20 | 1850.2451
5850 | 2023-09-01 18:00 | 127.7372 | 66.4 | 0 | 0 | 10 | 10 | 0
5851 | 2023-09-01 19:00 | 128.3921 | 65.03 | 0 | 0 | 10 | 0 | 0
5852 | 2023-09-01 20:00 | 104.268 | 65.03 | 10 | 0 | 0 | 0 | 1692.9801
5853 | 2023-09-01 21:00 | 90.0575 | 65.03 | 10 | 0 | 0 | 0 | 1550.8747
5854 | 2023-09-01 22:00 | 93.3209 | 65.03 | 10 | 0 | 0 | 0 | 1583.5091
5855 | 2023-09-01 23:00 | 91.9196 | 53.53 | 10 | 0 | 0 | 0 | 1454.496
5856 | 2023-09-02 00:00 | 92.4858 | 53.53 | 10 | 0 | 0 | 0 | 1460.1583
5857 | 2023-09-02 01:00 | 85.7387 | 53.53 | 10 | 0 | 0 | 0 | 1392.6872
5858 | 2023-09-02 02:00 | 76.0593 | 53.53 | 20 | 10 | 0 | 9.5 | 2591.7853
5859 | 2023-09-02 03:00 | 77.992 | 53.53 | 10 | 0 | 0 | 9.5 | 1315.2199
5860 | 2023-09-02 04:00 | 76.7226 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1439.6343
5861 | 2023-09-02 05:00 | 76.7912 | 53.53 | 10 | 0 | 0 | 10.5 | 1303.2115
5862 | 2023-09-02 06:00 | 59.2144 | 53.53 | 20 | 10 | 0 | 20 | 2254.8871
5863 | 2023-09-02 07:00 | 89.7932 | 53.53 | 10 | 0 | 0 | 20 | 1433.2325
5864 | 2023-09-02 08:00 | 91.7329 | 53.53 | 10 | 0 | 0 | 20 | 1452.6295
5865 | 2023-09-02 09:00 | 86.1418 | 53.53 | 10 | 0 | 0 | 20 | 1396.7185
5866 | 2023-09-02 10:00 | 93.8326 | 53.53 | 10 | 0 | 0 | 20 | 1473.6263
5867 | 2023-09-02 11:00 | 108.0979 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 80.8139
5868 | 2023-09-02 12:00 | 99.6041 | 53.53 | 20 | 10 | 0 | 20 | 3062.6817
5869 | 2023-09-02 13:00 | 116.6953 | 53.53 | 0 | 0 | 10 | 10 | 0
5870 | 2023-09-02 14:00 | 97.2635 | 53.53 | 20 | 10 | 0 | 19.5 | 3015.8701
5871 | 2023-09-02 15:00 | 123.001 | 53.53 | 0 | 0 | 10 | 9.5 | 0
5872 | 2023-09-02 16:00 | 97.2658 | 53.53 | 20 | 10 | 0 | 19 | 3015.9161
5873 | 2023-09-02 17:00 | 111.0675 | 53.53 | 1 | 0 | 9 | 10 | 164.5975
5874 | 2023-09-02 18:00 | 102.9297 | 53.53 | 10 | 0 | 0 | 10 | 1564.5971
5875 | 2023-09-02 19:00 | 120.7829 | 53.53 | 0 | 0 | 10 | 0 | 0
5876 | 2023-09-02 20:00 | 87.4023 | 53.53 | 20 | 10 | 0 | 9.5 | 2818.6458
5877 | 2023-09-02 21:00 | 86.4874 | 53.53 | 20 | 10 | 0 | 19 | 2800.348
5878 | 2023-09-02 22:00 | 102.6155 | 53.53 | 0 | 0 | 10 | 9 | 0
5879 | 2023-09-02 23:00 | 96.2852 | 53.53 | 1 | 0 | 9 | 0 | 149.8152
5880 | 2023-09-03 00:00 | 96.0085 | 53.53 | 10 | 0 | 0 | 0 | 1495.3849
5881 | 2023-09-03 01:00 | 83.3242 | 53.53 | 10 | 0 | 0 | 0 | 1368.5425
5882 | 2023-09-03 02:00 | 65.5189 | 53.53 | 20 | 10 | 0 | 9.5 | 2380.9779
5883 | 2023-09-03 03:00 | 65.4534 | 53.53 | 20 | 10 | 0 | 19 | 2379.6681
5884 | 2023-09-03 04:00 | 72.5133 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1393.1101
5885 | 2023-09-03 05:00 | 80.7412 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 67.1356
5886 | 2023-09-03 06:00 | 68.8177 | 53.53 | 20 | 10 | 0 | 20 | 2446.953
5887 | 2023-09-03 07:00 | 106.1094 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 79.8197
5888 | 2023-09-03 08:00 | 103.6199 | 53.53 | 10 | 0 | 0 | 10.5 | 1571.4986
5889 | 2023-09-03 09:00 | 94.1979 | 53.53 | 20 | 10 | 0 | 20 | 2954.558
5890 | 2023-09-03 10:00 | 102.9545 | 53.53 | 10 | 0 | 0 | 20 | 1564.8446
5891 | 2023-09-03 11:00 | 112.6048 | 53.53 | 0 | 0 | 10 | 10 | 0
5892 | 2023-09-03 12:00 | 116.4279 | 53.53 | 0 | 0 | 10 | 0 | 0
5893 | 2023-09-03 13:00 | 106.5909 | 53.53 | 10 | 0 | 0 | 0 | 1601.209
5894 | 2023-09-03 14:00 | 96.0916 | 53.53 | 10 | 0 | 0 | 0 | 1496.2161
5895 | 2023-09-03 15:00 | 94.3248 | 53.53 | 10 | 0 | 0 | 0 | 1478.5481
5896 | 2023-09-03 16:00 | 100.6146 | 53.53 | 10 | 0 | 0 | 0 | 1541.4463
5897 | 2023-09-03 17:00 | -5.537 | 53.53 | 20 | 10 | 0 | 9.5 | 959.8596
5898 | 2023-09-03 18:00 | -69.3467 | 53.53 | 20 | 10 | 0 | 19 | -316.3348
5899 | 2023-09-03 19:00 | 114.5507 | 53.53 | 0 | 0 | 10 | 9 | 0
5900 | 2023-09-03 20:00 | 91.2868 | 53.53 | 10 | 0 | 0 | 9 | 1448.1678
5901 | 2023-09-03 21:00 | 88.5562 | 53.53 | 10 | 0 | 0 | 9 | 1420.862
5902 | 2023-09-03 22:00 | 89.7114 | 53.53 | 10 | 0 | 0 | 9 | 1432.414
5903 | 2023-09-03 23:00 | 86.9349 | 53.53 | 11.0526 | 1.0526 | 0 | 10 | 1552.507
5904 | 2023-09-04 00:00 | 110.7573 | 53.53 | 0 | 0 | 10 | 0 | 0
5905 | 2023-09-04 01:00 | 92.1636 | 53.53 | 10 | 0 | 0 | 0 | 1456.9358
5906 | 2023-09-04 02:00 | 74.296 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1480.0908
5907 | 2023-09-04 03:00 | 68.1821 | 53.53 | 20 | 10 | 0 | 11 | 2434.241
5908 | 2023-09-04 04:00 | 79.8945 | 53.53 | 10 | 0 | 0 | 11 | 1334.2452
5909 | 2023-09-04 05:00 | 86.5689 | 53.53 | 0 | 0 | 10 | 1 | 0
5910 | 2023-09-04 06:00 | -44.8693 | 53.53 | 20 | 10 | 0 | 10.5 | 173.2132
5911 | 2023-09-04 07:00 | -65.8261 | 53.53 | 20 | 10 | 0 | 20 | -245.9215
5912 | 2023-09-04 08:00 | 108.5993 | 65.03 | 10 | 0 | 0 | 20 | 1736.2935
5913 | 2023-09-04 09:00 | 102.7728 | 65.03 | 10 | 0 | 0 | 20 | 1678.028
5914 | 2023-09-04 10:00 | 108.1893 | 65.03 | 10 | 0 | 0 | 20 | 1732.1934
5915 | 2023-09-04 11:00 | 106.3675 | 65.03 | 10 | 0 | 0 | 20 | 1713.9751
5916 | 2023-09-04 12:00 | 104.3391 | 65.03 | 10 | 0 | 0 | 20 | 1693.6913
5917 | 2023-09-04 13:00 | 104.9531 | 65.03 | 10 | 0 | 0 | 20 | 1699.831
5918 | 2023-09-04 14:00 | 107.5282 | 65.03 | 10 | 0 | 0 | 20 | 1725.5823
5919 | 2023-09-04 15:00 | 101.7867 | 65.03 | 10 | 0 | 0 | 20 | 1668.167
5920 | 2023-09-04 16:00 | 102.1442 | 65.03 | 10 | 0 | 0 | 20 | 1671.7416
5921 | 2023-09-04 17:00 | 135.6226 | 66.4 | 0 | 0 | 10 | 10 | 0
5922 | 2023-09-04 18:00 | 150.2741 | 66.4 | 0 | 0 | 10 | 0 | 0
5923 | 2023-09-04 19:00 | 111.3174 | 65.03 | 10 | 0 | 0 | 0 | 1763.4738
5924 | 2023-09-04 20:00 | 91.0318 | 65.03 | 10 | 0 | 0 | 0 | 1560.6179
5925 | 2023-09-04 21:00 | 92.6584 | 65.03 | 10 | 0 | 0 | 0 | 1576.8836
5926 | 2023-09-04 22:00 | 98.1355 | 65.03 | 10 | 0 | 0 | 0 | 1631.6552
5927 | 2023-09-04 23:00 | 101.606 | 53.53 | 10 | 0 | 0 | 0 | 1551.3599
5928 | 2023-09-05 00:00 | 98.7503 | 53.53 | 10 | 0 | 0 | 0 | 1522.803
5929 | 2023-09-05 01:00 | 95.2224 | 53.53 | 10 | 0 | 0 | 0 | 1487.5241
5930 | 2023-09-05 02:00 | 78.1974 | 53.53 | 10 | 0 | 0 | 0 | 1317.274
5931 | 2023-09-05 03:00 | 69.2111 | 53.53 | 20 | 10 | 0 | 9.5 | 2454.8216
5932 | 2023-09-05 04:00 | 72.1328 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1388.9049
5933 | 2023-09-05 05:00 | 73.7481 | 53.53 | 10 | 0 | 0 | 10.5 | 1272.7805
5934 | 2023-09-05 06:00 | 64.4413 | 53.53 | 20 | 10 | 0 | 20 | 2359.4263
5935 | 2023-09-05 07:00 | 86.5438 | 53.53 | 10 | 0 | 0 | 20 | 1400.7384
5936 | 2023-09-05 08:00 | 96.7555 | 65.03 | 10 | 0 | 0 | 20 | 1617.8549
5937 | 2023-09-05 09:00 | 110.3392 | 65.03 | 0 | 0 | 10 | 10 | 0
5938 | 2023-09-05 10:00 | 105.8079 | 65.03 | 10 | 0 | 0 | 10 | 1708.3788
5939 | 2023-09-05 11:00 | 108.9282 | 65.03 | 1 | 0 | 9 | 1 | 173.9582
5940 | 2023-09-05 12:00 | 93.2947 | 65.03 | 20 | 10 | 0 | 10.5 | 3166.4945
5941 | 2023-09-05 13:00 | 94.9178 | 65.03 | 20 | 10 | 0 | 20 | 3198.9558
5942 | 2023-09-05 14:00 | 109.4018 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.2159
5943 | 2023-09-05 15:00 | 89.7604 | 65.03 | 20 | 10 | 0 | 20 | 3095.8071
5944 | 2023-09-05 16:00 | 114.9973 | 65.03 | 10 | 0 | 0 | 20 | 1800.2729
5945 | 2023-09-05 17:00 | 108.3655 | 66.4 | 10 | 0 | 0 | 20 | 1747.6546
5946 | 2023-09-05 18:00 | 126.0955 | 66.4 | 0 | 0 | 10 | 10 | 0
5947 | 2023-09-05 19:00 | 113.0483 | 65.03 | 10 | 0 | 0 | 10 | 1780.7826
5948 | 2023-09-05 20:00 | 108.1435 | 65.03 | 10 | 0 | 0 | 10 | 1731.7352
5949 | 2023-09-05 21:00 | 139.3508 | 65.03 | 0 | 0 | 10 | 0 | 0
5950 | 2023-09-05 22:00 | 86.539 | 65.03 | 10 | 0 | 0 | 0 | 1515.6902
5951 | 2023-09-05 23:00 | 99.6975 | 53.53 | 10 | 0 | 0 | 0 | 1532.2751
5952 | 2023-09-06 00:00 | 83.4314 | 53.53 | 20 | 10 | 0 | 9.5 | 2739.2276
5953 | 2023-09-06 01:00 | 97.313 | 53.53 | 0.5 | 0 | 9.5 | 0 | 75.4215
5954 | 2023-09-06 02:00 | 72.3946 | 53.53 | 20 | 10 | 0 | 9.5 | 2518.4927
5955 | 2023-09-06 03:00 | 74.8909 | 53.53 | 10 | 0 | 0 | 9.5 | 1284.2087
5956 | 2023-09-06 04:00 | 67.916 | 53.53 | 20 | 10 | 0 | 19 | 2428.9201
5957 | 2023-09-06 05:00 | 80.4945 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 201.0368
5958 | 2023-09-06 06:00 | 65.0879 | 53.53 | 20 | 10 | 0 | 20 | 2372.3579
5959 | 2023-09-06 07:00 | 105.1819 | 53.53 | 10 | 0 | 0 | 20 | 1587.1195
5960 | 2023-09-06 08:00 | 101.0099 | 65.03 | 10 | 0 | 0 | 20 | 1660.3987
5961 | 2023-09-06 09:00 | 95.3112 | 65.03 | 10 | 0 | 0 | 20 | 1603.4122
5962 | 2023-09-06 10:00 | 119.2388 | 65.03 | 0 | 0 | 10 | 10 | 0
5963 | 2023-09-06 11:00 | 103.3983 | 65.03 | 20 | 10 | 0 | 19.5 | 3368.5661
5964 | 2023-09-06 12:00 | 123.2064 | 65.03 | 0 | 0 | 10 | 9.5 | 0
5965 | 2023-09-06 13:00 | 114.9619 | 65.03 | 0.5 | 0 | 9.5 | 0 | 89.9959
5966 | 2023-09-06 14:00 | 98.5749 | 65.03 | 20 | 10 | 0 | 9.5 | 3272.0989
5967 | 2023-09-06 15:00 | 103.2689 | 65.03 | 20 | 10 | 0 | 19 | 3365.9788
5968 | 2023-09-06 16:00 | 104.8228 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1877.3201
5969 | 2023-09-06 17:00 | 133.4167 | 66.4 | 0 | 0 | 10 | 10 | 0
5970 | 2023-09-06 18:00 | 122.4048 | 66.4 | 0 | 0 | 10 | 0 | 0
5971 | 2023-09-06 19:00 | 120.2561 | 65.03 | 10 | 0 | 0 | 0 | 1852.8609
5972 | 2023-09-06 20:00 | 97.4433 | 65.03 | 20 | 10 | 0 | 9.5 | 3249.4654
5973 | 2023-09-06 21:00 | 98.522 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1721.5999
5974 | 2023-09-06 22:00 | 110.8737 | 65.03 | 0 | 0 | 10 | 0 | 0
5975 | 2023-09-06 23:00 | 93.9261 | 53.53 | 10 | 0 | 0 | 0 | 1474.5611
5976 | 2023-09-07 00:00 | -48.6912 | 53.53 | 20 | 10 | 0 | 9.5 | 96.7752
5977 | 2023-09-07 01:00 | 90.0036 | 53.53 | 0.5 | 0 | 9.5 | 0 | 71.7668
5978 | 2023-09-07 02:00 | 70.0717 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1366.1243
5979 | 2023-09-07 03:00 | 65.3142 | 53.53 | 20 | 10 | 0 | 10.5 | 2376.883
5980 | 2023-09-07 04:00 | 68.859 | 53.53 | 20 | 10 | 0 | 20 | 2447.7793
5981 | 2023-09-07 05:00 | 88.0875 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 70.8088
5982 | 2023-09-07 06:00 | 72.3959 | 53.53 | 20 | 10 | 0 | 20 | 2518.5171
5983 | 2023-09-07 07:00 | 99.7811 | 53.53 | 10 | 0 | 0 | 20 | 1533.111
5984 | 2023-09-07 08:00 | 90.783 | 65.03 | 10 | 0 | 0 | 20 | 1558.1297
5985 | 2023-09-07 09:00 | 108.5456 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 86.7878
5986 | 2023-09-07 10:00 | 102.717 | 65.03 | 10 | 0 | 0 | 10.5 | 1677.4698
5987 | 2023-09-07 11:00 | 100.5362 | 65.03 | 10 | 0 | 0 | 10.5 | 1655.6615
5988 | 2023-09-07 12:00 | 105.293 | 65.03 | 10 | 0 | 0 | 10.5 | 1703.2302
5989 | 2023-09-07 13:00 | 100.443 | 65.03 | 10 | 0 | 0 | 10.5 | 1654.7297
5990 | 2023-09-07 14:00 | 92.1181 | 65.03 | 20 | 10 | 0 | 20 | 3142.9615
5991 | 2023-09-07 15:00 | 111.8667 | 65.03 | 10 | 0 | 0 | 20 | 1768.9673
5992 | 2023-09-07 16:00 | 105.789 | 65.03 | 10 | 0 | 0 | 20 | 1708.1902
5993 | 2023-09-07 17:00 | 116.6512 | 66.4 | 0 | 0 | 10 | 10 | 0
5994 | 2023-09-07 18:00 | 112.6076 | 66.4 | 0.5 | 0 | 9.5 | 0.5 | 89.5038
5995 | 2023-09-07 19:00 | 109.9838 | 65.03 | 10 | 0 | 0 | 0.5 | 1750.1381
5996 | 2023-09-07 20:00 | 100.6352 | 65.03 | 20 | 10 | 0 | 10 | 3313.3036
5997 | 2023-09-07 21:00 | 114.4634 | 65.03 | 0 | 0 | 10 | 0 | 0
5998 | 2023-09-07 22:00 | 100.4694 | 65.03 | 10 | 0 | 0 | 0 | 1654.9945
5999 | 2023-09-07 23:00 | 85.4096 | 53.53 | 20 | 10 | 0 | 9.5 | 2778.7929
6000 | 2023-09-08 00:00 | 95.645 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.5875
6001 | 2023-09-08 01:00 | 93.5014 | 53.53 | 10 | 0 | 0 | 0 | 1470.3142
6002 | 2023-09-08 02:00 | 81.2961 | 53.53 | 10 | 0 | 0 | 0 | 1348.2605
6003 | 2023-09-08 03:00 | 78.8893 | 53.53 | 10 | 0 | 0 | 0 | 1324.1926
6004 | 2023-09-08 04:00 | 59.1059 | 53.53 | 20 | 10 | 0 | 9.5 | 2252.7174
6005 | 2023-09-08 05:00 | 78.3411 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1457.5225
6006 | 2023-09-08 06:00 | 67.3994 | 53.53 | 20 | 10 | 0 | 20 | 2418.5888
6007 | 2023-09-08 07:00 | 85.2177 | 53.53 | 10 | 0 | 0 | 20 | 1387.4775
6008 | 2023-09-08 08:00 | 102.524 | 65.03 | 10 | 0 | 0 | 20 | 1675.5398
6009 | 2023-09-08 09:00 | 107.1787 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 86.1043
6010 | 2023-09-08 10:00 | 94.18 | 65.03 | 20 | 10 | 0 | 20 | 3184.1999
6011 | 2023-09-08 11:00 | 109.7826 | 65.03 | 1 | 0 | 9 | 11 | 174.8126
6012 | 2023-09-08 12:00 | 110.3319 | 65.03 | 0 | 0 | 10 | 1 | 0
6013 | 2023-09-08 13:00 | 104.2531 | 65.03 | 10 | 0 | 0 | 1 | 1692.8312
6014 | 2023-09-08 14:00 | 98.1691 | 65.03 | 20 | 10 | 0 | 10.5 | 3263.9812
6015 | 2023-09-08 15:00 | 97.5337 | 65.03 | 20 | 10 | 0 | 20 | 3251.2739
6016 | 2023-09-08 16:00 | 112.9083 | 65.03 | 10 | 0 | 0 | 20 | 1779.3834
6017 | 2023-09-08 17:00 | 109.7854 | 66.4 | 10 | 0 | 0 | 20 | 1761.8543
6018 | 2023-09-08 18:00 | 128.3038 | 66.4 | 0 | 0 | 10 | 10 | 0
6019 | 2023-09-08 19:00 | 117.6895 | 65.03 | 0 | 0 | 10 | 0 | 0
6020 | 2023-09-08 20:00 | 98.1898 | 65.03 | 10 | 0 | 0 | 0 | 1632.1978
6021 | 2023-09-08 21:00 | 88.8743 | 65.03 | 20 | 10 | 0 | 9.5 | 3078.0863
6022 | 2023-09-08 22:00 | 97.8218 | 65.03 | 0.5 | 0 | 9.5 | 0 | 81.4259
6023 | 2023-09-08 23:00 | 98.951 | 53.53 | 10 | 0 | 0 | 0 | 1524.8098
6024 | 2023-09-09 00:00 | 77.6408 | 53.53 | 20 | 10 | 0 | 9.5 | 2623.4169
6025 | 2023-09-09 01:00 | 89.9323 | 53.53 | 0.5 | 0 | 9.5 | 0 | 71.7311
6026 | 2023-09-09 02:00 | 66.5749 | 53.53 | 20 | 10 | 0 | 9.5 | 2402.0978
6027 | 2023-09-09 03:00 | 61.5077 | 53.53 | 20 | 10 | 0 | 19 | 2300.7549
6028 | 2023-09-09 04:00 | 73.2051 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 190.1027
6029 | 2023-09-09 05:00 | 53.8108 | 53.53 | 20 | 10 | 0 | 20 | 2146.8169
6030 | 2023-09-09 06:00 | 68.6384 | 53.53 | 10 | 0 | 0 | 20 | 1221.6843
6031 | 2023-09-09 07:00 | 101.5364 | 53.53 | 0 | 0 | 10 | 10 | 0
6032 | 2023-09-09 08:00 | 109.406 | 53.53 | 0 | 0 | 10 | 0 | 0
6033 | 2023-09-09 09:00 | 98.9997 | 53.53 | 10 | 0 | 0 | 0 | 1525.2966
6034 | 2023-09-09 10:00 | 93.7351 | 53.53 | 10 | 0 | 0 | 0 | 1472.6507
6035 | 2023-09-09 11:00 | 91.557 | 53.53 | 20 | 10 | 0 | 9.5 | 2901.7395
6036 | 2023-09-09 12:00 | 93.7265 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1627.5723
6037 | 2023-09-09 13:00 | 100.3284 | 53.53 | 10 | 0 | 0 | 10.5 | 1538.5841
6038 | 2023-09-09 14:00 | 90.5213 | 53.53 | 20 | 10 | 0 | 20 | 2881.0263
6039 | 2023-09-09 15:00 | 102.2762 | 53.53 | 10 | 0 | 0 | 20 | 1558.0618
6040 | 2023-09-09 16:00 | 118.3079 | 53.53 | 0 | 0 | 10 | 10 | 0
6041 | 2023-09-09 17:00 | 110.4385 | 53.53 | 0 | 0 | 10 | 0 | 0
6042 | 2023-09-09 18:00 | 102.6008 | 53.53 | 10 | 0 | 0 | 0 | 1561.3079
6043 | 2023-09-09 19:00 | 102.599 | 53.53 | 10 | 0 | 0 | 0 | 1561.2904
6044 | 2023-09-09 20:00 | 97.4569 | 53.53 | 10 | 0 | 0 | 0 | 1509.8689
6045 | 2023-09-09 21:00 | 90.4542 | 53.53 | 20 | 10 | 0 | 9.5 | 2879.684
6046 | 2023-09-09 22:00 | 98.4206 | 53.53 | 0.5 | 0 | 9.5 | 0 | 75.9753
6047 | 2023-09-09 23:00 | 82.2 | 53.53 | 20 | 10 | 0 | 9.5 | 2714.5996
6048 | 2023-09-10 00:00 | 92.9729 | 53.53 | 0.5 | 0 | 9.5 | 0 | 73.2514
6049 | 2023-09-10 01:00 | 84.7388 | 53.53 | 10 | 0 | 0 | 0 | 1382.6881
6050 | 2023-09-10 02:00 | 60.9663 | 53.53 | 20 | 10 | 0 | 9.5 | 2289.9254
6051 | 2023-09-10 03:00 | 63.0647 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1288.678
6052 | 2023-09-10 04:00 | 58.3556 | 53.53 | 20 | 10 | 0 | 20 | 2237.7127
6053 | 2023-09-10 05:00 | 86.3061 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 69.918
6054 | 2023-09-10 06:00 | 65.1858 | 53.53 | 20 | 10 | 0 | 20 | 2374.3159
6055 | 2023-09-10 07:00 | 91.2311 | 53.53 | 10 | 0 | 0 | 20 | 1447.6112
6056 | 2023-09-10 08:00 | 92.1793 | 53.53 | 10 | 0 | 0 | 20 | 1457.0932
6057 | 2023-09-10 09:00 | 89.1325 | 53.53 | 10 | 0 | 0 | 20 | 1426.6248
6058 | 2023-09-10 10:00 | 94.2043 | 53.53 | 10 | 0 | 0 | 20 | 1477.3433
6059 | 2023-09-10 11:00 | 105.685 | 53.53 | 0 | 0 | 10 | 10 | 0
6060 | 2023-09-10 12:00 | 92.2826 | 53.53 | 10 | 0 | 0 | 10 | 1458.1259
6061 | 2023-09-10 13:00 | 90.1523 | 53.53 | 20 | 10 | 0 | 19.5 | 2873.6451
6062 | 2023-09-10 14:00 | 97.0919 | 53.53 | 10 | 0 | 0 | 19.5 | 1506.2191
6063 | 2023-09-10 15:00 | 99.9356 | 53.53 | 0.5 | 0 | 9.5 | 10 | 76.7328
6064 | 2023-09-10 16:00 | 111.8229 | 53.53 | 0 | 0 | 10 | 0 | 0
6065 | 2023-09-10 17:00 | -42.3592 | 53.53 | 20 | 10 | 0 | 9.5 | 223.4164
6066 | 2023-09-10 18:00 | -29.9119 | 53.53 | 20 | 10 | 0 | 19 | 472.3613
6067 | 2023-09-10 19:00 | 116.9191 | 53.53 | 0 | 0 | 10 | 9 | 0
6068 | 2023-09-10 20:00 | 83.5878 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1587.6799
6069 | 2023-09-10 21:00 | 84.6236 | 53.53 | 10 | 0 | 0 | 10.5 | 1381.5362
6070 | 2023-09-10 22:00 | 83.9584 | 53.53 | 10 | 0 | 0 | 10.5 | 1374.8844
6071 | 2023-09-10 23:00 | 77.6623 | 53.53 | 20 | 10 | 0 | 20 | 2623.8456
6072 | 2023-09-11 00:00 | 100.6363 | 53.53 | 0 | 0 | 10 | 10 | 0
6073 | 2023-09-11 01:00 | 96.1711 | 53.53 | 0 | 0 | 10 | 0 | 0
6074 | 2023-09-11 02:00 | 74.5017 | 53.53 | 20 | 10 | 0 | 9.5 | 2560.6339
6075 | 2023-09-11 03:00 | 60.3835 | 53.53 | 20 | 10 | 0 | 19 | 2278.2705
6076 | 2023-09-11 04:00 | 95.2158 | 53.53 | 0 | 0 | 10 | 9 | 0
6077 | 2023-09-11 05:00 | 68.0156 | 53.53 | 20 | 10 | 0 | 18.5 | 2430.9123
6078 | 2023-09-11 06:00 | 95.1649 | 53.53 | 2 | 0 | 8 | 10.5 | 297.3898
6079 | 2023-09-11 07:00 | 85.0836 | 53.53 | 20 | 10 | 0 | 20 | 2772.2721
6080 | 2023-09-11 08:00 | 98.491 | 65.03 | 10 | 0 | 0 | 20 | 1635.2098
6081 | 2023-09-11 09:00 | 91.8085 | 65.03 | 10 | 0 | 0 | 20 | 1568.3855
6082 | 2023-09-11 10:00 | 106.7673 | 65.03 | 0 | 0 | 10 | 10 | 0
6083 | 2023-09-11 11:00 | 96.8646 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1704.1539
6084 | 2023-09-11 12:00 | 97.0176 | 65.03 | 10 | 0 | 0 | 10.5 | 1620.4757
6085 | 2023-09-11 13:00 | 95.4605 | 65.03 | 20 | 10 | 0 | 20 | 3209.8096
6086 | 2023-09-11 14:00 | 110.4644 | 65.03 | 10 | 0 | 0 | 20 | 1754.9436
6087 | 2023-09-11 15:00 | 109.8465 | 65.03 | 10 | 0 | 0 | 20 | 1748.7651
6088 | 2023-09-11 16:00 | 121.9536 | 65.03 | 0 | 0 | 10 | 10 | 0
6089 | 2023-09-11 17:00 | 114.25 | 66.4 | 10 | 0 | 0 | 10 | 1806.4999
6090 | 2023-09-11 18:00 | 120.5945 | 66.4 | 0 | 0 | 10 | 0 | 0
6091 | 2023-09-11 19:00 | 110.879 | 65.03 | 10 | 0 | 0 | 0 | 1759.0897
6092 | 2023-09-11 20:00 | 96.5077 | 65.03 | 10 | 0 | 0 | 0 | 1615.3767
6093 | 2023-09-11 21:00 | 95.2947 | 65.03 | 10 | 0 | 0 | 0 | 1603.247
6094 | 2023-09-11 22:00 | 102.636 | 65.03 | 10 | 0 | 0 | 0 | 1676.6603
6095 | 2023-09-11 23:00 | 102.8175 | 53.53 | 10 | 0 | 0 | 0 | 1563.4754
6096 | 2023-09-12 00:00 | 102.5545 | 53.53 | 10 | 0 | 0 | 0 | 1560.8446
6097 | 2023-09-12 01:00 | 88.313 | 53.53 | 10 | 0 | 0 | 0 | 1418.4304
6098 | 2023-09-12 02:00 | -50.4458 | 53.53 | 20 | 10 | 0 | 9.5 | 61.6847
6099 | 2023-09-12 03:00 | -21.3049 | 53.53 | 20 | 10 | 0 | 19 | 644.5015
6100 | 2023-09-12 04:00 | -17.5839 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 53.9191
6101 | 2023-09-12 05:00 | -62.6638 | 53.53 | 20 | 10 | 0 | 20 | -182.6754
6102 | 2023-09-12 06:00 | 70.0326 | 53.53 | 10 | 0 | 0 | 20 | 1235.6256
6103 | 2023-09-12 07:00 | 111.0624 | 53.53 | 10 | 0 | 0 | 20 | 1645.9244
6104 | 2023-09-12 08:00 | 106.3135 | 65.03 | 10 | 0 | 0 | 20 | 1713.4355
6105 | 2023-09-12 09:00 | 105.2428 | 65.03 | 10 | 0 | 0 | 20 | 1702.728
6106 | 2023-09-12 10:00 | 102.0068 | 65.03 | 10 | 0 | 0 | 20 | 1670.3683
6107 | 2023-09-12 11:00 | 130.9725 | 65.03 | 0 | 0 | 10 | 10 | 0
6108 | 2023-09-12 12:00 | 115.8784 | 65.03 | 0 | 0 | 10 | 0 | 0
6109 | 2023-09-12 13:00 | 99.0353 | 65.03 | 20 | 10 | 0 | 9.5 | 3281.3054
6110 | 2023-09-12 14:00 | 101.9282 | 65.03 | 20 | 10 | 0 | 19 | 3339.1632
6111 | 2023-09-12 15:00 | 102.342 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1849.9013
6112 | 2023-09-12 16:00 | 105.0166 | 65.03 | 10 | 0 | 0 | 20 | 1700.4664
6113 | 2023-09-12 17:00 | 114.1555 | 66.4 | 10 | 0 | 0 | 20 | 1805.5546
6114 | 2023-09-12 18:00 | 122.4159 | 66.4 | 0 | 0 | 10 | 10 | 0
6115 | 2023-09-12 19:00 | 132.5466 | 65.03 | 0 | 0 | 10 | 0 | 0
6116 | 2023-09-12 20:00 | 90.7557 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1639.8491
6117 | 2023-09-12 21:00 | 91.7203 | 65.03 | 10 | 0 | 0 | 0.5 | 1567.5027
6118 | 2023-09-12 22:00 | 95.525 | 65.03 | 10 | 0 | 0 | 0.5 | 1605.55
6119 | 2023-09-12 23:00 | 90.8279 | 53.53 | 20 | 10 | 0 | 10 | 2887.158
6120 | 2023-09-13 00:00 | 114.4303 | 53.53 | 0 | 0 | 10 | 0 | 0
6121 | 2023-09-13 01:00 | 102.6621 | 53.53 | 10 | 0 | 0 | 0 | 1561.9208
6122 | 2023-09-13 02:00 | 82.0858 | 53.53 | 10 | 0 | 0 | 0 | 1356.1578
6123 | 2023-09-13 03:00 | 71.9922 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1387.3501
6124 | 2023-09-13 04:00 | 71.8406 | 53.53 | 20 | 10 | 0 | 10.5 | 2507.4119
6125 | 2023-09-13 05:00 | 65.0716 | 53.53 | 20 | 10 | 0 | 20 | 2372.0329
6126 | 2023-09-13 06:00 | 80.5059 | 53.53 | 10 | 0 | 0 | 20 | 1340.3592
6127 | 2023-09-13 07:00 | 97.8663 | 53.53 | 10 | 0 | 0 | 20 | 1513.9632
6128 | 2023-09-13 08:00 | 115.668 | 65.03 | 0 | 0 | 10 | 10 | 0
6129 | 2023-09-13 09:00 | 102.3661 | 65.03 | 11.0526 | 1.0526 | 0 | 11 | 1850.1669
6130 | 2023-09-13 10:00 | 102.8573 | 65.03 | 10 | 0 | 0 | 11 | 1678.8726
6131 | 2023-09-13 11:00 | 105.2067 | 65.03 | 10 | 0 | 0 | 11 | 1702.3674
6132 | 2023-09-13 12:00 | 111.5679 | 65.03 | 0 | 0 | 10 | 1 | 0
6133 | 2023-09-13 13:00 | 94.9821 | 65.03 | 20 | 10 | 0 | 10.5 | 3200.2417
6134 | 2023-09-13 14:00 | 110.0757 | 65.03 | 10 | 0 | 0 | 10.5 | 1751.0568
6135 | 2023-09-13 15:00 | 103.7451 | 65.03 | 10 | 0 | 0 | 10.5 | 1687.7506
6136 | 2023-09-13 16:00 | 97.0958 | 65.03 | 20 | 10 | 0 | 20 | 3242.5163
6137 | 2023-09-13 17:00 | 107.2747 | 66.4 | 10 | 0 | 0 | 20 | 1736.7473
6138 | 2023-09-13 18:00 | 117.8954 | 66.4 | 0 | 0 | 10 | 10 | 0
6139 | 2023-09-13 19:00 | 132.4959 | 65.03 | 0 | 0 | 10 | 0 | 0
6140 | 2023-09-13 20:00 | 115.2156 | 65.03 | 10 | 0 | 0 | 0 | 1802.456
6141 | 2023-09-13 21:00 | 101.7109 | 65.03 | 20 | 10 | 0 | 9.5 | 3334.8179
6142 | 2023-09-13 22:00 | 118.935 | 65.03 | 0.5 | 0 | 9.5 | 0 | 91.9825
6143 | 2023-09-13 23:00 | 93.5783 | 53.53 | 20 | 10 | 0 | 9.5 | 2942.1663
6144 | 2023-09-14 00:00 | 102.1753 | 53.53 | 0.5 | 0 | 9.5 | 0 | 77.8527
6145 | 2023-09-14 01:00 | 90.7331 | 53.53 | 10 | 0 | 0 | 0 | 1442.6314
6146 | 2023-09-14 02:00 | -53.7782 | 53.53 | 20 | 10 | 0 | 9.5 | -4.9631
6147 | 2023-09-14 03:00 | -13.8415 | 53.53 | 20 | 10 | 0 | 19 | 793.7701
6148 | 2023-09-14 04:00 | 62.3717 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1281.0188
6149 | 2023-09-14 05:00 | 85.6801 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 69.6051
6150 | 2023-09-14 06:00 | 69.5209 | 53.53 | 20 | 10 | 0 | 20 | 2461.0175
6151 | 2023-09-14 07:00 | 88.5555 | 53.53 | 10 | 0 | 0 | 20 | 1420.8552
6152 | 2023-09-14 08:00 | 96.4453 | 65.03 | 10 | 0 | 0 | 20 | 1614.7533
6153 | 2023-09-14 09:00 | 102.4116 | 65.03 | 10 | 0 | 0 | 20 | 1674.4165
6154 | 2023-09-14 10:00 | 121.3312 | 65.03 | 0 | 0 | 10 | 10 | 0
6155 | 2023-09-14 11:00 | 125.751 | 65.03 | 0 | 0 | 10 | 0 | 0
6156 | 2023-09-14 12:00 | 94.088 | 65.03 | 20 | 10 | 0 | 9.5 | 3182.3596
6157 | 2023-09-14 13:00 | 101.3764 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1839.2287
6158 | 2023-09-14 14:00 | 97.2288 | 65.03 | 20 | 10 | 0 | 20 | 3245.1769
6159 | 2023-09-14 15:00 | 112.5269 | 65.03 | 10 | 0 | 0 | 20 | 1775.5691
6160 | 2023-09-14 16:00 | 106.1429 | 65.03 | 10 | 0 | 0 | 20 | 1711.7287
6161 | 2023-09-14 17:00 | 114.5522 | 66.4 | 0 | 0 | 10 | 10 | 0
6162 | 2023-09-14 18:00 | 119.4486 | 66.4 | 0 | 0 | 10 | 0 | 0
6163 | 2023-09-14 19:00 | 115.5623 | 65.03 | 10 | 0 | 0 | 0 | 1805.9227
6164 | 2023-09-14 20:00 | 114.4732 | 65.03 | 10 | 0 | 0 | 0 | 1795.0321
6165 | 2023-09-14 21:00 | 103.3563 | 65.03 | 10 | 0 | 0 | 0 | 1683.8625
6166 | 2023-09-14 22:00 | 104.4623 | 65.03 | 10 | 0 | 0 | 0 | 1694.9231
6167 | 2023-09-14 23:00 | 80.1307 | 53.53 | 20 | 10 | 0 | 9.5 | 2673.2137
6168 | 2023-09-15 00:00 | 93.4024 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1546.6566
6169 | 2023-09-15 01:00 | 115.6027 | 53.53 | 0 | 0 | 10 | 0 | 0
6170 | 2023-09-15 02:00 | 86.1134 | 53.53 | 10 | 0 | 0 | 0 | 1396.434
6171 | 2023-09-15 03:00 | 63.2626 | 53.53 | 20 | 10 | 0 | 9.5 | 2335.853
6172 | 2023-09-15 04:00 | -62.0041 | 53.53 | 20 | 10 | 0 | 19 | -169.4827
6173 | 2023-09-15 05:00 | 66.3323 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1324.7935
6174 | 2023-09-15 06:00 | 90.6695 | 53.53 | 10 | 0 | 0 | 20 | 1441.9947
6175 | 2023-09-15 07:00 | 95.7992 | 53.53 | 10 | 0 | 0 | 20 | 1493.2919
6176 | 2023-09-15 08:00 | 98.7549 | 65.03 | 10 | 0 | 0 | 20 | 1637.8492
6177 | 2023-09-15 09:00 | 104.1558 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 84.5929
6178 | 2023-09-15 10:00 | 90.3332 | 65.03 | 20 | 10 | 0 | 20 | 3107.2632
6179 | 2023-09-15 11:00 | 96.9527 | 65.03 | 10 | 0 | 0 | 20 | 1619.8267
6180 | 2023-09-15 12:00 | 104.1731 | 65.03 | 10 | 0 | 0 | 20 | 1692.0313
6181 | 2023-09-15 13:00 | 111.118 | 65.03 | 0 | 0 | 10 | 10 | 0
6182 | 2023-09-15 14:00 | 92.8623 | 65.03 | 20 | 10 | 0 | 19.5 | 3157.8458
6183 | 2023-09-15 15:00 | 101.197 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1749.7582
6184 | 2023-09-15 16:00 | 112.743 | 65.03 | 10 | 0 | 0 | 20 | 1777.7298
6185 | 2023-09-15 17:00 | 110.0729 | 66.4 | 10 | 0 | 0 | 20 | 1764.7287
6186 | 2023-09-15 18:00 | 120.6776 | 66.4 | 0 | 0 | 10 | 10 | 0
6187 | 2023-09-15 19:00 | 119.398 | 65.03 | 0 | 0 | 10 | 0 | 0
6188 | 2023-09-15 20:00 | 115.7106 | 65.03 | 10 | 0 | 0 | 0 | 1807.4058
6189 | 2023-09-15 21:00 | 97.2305 | 65.03 | 10 | 0 | 0 | 0 | 1622.6052
6190 | 2023-09-15 22:00 | 97.6439 | 65.03 | 10 | 0 | 0 | 0 | 1626.7387
6191 | 2023-09-15 23:00 | 101.2079 | 53.53 | 10 | 0 | 0 | 0 | 1547.3789
6192 | 2023-09-16 00:00 | 77.6915 | 53.53 | 10 | 0 | 0 | 0 | 1312.2146
6193 | 2023-09-16 01:00 | 84.2954 | 53.53 | 10 | 0 | 0 | 0 | 1378.2538
6194 | 2023-09-16 02:00 | 62.7037 | 53.53 | 20 | 10 | 0 | 9.5 | 2324.6744
6195 | 2023-09-16 03:00 | 64.8779 | 53.53 | 20 | 10 | 0 | 19 | 2368.1576
6196 | 2023-09-16 04:00 | 73.1444 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 190.0116
6197 | 2023-09-16 05:00 | 70.42 | 53.53 | 10 | 0 | 0 | 10.5 | 1239.4997
6198 | 2023-09-16 06:00 | 60.8691 | 53.53 | 20 | 10 | 0 | 20 | 2287.9821
6199 | 2023-09-16 07:00 | 86.9449 | 53.53 | 10 | 0 | 0 | 20 | 1404.7486
6200 | 2023-09-16 08:00 | 109.9938 | 53.53 | 0 | 0 | 10 | 10 | 0
6201 | 2023-09-16 09:00 | 90.3798 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1514.8402
6202 | 2023-09-16 10:00 | 97.0111 | 53.53 | 10 | 0 | 0 | 10.5 | 1505.4111
6203 | 2023-09-16 11:00 | 94.4908 | 53.53 | 10 | 0 | 0 | 10.5 | 1480.2078
6204 | 2023-09-16 12:00 | 95.4302 | 53.53 | 10 | 0 | 0 | 10.5 | 1489.6021
6205 | 2023-09-16 13:00 | 86.2263 | 53.53 | 20 | 10 | 0 | 20 | 2795.1253
6206 | 2023-09-16 14:00 | 109.0704 | 53.53 | 0 | 0 | 10 | 10 | 0
6207 | 2023-09-16 15:00 | 90.7159 | 53.53 | 20 | 10 | 0 | 19.5 | 2884.9181
6208 | 2023-09-16 16:00 | 104.9098 | 53.53 | 10 | 0 | 0 | 19.5 | 1584.3976
6209 | 2023-09-16 17:00 | 106.6466 | 53.53 | 0.5 | 0 | 9.5 | 10 | 80.0883
6210 | 2023-09-16 18:00 | 106.6209 | 53.53 | 10 | 0 | 0 | 10 | 1601.509
6211 | 2023-09-16 19:00 | 121.8729 | 53.53 | 0 | 0 | 10 | 0 | 0
6212 | 2023-09-16 20:00 | 99.5829 | 53.53 | 10 | 0 | 0 | 0 | 1531.1292
6213 | 2023-09-16 21:00 | 92.5133 | 53.53 | 10 | 0 | 0 | 0 | 1460.4332
6214 | 2023-09-16 22:00 | 97.3113 | 53.53 | 10 | 0 | 0 | 0 | 1508.4128
6215 | 2023-09-16 23:00 | 83.8252 | 53.53 | 10 | 0 | 0 | 0 | 1373.5519
6216 | 2023-09-17 00:00 | 85.8356 | 53.53 | 10 | 0 | 0 | 0 | 1393.6563
6217 | 2023-09-17 01:00 | 81.3976 | 53.53 | 10 | 0 | 0 | 0 | 1349.2756
6218 | 2023-09-17 02:00 | 73.6874 | 53.53 | 10 | 0 | 0 | 0 | 1272.1738
6219 | 2023-09-17 03:00 | 61.203 | 53.53 | 20 | 10 | 0 | 9.5 | 2294.6599
6220 | 2023-09-17 04:00 | 79.9319 | 53.53 | 1.5 | 0 | 8.5 | 1 | 200.1929
6221 | 2023-09-17 05:00 | 63.6383 | 53.53 | 20 | 10 | 0 | 10.5 | 2343.3662
6222 | 2023-09-17 06:00 | 66.0526 | 53.53 | 20 | 10 | 0 | 20 | 2391.6519
6223 | 2023-09-17 07:00 | 92.2885 | 53.53 | 10 | 0 | 0 | 20 | 1458.1846
6224 | 2023-09-17 08:00 | 96.0779 | 53.53 | 10 | 0 | 0 | 20 | 1496.0793
6225 | 2023-09-17 09:00 | 93.7609 | 53.53 | 10 | 0 | 0 | 20 | 1472.9093
6226 | 2023-09-17 10:00 | 95.6741 | 53.53 | 10 | 0 | 0 | 20 | 1492.0414
6227 | 2023-09-17 11:00 | 103.5867 | 53.53 | 0 | 0 | 10 | 10 | 0
6228 | 2023-09-17 12:00 | 91.39 | 53.53 | 20 | 10 | 0 | 19.5 | 2898.4002
6229 | 2023-09-17 13:00 | 94.9692 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1563.1498
6230 | 2023-09-17 14:00 | 95.9756 | 53.53 | 10 | 0 | 0 | 20 | 1495.0558
6231 | 2023-09-17 15:00 | 103.3013 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 78.4157
6232 | 2023-09-17 16:00 | 95.1606 | 53.53 | 20 | 10 | 0 | 20 | 2973.8114
6233 | 2023-09-17 17:00 | 128.9054 | 53.53 | 0 | 0 | 10 | 10 | 0
6234 | 2023-09-17 18:00 | 109.7514 | 53.53 | 0 | 0 | 10 | 0 | 0
6235 | 2023-09-17 19:00 | 109.1777 | 53.53 | 10 | 0 | 0 | 0 | 1627.0775
6236 | 2023-09-17 20:00 | 89.6479 | 53.53 | 10 | 0 | 0 | 0 | 1431.7792
6237 | 2023-09-17 21:00 | 82.7404 | 53.53 | 20 | 10 | 0 | 9.5 | 2725.4087
6238 | 2023-09-17 22:00 | 84.2158 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1522.4538
6239 | 2023-09-17 23:00 | 82.2189 | 53.53 | 20 | 10 | 0 | 20 | 2714.979
6240 | 2023-09-18 00:00 | 104.0483 | 53.53 | 0 | 0 | 10 | 10 | 0
6241 | 2023-09-18 01:00 | 93.6511 | 53.53 | 0 | 0 | 10 | 0 | 0
6242 | 2023-09-18 02:00 | 70.5154 | 53.53 | 20 | 10 | 0 | 9.5 | 2480.9072
6243 | 2023-09-18 03:00 | 85.0179 | 53.53 | 10 | 0 | 0 | 9.5 | 1385.4793
6244 | 2023-09-18 04:00 | 88.7127 | 53.53 | 10 | 0 | 0 | 9.5 | 1422.4272
6245 | 2023-09-18 05:00 | 85.3319 | 53.53 | 10 | 0 | 0 | 9.5 | 1388.6187
6246 | 2023-09-18 06:00 | 68.2533 | 53.53 | 20 | 10 | 0 | 19 | 2435.6654
6247 | 2023-09-18 07:00 | 90.4467 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 215.965
6248 | 2023-09-18 08:00 | -10.4004 | 65.03 | 20 | 10 | 0 | 20 | 1092.5924
6249 | 2023-09-18 09:00 | 105.7739 | 65.03 | 10 | 0 | 0 | 20 | 1708.0388
6250 | 2023-09-18 10:00 | 101.9696 | 65.03 | 10 | 0 | 0 | 20 | 1669.9957
6251 | 2023-09-18 11:00 | 109.9105 | 65.03 | 10 | 0 | 0 | 20 | 1749.4049
6252 | 2023-09-18 12:00 | 112.7188 | 65.03 | 0 | 0 | 10 | 10 | 0
6253 | 2023-09-18 13:00 | 99.9597 | 65.03 | 20 | 10 | 0 | 19.5 | 3299.7937
6254 | 2023-09-18 14:00 | 105.5995 | 65.03 | 10 | 0 | 0 | 19.5 | 1706.2949
6255 | 2023-09-18 15:00 | 111.9094 | 65.03 | 1 | 0 | 9 | 10.5 | 176.9394
6256 | 2023-09-18 16:00 | 96.5493 | 65.03 | 20 | 10 | 0 | 20 | 3231.5851
6257 | 2023-09-18 17:00 | 118.9911 | 66.4 | 0 | 0 | 10 | 10 | 0
6258 | 2023-09-18 18:00 | 111.794 | 66.4 | 0 | 0 | 10 | 0 | 0
6259 | 2023-09-18 19:00 | 112.5102 | 65.03 | 10 | 0 | 0 | 0 | 1775.4022
6260 | 2023-09-18 20:00 | 95.0125 | 65.03 | 10 | 0 | 0 | 0 | 1600.4251
6261 | 2023-09-18 21:00 | 102.7455 | 65.03 | 10 | 0 | 0 | 0 | 1677.7547
6262 | 2023-09-18 22:00 | 96.5961 | 65.03 | 10 | 0 | 0 | 0 | 1616.2613
6263 | 2023-09-18 23:00 | 89.4789 | 53.53 | 10 | 0 | 0 | 0 | 1430.0894
6264 | 2023-09-19 00:00 | 94.288 | 53.53 | 10 | 0 | 0 | 0 | 1478.1797
6265 | 2023-09-19 01:00 | 86.62 | 53.53 | 10 | 0 | 0 | 0 | 1401.4996
6266 | 2023-09-19 02:00 | 77.3303 | 53.53 | 10 | 0 | 0 | 0 | 1308.6035
6267 | 2023-09-19 03:00 | 84.0015 | 53.53 | 10 | 0 | 0 | 0 | 1375.3149
6268 | 2023-09-19 04:00 | 73.3113 | 53.53 | 20 | 10 | 0 | 9.5 | 2536.8256
6269 | 2023-09-19 05:00 | 72.4237 | 53.53 | 20 | 10 | 0 | 19 | 2519.0743
6270 | 2023-09-19 06:00 | 76.862 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1441.175
6271 | 2023-09-19 07:00 | 82.5019 | 53.53 | 10 | 0 | 0 | 20 | 1360.3191
6272 | 2023-09-19 08:00 | 108.2668 | 65.03 | 10 | 0 | 0 | 20 | 1732.9676
6273 | 2023-09-19 09:00 | 142.2969 | 65.03 | 0 | 0 | 10 | 10 | 0
6274 | 2023-09-19 10:00 | 102.995 | 65.03 | 20 | 10 | 0 | 19.5 | 3360.4992
6275 | 2023-09-19 11:00 | 103.0206 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1768.9542
6276 | 2023-09-19 12:00 | 110.1464 | 65.03 | 10 | 0 | 0 | 20 | 1751.7639
6277 | 2023-09-19 13:00 | 119.8534 | 65.03 | 0 | 0 | 10 | 10 | 0
6278 | 2023-09-19 14:00 | 112.3923 | 65.03 | 10 | 0 | 0 | 10 | 1774.223
6279 | 2023-09-19 15:00 | 91.9928 | 65.03 | 20 | 10 | 0 | 19.5 | 3140.4565
6280 | 2023-09-19 16:00 | 108.5019 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1826.6515
6281 | 2023-09-19 17:00 | 147.9778 | 66.4 | 0 | 0 | 10 | 10 | 0
6282 | 2023-09-19 18:00 | 124.0309 | 66.4 | 0 | 0 | 10 | 0 | 0
6283 | 2023-09-19 19:00 | 111.5794 | 65.03 | 10 | 0 | 0 | 0 | 1766.0939
6284 | 2023-09-19 20:00 | 101.104 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1748.7785
6285 | 2023-09-19 21:00 | 90.9231 | 65.03 | 20 | 10 | 0 | 10 | 3119.0616
6286 | 2023-09-19 22:00 | 110.0859 | 65.03 | 0 | 0 | 10 | 0 | 0
6287 | 2023-09-19 23:00 | 87.6655 | 53.53 | 10 | 0 | 0 | 0 | 1411.9551
6288 | 2023-09-20 00:00 | 94.4614 | 53.53 | 10 | 0 | 0 | 0 | 1479.9138
6289 | 2023-09-20 01:00 | 88.2261 | 53.53 | 10 | 0 | 0 | 0 | 1417.5605
6290 | 2023-09-20 02:00 | 70.1182 | 53.53 | 20 | 10 | 0 | 9.5 | 2472.965
6291 | 2023-09-20 03:00 | 87.9435 | 53.53 | 0.5 | 0 | 9.5 | 0 | 70.7368
6292 | 2023-09-20 04:00 | 74.6864 | 53.53 | 10 | 0 | 0 | 0 | 1282.164
6293 | 2023-09-20 05:00 | 70.0372 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1365.7428
6294 | 2023-09-20 06:00 | 66.6292 | 53.53 | 20 | 10 | 0 | 10.5 | 2403.1836
6295 | 2023-09-20 07:00 | -10.4129 | 53.53 | 20 | 10 | 0 | 20 | 862.3427
6296 | 2023-09-20 08:00 | 96.0739 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 80.552
6297 | 2023-09-20 09:00 | -34.2837 | 65.03 | 20 | 10 | 0 | 20 | 614.926
6298 | 2023-09-20 10:00 | 112.4453 | 65.03 | 0 | 0 | 10 | 10 | 0
6299 | 2023-09-20 11:00 | 100.0299 | 65.03 | 11.0526 | 1.0526 | 0 | 11 | 1824.3465
6300 | 2023-09-20 12:00 | 118.9447 | 65.03 | 0 | 0 | 10 | 1 | 0
6301 | 2023-09-20 13:00 | 99.0568 | 65.03 | 20 | 10 | 0 | 10.5 | 3281.736
6302 | 2023-09-20 14:00 | 102.1755 | 65.03 | 10 | 0 | 0 | 10.5 | 1672.0546
6303 | 2023-09-20 15:00 | 96.9819 | 65.03 | 20 | 10 | 0 | 20 | 3240.2372
6304 | 2023-09-20 16:00 | 112.5514 | 65.03 | 10 | 0 | 0 | 20 | 1775.8138
6305 | 2023-09-20 17:00 | 140.8035 | 66.4 | 0 | 0 | 10 | 10 | 0
6306 | 2023-09-20 18:00 | 108.6349 | 66.4 | 10 | 0 | 0 | 10 | 1750.3486
6307 | 2023-09-20 19:00 | 116.4323 | 65.03 | 0 | 0 | 10 | 0 | 0
6308 | 2023-09-20 20:00 | 110.4347 | 65.03 | 10 | 0 | 0 | 0 | 1754.6473
6309 | 2023-09-20 21:00 | 90.0948 | 65.03 | 20 | 10 | 0 | 9.5 | 3102.4951
6310 | 2023-09-20 22:00 | 103.5311 | 65.03 | 0.5 | 0 | 9.5 | 0 | 84.2805
6311 | 2023-09-20 23:00 | 104.9631 | 53.53 | 10 | 0 | 0 | 0 | 1584.9311
6312 | 2023-09-21 00:00 | 94.492 | 53.53 | 10 | 0 | 0 | 0 | 1480.2196
6313 | 2023-09-21 01:00 | 98.3855 | 53.53 | 10 | 0 | 0 | 0 | 1519.1546
6314 | 2023-09-21 02:00 | 91.2982 | 53.53 | 10 | 0 | 0 | 0 | 1448.2823
6315 | 2023-09-21 03:00 | 93.7519 | 53.53 | 10 | 0 | 0 | 0 | 1472.819
6316 | 2023-09-21 04:00 | 73.4378 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1403.3288
6317 | 2023-09-21 05:00 | 70.208 | 53.53 | 20 | 10 | 0 | 10.5 | 2474.7602
6318 | 2023-09-21 06:00 | 67.8687 | 53.53 | 20 | 10 | 0 | 20 | 2427.9748
6319 | 2023-09-21 07:00 | 102.4124 | 53.53 | 10 | 0 | 0 | 20 | 1559.4237
6320 | 2023-09-21 08:00 | 95.4642 | 65.03 | 10 | 0 | 0 | 20 | 1604.9415
6321 | 2023-09-21 09:00 | 102.074 | 65.03 | 10 | 0 | 0 | 20 | 1671.0399
6322 | 2023-09-21 10:00 | 104.6805 | 65.03 | 10 | 0 | 0 | 20 | 1697.1047
6323 | 2023-09-21 11:00 | 100.3966 | 65.03 | 10 | 0 | 0 | 20 | 1654.2663
6324 | 2023-09-21 12:00 | 106.0876 | 65.03 | 10 | 0 | 0 | 20 | 1711.1756
6325 | 2023-09-21 13:00 | 132.8576 | 65.03 | 0 | 0 | 10 | 10 | 0
6326 | 2023-09-21 14:00 | 103.0028 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1768.7658
6327 | 2023-09-21 15:00 | 100.837 | 65.03 | 20 | 10 | 0 | 20 | 3317.341
6328 | 2023-09-21 16:00 | 112.8004 | 65.03 | 10 | 0 | 0 | 20 | 1778.3035
6329 | 2023-09-21 17:00 | 120.7613 | 66.4 | 0 | 0 | 10 | 10 | 0
6330 | 2023-09-21 18:00 | 132.399 | 66.4 | 0 | 0 | 10 | 0 | 0
6331 | 2023-09-21 19:00 | 120.1645 | 65.03 | 10 | 0 | 0 | 0 | 1851.9448
6332 | 2023-09-21 20:00 | 97.1029 | 65.03 | 10 | 0 | 0 | 0 | 1621.3287
6333 | 2023-09-21 21:00 | 88.5383 | 65.03 | 10 | 0 | 0 | 0 | 1535.6832
6334 | 2023-09-21 22:00 | 89.2766 | 65.03 | 10 | 0 | 0 | 0 | 1543.0658
6335 | 2023-09-21 23:00 | 83.3118 | 53.53 | 20 | 10 | 0 | 9.5 | 2736.8364
6336 | 2023-09-22 00:00 | 96.9116 | 53.53 | 0.5 | 0 | 9.5 | 0 | 75.2208
6337 | 2023-09-22 01:00 | 85.5116 | 53.53 | 10 | 0 | 0 | 0 | 1390.4156
6338 | 2023-09-22 02:00 | 85.334 | 53.53 | 10 | 0 | 0 | 0 | 1388.64
6339 | 2023-09-22 03:00 | 74.1262 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1410.9368
6340 | 2023-09-22 04:00 | 72.1324 | 53.53 | 20 | 10 | 0 | 10.5 | 2513.2475
6341 | 2023-09-22 05:00 | 68.307 | 53.53 | 20 | 10 | 0 | 20 | 2436.7393
6342 | 2023-09-22 06:00 | 79.0293 | 53.53 | 10 | 0 | 0 | 20 | 1325.5927
6343 | 2023-09-22 07:00 | 88.5375 | 53.53 | 10 | 0 | 0 | 20 | 1420.6748
6344 | 2023-09-22 08:00 | 97.5002 | 65.03 | 10 | 0 | 0 | 20 | 1625.3018
6345 | 2023-09-22 09:00 | 114.6065 | 65.03 | 0 | 0 | 10 | 10 | 0
6346 | 2023-09-22 10:00 | 106.7046 | 65.03 | 10 | 0 | 0 | 10 | 1717.3459
6347 | 2023-09-22 11:00 | 102.197 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1760.2841
6348 | 2023-09-22 12:00 | 109.2031 | 65.03 | 10 | 0 | 0 | 10.5 | 1742.3309
6349 | 2023-09-22 13:00 | 103.9654 | 65.03 | 10 | 0 | 0 | 10.5 | 1689.9538
6350 | 2023-09-22 14:00 | 106.9424 | 65.03 | 10 | 0 | 0 | 10.5 | 1719.7245
6351 | 2023-09-22 15:00 | 98.4649 | 65.03 | 20 | 10 | 0 | 20 | 3269.8971
6352 | 2023-09-22 16:00 | 125.4236 | 65.03 | 0 | 0 | 10 | 10 | 0
6353 | 2023-09-22 17:00 | 114.9081 | 66.4 | 10 | 0 | 0 | 10 | 1813.0812
6354 | 2023-09-22 18:00 | 133.7706 | 66.4 | 0 | 0 | 10 | 0 | 0
6355 | 2023-09-22 19:00 | 117.5212 | 65.03 | 10 | 0 | 0 | 0 | 1825.5117
6356 | 2023-09-22 20:00 | 105.7473 | 65.03 | 10 | 0 | 0 | 0 | 1707.7727
6357 | 2023-09-22 21:00 | 105.0585 | 65.03 | 10 | 0 | 0 | 0 | 1700.8854
6358 | 2023-09-22 22:00 | 109.1647 | 65.03 | 10 | 0 | 0 | 0 | 1741.9473
6359 | 2023-09-22 23:00 | 88.3258 | 53.53 | 20 | 10 | 0 | 9.5 | 2837.1158
6360 | 2023-09-23 00:00 | 95.4193 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1567.8869
6361 | 2023-09-23 01:00 | 104.4003 | 53.53 | 0 | 0 | 10 | 0 | 0
6362 | 2023-09-23 02:00 | -42.7816 | 53.53 | 20 | 10 | 0 | 9.5 | 214.9681
6363 | 2023-09-23 03:00 | -18.2586 | 53.53 | 20 | 10 | 0 | 19 | 705.4276
6364 | 2023-09-23 04:00 | 62.2652 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 173.6928
6365 | 2023-09-23 05:00 | -7.8389 | 53.53 | 20 | 10 | 0 | 20 | 913.821
6366 | 2023-09-23 06:00 | 82.6735 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 68.1017
6367 | 2023-09-23 07:00 | -74.8609 | 53.53 | 20 | 10 | 0 | 20 | -426.6171
6368 | 2023-09-23 08:00 | 89.7432 | 53.53 | 10 | 0 | 0 | 20 | 1432.7317
6369 | 2023-09-23 09:00 | 111.4325 | 53.53 | 0 | 0 | 10 | 10 | 0
6370 | 2023-09-23 10:00 | 101.05 | 53.53 | 10 | 0 | 0 | 10 | 1545.7998
6371 | 2023-09-23 11:00 | 118.1263 | 53.53 | 0 | 0 | 10 | 0 | 0
6372 | 2023-09-23 12:00 | 92.7383 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1616.65
6373 | 2023-09-23 13:00 | 96.8636 | 53.53 | 10 | 0 | 0 | 1 | 1503.9358
6374 | 2023-09-23 14:00 | 91.4034 | 53.53 | 20 | 10 | 0 | 10.5 | 2898.6678
6375 | 2023-09-23 15:00 | 96.9965 | 53.53 | 10 | 0 | 0 | 10.5 | 1505.265
6376 | 2023-09-23 16:00 | 85.5807 | 53.53 | 20 | 10 | 0 | 20 | 2782.2133
6377 | 2023-09-23 17:00 | 116.6014 | 53.53 | 0 | 0 | 10 | 10 | 0
6378 | 2023-09-23 18:00 | 113.446 | 53.53 | 0 | 0 | 10 | 0 | 0
6379 | 2023-09-23 19:00 | 110.4704 | 53.53 | 10 | 0 | 0 | 0 | 1640.0035
6380 | 2023-09-23 20:00 | 88.1355 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1565.7766
6381 | 2023-09-23 21:00 | 85.0129 | 53.53 | 20 | 10 | 0 | 10.5 | 2770.857
6382 | 2023-09-23 22:00 | 96.9977 | 53.53 | 0 | 0 | 10 | 0.5 | 0
6383 | 2023-09-23 23:00 | 78.4921 | 53.53 | 20 | 10 | 0 | 10 | 2640.4429
6384 | 2023-09-24 00:00 | 90.048 | 53.53 | 10 | 0 | 0 | 10 | 1435.7801
6385 | 2023-09-24 01:00 | 107.4802 | 53.53 | 0 | 0 | 10 | 0 | 0
6386 | 2023-09-24 02:00 | -48.8212 | 53.53 | 20 | 10 | 0 | 9.5 | 94.1757
6387 | 2023-09-24 03:00 | -53.2329 | 53.53 | 20 | 10 | 0 | 19 | 5.9415
6388 | 2023-09-24 04:00 | 62.1802 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1278.9017
6389 | 2023-09-24 05:00 | 69.2677 | 53.53 | 10 | 0 | 0 | 20 | 1227.977
6390 | 2023-09-24 06:00 | 65.3767 | 53.53 | 10 | 0 | 0 | 20 | 1189.0671
6391 | 2023-09-24 07:00 | 77.3274 | 53.53 | 10 | 0 | 0 | 20 | 1308.5741
6392 | 2023-09-24 08:00 | 98.9618 | 53.53 | 10 | 0 | 0 | 20 | 1524.9183
6393 | 2023-09-24 09:00 | 95.8233 | 53.53 | 10 | 0 | 0 | 20 | 1493.5329
6394 | 2023-09-24 10:00 | 115.2954 | 53.53 | 0 | 0 | 10 | 10 | 0
6395 | 2023-09-24 11:00 | 94.0694 | 53.53 | 11.0526 | 1.0526 | 0 | 11 | 1631.3622
6396 | 2023-09-24 12:00 | 106.3892 | 53.53 | 0 | 0 | 10 | 1 | 0
6397 | 2023-09-24 13:00 | 87.9927 | 53.53 | 20 | 10 | 0 | 10.5 | 2830.4536
6398 | 2023-09-24 14:00 | 89.2638 | 53.53 | 20 | 10 | 0 | 20 | 2855.8758
6399 | 2023-09-24 15:00 | 101.9413 | 53.53 | 10 | 0 | 0 | 20 | 1554.7134
6400 | 2023-09-24 16:00 | 105.5032 | 53.53 | 0 | 0 | 10 | 10 | 0
6401 | 2023-09-24 17:00 | 104.657 | 53.53 | 10 | 0 | 0 | 10 | 1581.8701
6402 | 2023-09-24 18:00 | 111.0795 | 53.53 | 0 | 0 | 10 | 0 | 0
6403 | 2023-09-24 19:00 | 102.4155 | 53.53 | 10 | 0 | 0 | 0 | 1559.455
6404 | 2023-09-24 20:00 | 89.5754 | 53.53 | 20 | 10 | 0 | 9.5 | 2862.1089
6405 | 2023-09-24 21:00 | 98.0335 | 53.53 | 0.5 | 0 | 9.5 | 0 | 75.7818
6406 | 2023-09-24 22:00 | 87.84 | 53.53 | 10 | 0 | 0 | 0 | 1413.6999
6407 | 2023-09-24 23:00 | 84.0986 | 53.53 | 10 | 0 | 0 | 0 | 1376.2861
6408 | 2023-09-25 00:00 | 86.7115 | 53.53 | 10 | 0 | 0 | 0 | 1402.4146
6409 | 2023-09-25 01:00 | 89.4793 | 53.53 | 10 | 0 | 0 | 0 | 1430.0931
6410 | 2023-09-25 02:00 | 91.2627 | 53.53 | 10 | 0 | 0 | 0 | 1447.9274
6411 | 2023-09-25 03:00 | 74.4513 | 53.53 | 10 | 0 | 0 | 0 | 1279.8127
6412 | 2023-09-25 04:00 | 67.4059 | 53.53 | 20 | 10 | 0 | 9.5 | 2418.7189
6413 | 2023-09-25 05:00 | 71.6456 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1383.5193
6414 | 2023-09-25 06:00 | 64.3798 | 53.53 | 20 | 10 | 0 | 20 | 2358.1967
6415 | 2023-09-25 07:00 | 87.3403 | 53.53 | 10 | 0 | 0 | 20 | 1408.7026
6416 | 2023-09-25 08:00 | 116.4973 | 65.03 | 0 | 0 | 10 | 10 | 0
6417 | 2023-09-25 09:00 | 102.8522 | 65.03 | 20 | 10 | 0 | 19.5 | 3357.6441
6418 | 2023-09-25 10:00 | 122.9822 | 65.03 | 0 | 0 | 10 | 9.5 | 0
6419 | 2023-09-25 11:00 | 103.1933 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1859.3105
6420 | 2023-09-25 12:00 | 103.6299 | 65.03 | 10 | 0 | 0 | 10.5 | 1686.5992
6421 | 2023-09-25 13:00 | 109.1982 | 65.03 | 10 | 0 | 0 | 10.5 | 1742.282
6422 | 2023-09-25 14:00 | 90.1116 | 65.03 | 20 | 10 | 0 | 20 | 3102.8319
6423 | 2023-09-25 15:00 | 105.4836 | 65.03 | 10 | 0 | 0 | 20 | 1705.1358
6424 | 2023-09-25 16:00 | 103.5336 | 65.03 | 10 | 0 | 0 | 20 | 1685.6359
6425 | 2023-09-25 17:00 | 132.9422 | 66.4 | 0 | 0 | 10 | 10 | 0
6426 | 2023-09-25 18:00 | 127.2891 | 66.4 | 0 | 0 | 10 | 0 | 0
6427 | 2023-09-25 19:00 | 111.6907 | 65.03 | 10 | 0 | 0 | 0 | 1767.2065
6428 | 2023-09-25 20:00 | 110.1874 | 65.03 | 10 | 0 | 0 | 0 | 1752.1741
6429 | 2023-09-25 21:00 | 97.0064 | 65.03 | 10 | 0 | 0 | 0 | 1620.3637
6430 | 2023-09-25 22:00 | 92.9573 | 65.03 | 10 | 0 | 0 | 0 | 1579.8731
6431 | 2023-09-25 23:00 | 95.4212 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1567.907
6432 | 2023-09-26 00:00 | 92.4229 | 53.53 | 20 | 10 | 0 | 10 | 2919.0573
6433 | 2023-09-26 01:00 | 108.5612 | 53.53 | 0 | 0 | 10 | 0 | 0
6434 | 2023-09-26 02:00 | 76.5881 | 53.53 | 20 | 10 | 0 | 9.5 | 2602.3612
6435 | 2023-09-26 03:00 | 75.4893 | 53.53 | 20 | 10 | 0 | 19 | 2580.3865
6436 | 2023-09-26 04:00 | 81.6538 | 53.53 | 10 | 0 | 0 | 19 | 1351.8378
6437 | 2023-09-26 05:00 | 83.5982 | 53.53 | 10 | 0 | 0 | 19 | 1371.2822
6438 | 2023-09-26 06:00 | 80.5236 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1481.6451
6439 | 2023-09-26 07:00 | 107.1702 | 53.53 | 10 | 0 | 0 | 20 | 1607.0016
6440 | 2023-09-26 08:00 | 108.9068 | 65.03 | 10 | 0 | 0 | 20 | 1739.368
6441 | 2023-09-26 09:00 | 105.1878 | 65.03 | 10 | 0 | 0 | 20 | 1702.1785
6442 | 2023-09-26 10:00 | 115.1551 | 65.03 | 0 | 0 | 10 | 10 | 0
6443 | 2023-09-26 11:00 | 103.2258 | 65.03 | 20 | 10 | 0 | 19.5 | 3365.1159
6444 | 2023-09-26 12:00 | 104.1489 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1780.8306
6445 | 2023-09-26 13:00 | 120.8009 | 65.03 | 0 | 0 | 10 | 10 | 0
6446 | 2023-09-26 14:00 | 119.5668 | 65.03 | 0 | 0 | 10 | 0 | 0
6447 | 2023-09-26 15:00 | 103.8371 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1866.4254
6448 | 2023-09-26 16:00 | 100.7179 | 65.03 | 20 | 10 | 0 | 10.5 | 3314.9589
6449 | 2023-09-26 17:00 | -50.9466 | 66.4 | 20 | 10 | 0 | 20 | 309.0683
6450 | 2023-09-26 18:00 | 125.6835 | 66.4 | 0 | 0 | 10 | 10 | 0
6451 | 2023-09-26 19:00 | 121.3808 | 65.03 | 0 | 0 | 10 | 0 | 0
6452 | 2023-09-26 20:00 | 96.5972 | 65.03 | 10 | 0 | 0 | 0 | 1616.2715
6453 | 2023-09-26 21:00 | -11.232 | 65.03 | 20 | 10 | 0 | 9.5 | 1075.9592
6454 | 2023-09-26 22:00 | -40.6352 | 65.03 | 20 | 10 | 0 | 19 | 487.896
6455 | 2023-09-26 23:00 | 89.3809 | 53.53 | 10 | 0 | 0 | 19 | 1429.1088
6456 | 2023-09-27 00:00 | 94.8851 | 53.53 | 1 | 0 | 9 | 10 | 148.4151
6457 | 2023-09-27 01:00 | 95.9704 | 53.53 | 0 | 0 | 10 | 0 | 0
6458 | 2023-09-27 02:00 | -32.5312 | 53.53 | 20 | 10 | 0 | 9.5 | 419.9755
6459 | 2023-09-27 03:00 | 81.685 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1494.4819
6460 | 2023-09-27 04:00 | 85.6993 | 53.53 | 10 | 0 | 0 | 10.5 | 1392.2933
6461 | 2023-09-27 05:00 | 82.3414 | 53.53 | 10 | 0 | 0 | 10.5 | 1358.7139
6462 | 2023-09-27 06:00 | 71.91 | 53.53 | 20 | 10 | 0 | 20 | 2508.7994
6463 | 2023-09-27 07:00 | 100.2611 | 53.53 | 10 | 0 | 0 | 20 | 1537.911
6464 | 2023-09-27 08:00 | 104.4899 | 65.03 | 10 | 0 | 0 | 20 | 1695.1991
6465 | 2023-09-27 09:00 | 96.1542 | 65.03 | 10 | 0 | 0 | 20 | 1611.8417
6466 | 2023-09-27 10:00 | 109.489 | 65.03 | 10 | 0 | 0 | 20 | 1745.1896
6467 | 2023-09-27 11:00 | 105.0187 | 65.03 | 10 | 0 | 0 | 20 | 1700.4867
6468 | 2023-09-27 12:00 | 133.3297 | 65.03 | 0 | 0 | 10 | 10 | 0
6469 | 2023-09-27 13:00 | 117.6067 | 65.03 | 0 | 0 | 10 | 0 | 0
6470 | 2023-09-27 14:00 | 109.8436 | 65.03 | 10 | 0 | 0 | 0 | 1748.736
6471 | 2023-09-27 15:00 | 105.8387 | 65.03 | 10 | 0 | 0 | 0 | 1708.687
6472 | 2023-09-27 16:00 | 105.1569 | 65.03 | 10 | 0 | 0 | 0 | 1701.8688
6473 | 2023-09-27 17:00 | 112.3983 | 66.4 | 10 | 0 | 0 | 0 | 1787.9827
6474 | 2023-09-27 18:00 | 108.7361 | 66.4 | 10 | 0 | 0 | 0 | 1751.3613
6475 | 2023-09-27 19:00 | 113.1406 | 65.03 | 10 | 0 | 0 | 0 | 1781.7055
6476 | 2023-09-27 20:00 | 98.543 | 65.03 | 10 | 0 | 0 | 0 | 1635.7298
6477 | 2023-09-27 21:00 | 87.191 | 65.03 | 10 | 0 | 0 | 0 | 1522.2099
6478 | 2023-09-27 22:00 | 95.1318 | 65.03 | 10 | 0 | 0 | 0 | 1601.6179
6479 | 2023-09-27 23:00 | 92.1085 | 53.53 | 10 | 0 | 0 | 0 | 1456.3851
6480 | 2023-09-28 00:00 | 92.3337 | 53.53 | 10 | 0 | 0 | 0 | 1458.6371
6481 | 2023-09-28 01:00 | 89.397 | 53.53 | 10 | 0 | 0 | 0 | 1429.2695
6482 | 2023-09-28 02:00 | 71.4638 | 53.53 | 20 | 10 | 0 | 9.5 | 2499.8759
6483 | 2023-09-28 03:00 | 90.8301 | 53.53 | 0.5 | 0 | 9.5 | 0 | 72.18
6484 | 2023-09-28 04:00 | 79.392 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1469.1377
6485 | 2023-09-28 05:00 | 70.0302 | 53.53 | 20 | 10 | 0 | 10.5 | 2471.2049
6486 | 2023-09-28 06:00 | 73.3909 | 53.53 | 20 | 10 | 0 | 20 | 2538.4183
6487 | 2023-09-28 07:00 | 93.6869 | 53.53 | 10 | 0 | 0 | 20 | 1472.1686
6488 | 2023-09-28 08:00 | 98.754 | 65.03 | 10 | 0 | 0 | 20 | 1637.8397
6489 | 2023-09-28 09:00 | 98.747 | 65.03 | 10 | 0 | 0 | 20 | 1637.7697
6490 | 2023-09-28 10:00 | 112.7515 | 65.03 | 0 | 0 | 10 | 10 | 0
6491 | 2023-09-28 11:00 | 100.9401 | 65.03 | 10 | 0 | 0 | 10 | 1659.701
6492 | 2023-09-28 12:00 | 96.9 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1704.5265
6493 | 2023-09-28 13:00 | 103.5768 | 65.03 | 10 | 0 | 0 | 10.5 | 1686.0684
6494 | 2023-09-28 14:00 | 104.7992 | 65.03 | 10 | 0 | 0 | 10.5 | 1698.2923
6495 | 2023-09-28 15:00 | 92.7314 | 65.03 | 20 | 10 | 0 | 20 | 3155.2282
6496 | 2023-09-28 16:00 | 103.5946 | 65.03 | 10 | 0 | 0 | 20 | 1686.2457
6497 | 2023-09-28 17:00 | 126.3343 | 66.4 | 0 | 0 | 10 | 10 | 0
6498 | 2023-09-28 18:00 | 122.5223 | 66.4 | 10 | 0 | 0 | 10 | 1889.2228
6499 | 2023-09-28 19:00 | 142.7024 | 65.03 | 0 | 0 | 10 | 0 | 0
6500 | 2023-09-28 20:00 | 110.2852 | 65.03 | 20 | 10 | 0 | 9.5 | 3506.304
6501 | 2023-09-28 21:00 | 112.51 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1868.8425
6502 | 2023-09-28 22:00 | 131.809 | 65.03 | 0 | 0 | 10 | 0 | 0
6503 | 2023-09-28 23:00 | 100.2831 | 53.53 | 10 | 0 | 0 | 0 | 1538.1307
6504 | 2023-09-29 00:00 | 95.1517 | 53.53 | 10 | 0 | 0 | 0 | 1486.8174
6505 | 2023-09-29 01:00 | 102.38 | 53.53 | 10 | 0 | 0 | 0 | 1559.0997
6506 | 2023-09-29 02:00 | 70.037 | 53.53 | 20 | 10 | 0 | 9.5 | 2471.3399
6507 | 2023-09-29 03:00 | 74.7191 | 53.53 | 10 | 0 | 0 | 9.5 | 1282.4914
6508 | 2023-09-29 04:00 | 69.4832 | 53.53 | 20 | 10 | 0 | 19 | 2460.264
6509 | 2023-09-29 05:00 | 77.0687 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 195.898
6510 | 2023-09-29 06:00 | 69.4574 | 53.53 | 20 | 10 | 0 | 20 | 2459.7479
6511 | 2023-09-29 07:00 | 89.2425 | 53.53 | 10 | 0 | 0 | 20 | 1427.7253
6512 | 2023-09-29 08:00 | 107.1999 | 65.03 | 0 | 0 | 10 | 10 | 0
6513 | 2023-09-29 09:00 | 102.8865 | 65.03 | 10 | 0 | 0 | 10 | 1679.1651
6514 | 2023-09-29 10:00 | 92.9202 | 65.03 | 20 | 10 | 0 | 19.5 | 3159.0039
6515 | 2023-09-29 11:00 | 95.053 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1685.0839
6516 | 2023-09-29 12:00 | 96.6183 | 65.03 | 10 | 0 | 0 | 20 | 1616.4834
6517 | 2023-09-29 13:00 | 98.0805 | 65.03 | 10 | 0 | 0 | 20 | 1631.1053
6518 | 2023-09-29 14:00 | 107.208 | 65.03 | 10 | 0 | 0 | 20 | 1722.3796
6519 | 2023-09-29 15:00 | 105.5955 | 65.03 | 10 | 0 | 0 | 20 | 1706.2547
6520 | 2023-09-29 16:00 | 113.3122 | 65.03 | 10 | 0 | 0 | 20 | 1783.4217
6521 | 2023-09-29 17:00 | 125.2327 | 66.4 | 0 | 0 | 10 | 10 | 0
6522 | 2023-09-29 18:00 | 128.3806 | 66.4 | 0 | 0 | 10 | 0 | 0
6523 | 2023-09-29 19:00 | 123.9042 | 65.03 | 10 | 0 | 0 | 0 | 1889.3423
6524 | 2023-09-29 20:00 | 100.5214 | 65.03 | 10 | 0 | 0 | 0 | 1655.5142
6525 | 2023-09-29 21:00 | 108.6657 | 65.03 | 10 | 0 | 0 | 0 | 1736.9575
6526 | 2023-09-29 22:00 | 106.8387 | 65.03 | 10 | 0 | 0 | 0 | 1718.687
6527 | 2023-09-29 23:00 | 96.8843 | 53.53 | 10 | 0 | 0 | 0 | 1504.1431
6528 | 2023-09-30 00:00 | 97.5038 | 53.53 | 10 | 0 | 0 | 0 | 1510.3377
6529 | 2023-09-30 01:00 | 73.2666 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1401.4365
6530 | 2023-09-30 02:00 | 63.812 | 53.53 | 20 | 10 | 0 | 10.5 | 2346.841
6531 | 2023-09-30 03:00 | 63.7069 | 53.53 | 20 | 10 | 0 | 20 | 2344.7386
6532 | 2023-09-30 04:00 | 76.2265 | 53.53 | 10 | 0 | 0 | 20 | 1297.5648
6533 | 2023-09-30 05:00 | 80.9549 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 67.2425
6534 | 2023-09-30 06:00 | 57.0791 | 53.53 | 20 | 10 | 0 | 20 | 2212.181
6535 | 2023-09-30 07:00 | 99.075 | 53.53 | 0 | 0 | 10 | 10 | 0
6536 | 2023-09-30 08:00 | 88.4903 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1494.9502
6537 | 2023-09-30 09:00 | 88.6505 | 53.53 | 10 | 0 | 0 | 10.5 | 1421.8054
6538 | 2023-09-30 10:00 | 94.2015 | 53.53 | 10 | 0 | 0 | 10.5 | 1477.3149
6539 | 2023-09-30 11:00 | 93.6221 | 53.53 | 10 | 0 | 0 | 10.5 | 1471.5213
6540 | 2023-09-30 12:00 | 86.5621 | 53.53 | 20 | 10 | 0 | 20 | 2801.8416
6541 | 2023-09-30 13:00 | 101.28 | 53.53 | 10 | 0 | 0 | 20 | 1548.0997
6542 | 2023-09-30 14:00 | 101.5503 | 53.53 | 10 | 0 | 0 | 20 | 1550.8026
6543 | 2023-09-30 15:00 | 105.1963 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 79.3632
6544 | 2023-09-30 16:00 | 92.8499 | 53.53 | 20 | 10 | 0 | 20 | 2927.5978
6545 | 2023-09-30 17:00 | 110.6032 | 53.53 | 10 | 0 | 0 | 20 | 1641.3319
6546 | 2023-09-30 18:00 | 110.6711 | 53.53 | 0 | 0 | 10 | 10 | 0
6547 | 2023-09-30 19:00 | 127.3809 | 53.53 | 0 | 0 | 10 | 0 | 0
6548 | 2023-09-30 20:00 | 76.5808 | 53.53 | 20 | 10 | 0 | 9.5 | 2602.2152
6549 | 2023-09-30 21:00 | 84.6595 | 53.53 | 10 | 0 | 0 | 9.5 | 1381.8954
6550 | 2023-09-30 22:00 | 90.9399 | 53.53 | 0.5 | 0 | 9.5 | 0 | 72.2349
6551 | 2023-09-30 23:00 | 78.9494 | 53.53 | 10 | 0 | 0 | 0 | 1324.7937
6552 | 2023-10-01 00:00 | 84.0341 | 53.53 | 10 | 0 | 0 | 0 | 1375.6407
6553 | 2023-10-01 01:00 | 84.9704 | 53.53 | 10 | 0 | 0 | 0 | 1385.004
6554 | 2023-10-01 02:00 | 61.4218 | 53.53 | 20 | 10 | 0 | 9.5 | 2299.0359
6555 | 2023-10-01 03:00 | 66.3865 | 53.53 | 10 | 0 | 0 | 9.5 | 1199.1653
6556 | 2023-10-01 04:00 | 71.0826 | 53.53 | 1.5 | 0 | 8.5 | 1 | 186.9188
6557 | 2023-10-01 05:00 | 64.1876 | 53.53 | 20 | 10 | 0 | 10.5 | 2354.353
6558 | 2023-10-01 06:00 | 62.7203 | 53.53 | 20 | 10 | 0 | 20 | 2325.0056
6559 | 2023-10-01 07:00 | 84.6855 | 53.53 | 10 | 0 | 0 | 20 | 1382.1548
6560 | 2023-10-01 08:00 | 95.8426 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 74.6863
6561 | 2023-10-01 09:00 | 85.7302 | 53.53 | 20 | 10 | 0 | 20 | 2785.204
6562 | 2023-10-01 10:00 | 99.6111 | 53.53 | 10 | 0 | 0 | 20 | 1531.4108
6563 | 2023-10-01 11:00 | 92.7346 | 53.53 | 10 | 0 | 0 | 20 | 1462.6464
6564 | 2023-10-01 12:00 | 107.3992 | 53.53 | 0 | 0 | 10 | 10 | 0
6565 | 2023-10-01 13:00 | 100.7485 | 53.53 | 10 | 0 | 0 | 10 | 1542.7852
6566 | 2023-10-01 14:00 | 106.4112 | 53.53 | 0 | 0 | 10 | 0 | 0
6567 | 2023-10-01 15:00 | 89.3577 | 53.53 | 20 | 10 | 0 | 9.5 | 2857.7545
6568 | 2023-10-01 16:00 | 93.2625 | 53.53 | 20 | 10 | 0 | 19 | 2935.8494
6569 | 2023-10-01 17:00 | 103.1195 | 53.53 | 10 | 0 | 0 | 19 | 1566.4946
6570 | 2023-10-01 18:00 | 106.1314 | 53.53 | 1 | 0 | 9 | 10 | 159.6614
6571 | 2023-10-01 19:00 | 122.2961 | 53.53 | 0 | 0 | 10 | 0 | 0
6572 | 2023-10-01 20:00 | 104.9592 | 53.53 | 10 | 0 | 0 | 0 | 1584.8925
6573 | 2023-10-01 21:00 | 83.6137 | 53.53 | 20 | 10 | 0 | 9.5 | 2742.8747
6574 | 2023-10-01 22:00 | 87.687 | 53.53 | 10 | 0 | 0 | 9.5 | 1412.1703
6575 | 2023-10-01 23:00 | 85.3333 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1461.7192
6576 | 2023-10-02 00:00 | 98.6998 | 53.53 | 0 | 0 | 10 | 0 | 0
6577 | 2023-10-02 01:00 | 83.6437 | 53.53 | 10 | 0 | 0 | 0 | 1371.7373
6578 | 2023-10-02 02:00 | 64.354 | 53.53 | 20 | 10 | 0 | 9.5 | 2357.6795
6579 | 2023-10-02 03:00 | 77.8539 | 53.53 | 1.5 | 0 | 8.5 | 1 | 197.0759
6580 | 2023-10-02 04:00 | 62.83 | 53.53 | 20 | 10 | 0 | 10.5 | 2327.1994
6581 | 2023-10-02 05:00 | 70.7622 | 53.53 | 20 | 10 | 0 | 20 | 2485.844
6582 | 2023-10-02 06:00 | 75.144 | 53.53 | 10 | 0 | 0 | 20 | 1286.7404
6583 | 2023-10-02 07:00 | 97.2185 | 53.53 | 10 | 0 | 0 | 20 | 1507.4851
6584 | 2023-10-02 08:00 | 102.8577 | 65.03 | 10 | 0 | 0 | 20 | 1678.877
6585 | 2023-10-02 09:00 | 101.3003 | 65.03 | 10 | 0 | 0 | 20 | 1663.3027
6586 | 2023-10-02 10:00 | 111.1073 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 88.0687
6587 | 2023-10-02 11:00 | 106.1315 | 65.03 | 10 | 0 | 0 | 10.5 | 1711.6153
6588 | 2023-10-02 12:00 | 99.4876 | 65.03 | 20 | 10 | 0 | 20 | 3290.3518
6589 | 2023-10-02 13:00 | 104.1828 | 65.03 | 10 | 0 | 0 | 20 | 1692.1283
6590 | 2023-10-02 14:00 | 106.9438 | 65.03 | 10 | 0 | 0 | 20 | 1719.7376
6591 | 2023-10-02 15:00 | 120.759 | 65.03 | 0 | 0 | 10 | 10 | 0
6592 | 2023-10-02 16:00 | 110.5494 | 65.03 | 10 | 0 | 0 | 10 | 1755.7941
6593 | 2023-10-02 17:00 | 129.8884 | 66.4 | 0 | 0 | 10 | 0 | 0
6594 | 2023-10-02 18:00 | 114.7137 | 66.4 | 10 | 0 | 0 | 0 | 1811.1372
6595 | 2023-10-02 19:00 | 115.2605 | 65.03 | 10 | 0 | 0 | 0 | 1802.9046
6596 | 2023-10-02 20:00 | 97.1938 | 65.03 | 10 | 0 | 0 | 0 | 1622.2384
6597 | 2023-10-02 21:00 | 97.8444 | 65.03 | 10 | 0 | 0 | 0 | 1628.7437
6598 | 2023-10-02 22:00 | 92.3742 | 65.03 | 10 | 0 | 0 | 0 | 1574.0423
6599 | 2023-10-02 23:00 | -22.8112 | 53.53 | 20 | 10 | 0 | 9.5 | 614.3761
6600 | 2023-10-03 00:00 | -36.7282 | 53.53 | 20 | 10 | 0 | 19 | 336.0355
6601 | 2023-10-03 01:00 | 91.7077 | 53.53 | 0 | 0 | 10 | 9 | 0
6602 | 2023-10-03 02:00 | 79.2056 | 53.53 | 10 | 0 | 0 | 9 | 1327.3562
6603 | 2023-10-03 03:00 | 75.6272 | 53.53 | 10 | 0 | 0 | 9 | 1291.5721
6604 | 2023-10-03 04:00 | 79.9243 | 53.53 | 2 | 0 | 8 | 1 | 266.9085
6605 | 2023-10-03 05:00 | 65.6012 | 53.53 | 20 | 10 | 0 | 10.5 | 2382.6246
6606 | 2023-10-03 06:00 | 72.8294 | 53.53 | 20 | 10 | 0 | 20 | 2527.1875
6607 | 2023-10-03 07:00 | 93.4668 | 53.53 | 10 | 0 | 0 | 20 | 1469.9678
6608 | 2023-10-03 08:00 | 109.0418 | 65.03 | 0 | 0 | 10 | 10 | 0
6609 | 2023-10-03 09:00 | 99.6027 | 65.03 | 10 | 0 | 0 | 10 | 1646.3267
6610 | 2023-10-03 10:00 | 90.7077 | 65.03 | 20 | 10 | 0 | 19.5 | 3114.7543
6611 | 2023-10-03 11:00 | 96.9703 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1705.2668
6612 | 2023-10-03 12:00 | 103.4446 | 65.03 | 10 | 0 | 0 | 20 | 1684.7461
6613 | 2023-10-03 13:00 | 104.3821 | 65.03 | 10 | 0 | 0 | 20 | 1694.1206
6614 | 2023-10-03 14:00 | 120.3281 | 65.03 | 0 | 0 | 10 | 10 | 0
6615 | 2023-10-03 15:00 | 108.6742 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1828.4655
6616 | 2023-10-03 16:00 | 104.5173 | 65.03 | 20 | 10 | 0 | 20 | 3390.9465
6617 | 2023-10-03 17:00 | 118.6565 | 66.4 | 0 | 0 | 10 | 10 | 0
6618 | 2023-10-03 18:00 | 128.7162 | 66.4 | 0 | 0 | 10 | 0 | 0
6619 | 2023-10-03 19:00 | 114.8421 | 65.03 | 10 | 0 | 0 | 0 | 1798.7211
6620 | 2023-10-03 20:00 | 97.868 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1714.7159
6621 | 2023-10-03 21:00 | -49.0442 | 65.03 | 20 | 10 | 0 | 10 | 319.7157
6622 | 2023-10-03 22:00 | 112.1638 | 65.03 | 0 | 0 | 10 | 0 | 0
6623 | 2023-10-03 23:00 | -72.5696 | 53.53 | 20 | 10 | 0 | 9.5 | -380.7927
6624 | 2023-10-04 00:00 | 89.1172 | 53.53 | 0.5 | 0 | 9.5 | 0 | 71.3236
6625 | 2023-10-04 01:00 | -49.4749 | 53.53 | 20 | 10 | 0 | 9.5 | 81.1025
6626 | 2023-10-04 02:00 | -73.7522 | 53.53 | 20 | 10 | 0 | 19 | -404.4444
6627 | 2023-10-04 03:00 | -39.6006 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 153.9562
6628 | 2023-10-04 04:00 | -30.0885 | 53.53 | 10 | 0 | 0 | 20 | 234.4148
6629 | 2023-10-04 05:00 | 69.4428 | 53.53 | 10 | 0 | 0 | 20 | 1229.7282
6630 | 2023-10-04 06:00 | 76.5743 | 53.53 | 10 | 0 | 0 | 20 | 1301.0427
6631 | 2023-10-04 07:00 | 91.3521 | 53.53 | 10 | 0 | 0 | 20 | 1448.821
6632 | 2023-10-04 08:00 | 100.7166 | 65.03 | 10 | 0 | 0 | 20 | 1657.4659
6633 | 2023-10-04 09:00 | 95.6426 | 65.03 | 10 | 0 | 0 | 20 | 1606.726
6634 | 2023-10-04 10:00 | 104.4874 | 65.03 | 10 | 0 | 0 | 20 | 1695.1744
6635 | 2023-10-04 11:00 | 102.5754 | 65.03 | 10 | 0 | 0 | 20 | 1676.0542
6636 | 2023-10-04 12:00 | 101.5987 | 65.03 | 10 | 0 | 0 | 20 | 1666.2868
6637 | 2023-10-04 13:00 | 105.4344 | 65.03 | 10 | 0 | 0 | 20 | 1704.6443
6638 | 2023-10-04 14:00 | 110.1876 | 65.03 | 10 | 0 | 0 | 20 | 1752.1762
6639 | 2023-10-04 15:00 | 109.7547 | 65.03 | 10 | 0 | 0 | 20 | 1747.8475
6640 | 2023-10-04 16:00 | 108.4073 | 65.03 | 10 | 0 | 0 | 20 | 1734.3728
6641 | 2023-10-04 17:00 | 117.1569 | 66.4 | 0 | 0 | 10 | 10 | 0
6642 | 2023-10-04 18:00 | 114.9878 | 66.4 | 0 | 0 | 10 | 0 | 0
6643 | 2023-10-04 19:00 | 112.1764 | 65.03 | 10 | 0 | 0 | 0 | 1772.0636
6644 | 2023-10-04 20:00 | 94.823 | 65.03 | 10 | 0 | 0 | 0 | 1598.5298
6645 | 2023-10-04 21:00 | 99.0461 | 65.03 | 10 | 0 | 0 | 0 | 1640.7612
6646 | 2023-10-04 22:00 | 93.6451 | 65.03 | 10 | 0 | 0 | 0 | 1586.7508
6647 | 2023-10-04 23:00 | 94.6292 | 53.53 | 10 | 0 | 0 | 0 | 1481.5922
6648 | 2023-10-05 00:00 | 87.6117 | 53.53 | 10 | 0 | 0 | 0 | 1411.4169
6649 | 2023-10-05 01:00 | 84.0874 | 53.53 | 10 | 0 | 0 | 0 | 1376.1741
6650 | 2023-10-05 02:00 | 80.8651 | 53.53 | 10 | 0 | 0 | 0 | 1343.951
6651 | 2023-10-05 03:00 | 70.5818 | 53.53 | 10 | 0 | 0 | 0 | 1241.118
6652 | 2023-10-05 04:00 | 68.3467 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1347.0585
6653 | 2023-10-05 05:00 | 66.9046 | 53.53 | 20 | 10 | 0 | 10.5 | 2408.6921
6654 | 2023-10-05 06:00 | -7.4942 | 53.53 | 20 | 10 | 0 | 20 | 920.7158
6655 | 2023-10-05 07:00 | 106.662 | 53.53 | 10 | 0 | 0 | 20 | 1601.92
6656 | 2023-10-05 08:00 | 101.0509 | 65.03 | 10 | 0 | 0 | 20 | 1660.8088
6657 | 2023-10-05 09:00 | 102.3327 | 65.03 | 10 | 0 | 0 | 20 | 1673.6275
6658 | 2023-10-05 10:00 | 113.3778 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 89.2039
6659 | 2023-10-05 11:00 | 93.4214 | 65.03 | 20 | 10 | 0 | 20 | 3169.0286
6660 | 2023-10-05 12:00 | 124.0007 | 65.03 | 0 | 0 | 10 | 10 | 0
6661 | 2023-10-05 13:00 | 130.9432 | 65.03 | 0 | 0 | 10 | 0 | 0
6662 | 2023-10-05 14:00 | 89.9986 | 65.03 | 20 | 10 | 0 | 9.5 | 3100.5727
6663 | 2023-10-05 15:00 | 103.1776 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1859.1369
6664 | 2023-10-05 16:00 | 99.0481 | 65.03 | 20 | 10 | 0 | 20 | 3281.5611
6665 | 2023-10-05 17:00 | 116.9893 | 66.4 | 0 | 0 | 10 | 10 | 0
6666 | 2023-10-05 18:00 | 115.9494 | 66.4 | 10 | 0 | 0 | 10 | 1823.4936
6667 | 2023-10-05 19:00 | 125.7918 | 65.03 | 0 | 0 | 10 | 0 | 0
6668 | 2023-10-05 20:00 | 98.0681 | 65.03 | 10 | 0 | 0 | 0 | 1630.9813
6669 | 2023-10-05 21:00 | 92.9204 | 65.03 | 10 | 0 | 0 | 0 | 1579.5045
6670 | 2023-10-05 22:00 | 97.6397 | 65.03 | 10 | 0 | 0 | 0 | 1626.697
6671 | 2023-10-05 23:00 | 98.0733 | 53.53 | 10 | 0 | 0 | 0 | 1516.0327
6672 | 2023-10-06 00:00 | 86.4256 | 53.53 | 10 | 0 | 0 | 0 | 1399.556
6673 | 2023-10-06 01:00 | -62.9031 | 53.53 | 20 | 10 | 0 | 9.5 | -187.4615
6674 | 2023-10-06 02:00 | -52.8804 | 53.53 | 20 | 10 | 0 | 19 | 12.9926
6675 | 2023-10-06 03:00 | 69.516 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1359.9817
6676 | 2023-10-06 04:00 | 72.8891 | 53.53 | 10 | 0 | 0 | 20 | 1264.1909
6677 | 2023-10-06 05:00 | 71.086 | 53.53 | 10 | 0 | 0 | 20 | 1246.1599
6678 | 2023-10-06 06:00 | 78.3662 | 53.53 | 10 | 0 | 0 | 20 | 1318.9622
6679 | 2023-10-06 07:00 | 111.4497 | 53.53 | 10 | 0 | 0 | 20 | 1649.7971
6680 | 2023-10-06 08:00 | 108.6491 | 65.03 | 0 | 0 | 10 | 10 | 0
6681 | 2023-10-06 09:00 | 94.7514 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1681.9097
6682 | 2023-10-06 10:00 | 95.4029 | 65.03 | 10 | 0 | 0 | 10.5 | 1604.329
6683 | 2023-10-06 11:00 | 101.0782 | 65.03 | 10 | 0 | 0 | 10.5 | 1661.082
6684 | 2023-10-06 12:00 | 101.9654 | 65.03 | 10 | 0 | 0 | 10.5 | 1669.9537
6685 | 2023-10-06 13:00 | 93.8122 | 65.03 | 20 | 10 | 0 | 20 | 3176.8432
6686 | 2023-10-06 14:00 | 110.8645 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.9472
6687 | 2023-10-06 15:00 | 96.9453 | 65.03 | 20 | 10 | 0 | 20 | 3239.5062
6688 | 2023-10-06 16:00 | 118.0274 | 65.03 | 10 | 0 | 0 | 20 | 1830.574
6689 | 2023-10-06 17:00 | 137.0648 | 66.4 | 0 | 0 | 10 | 10 | 0
6690 | 2023-10-06 18:00 | 117.104 | 66.4 | 10 | 0 | 0 | 10 | 1835.0405
6691 | 2023-10-06 19:00 | 122.4172 | 65.03 | 0 | 0 | 10 | 0 | 0
6692 | 2023-10-06 20:00 | 91.1738 | 65.03 | 20 | 10 | 0 | 9.5 | 3124.0769
6693 | 2023-10-06 21:00 | 104.0421 | 65.03 | 0.5 | 0 | 9.5 | 0 | 84.536
6694 | 2023-10-06 22:00 | 95.4277 | 65.03 | 10 | 0 | 0 | 0 | 1604.5768
6695 | 2023-10-06 23:00 | 86.9404 | 53.53 | 10 | 0 | 0 | 0 | 1404.7036
6696 | 2023-10-07 00:00 | 83.8198 | 53.53 | 10 | 0 | 0 | 0 | 1373.4981
6697 | 2023-10-07 01:00 | 82.6383 | 53.53 | 10 | 0 | 0 | 0 | 1361.6825
6698 | 2023-10-07 02:00 | 63.5748 | 53.53 | 20 | 10 | 0 | 9.5 | 2342.0956
6699 | 2023-10-07 03:00 | 74.1392 | 53.53 | 0.5 | 0 | 9.5 | 0 | 63.8346
6700 | 2023-10-07 04:00 | 60.6509 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1261.9991
6701 | 2023-10-07 05:00 | -42.93 | 53.53 | 20 | 10 | 0 | 10.5 | 212.0006
6702 | 2023-10-07 06:00 | 57.698 | 53.53 | 20 | 10 | 0 | 20 | 2224.5591
6703 | 2023-10-07 07:00 | 101.4876 | 53.53 | 0 | 0 | 10 | 10 | 0
6704 | 2023-10-07 08:00 | 89.3273 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1503.7606
6705 | 2023-10-07 09:00 | 95.8907 | 53.53 | 10 | 0 | 0 | 10.5 | 1494.2071
6706 | 2023-10-07 10:00 | 92.4794 | 53.53 | 10 | 0 | 0 | 10.5 | 1460.0939
6707 | 2023-10-07 11:00 | -71.4042 | 53.53 | 20 | 10 | 0 | 20 | -357.4846
6708 | 2023-10-07 12:00 | 102.6925 | 53.53 | 10 | 0 | 0 | 20 | 1562.2248
6709 | 2023-10-07 13:00 | 110.1041 | 53.53 | 0 | 0 | 10 | 10 | 0
6710 | 2023-10-07 14:00 | 106.6298 | 53.53 | 0 | 0 | 10 | 0 | 0
6711 | 2023-10-07 15:00 | 93.039 | 53.53 | 20 | 10 | 0 | 9.5 | 2931.3807
6712 | 2023-10-07 16:00 | 97.3191 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1587.8856
6713 | 2023-10-07 17:00 | 105.67 | 53.53 | 0 | 0 | 10 | 0 | 0
6714 | 2023-10-07 18:00 | 104.4658 | 53.53 | 10 | 0 | 0 | 0 | 1579.9577
6715 | 2023-10-07 19:00 | 103.6235 | 53.53 | 10 | 0 | 0 | 0 | 1571.5347
6716 | 2023-10-07 20:00 | 87.8228 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1562.3203
6717 | 2023-10-07 21:00 | 92.8422 | 53.53 | 10 | 0 | 0 | 1 | 1463.7222
6718 | 2023-10-07 22:00 | 79.9864 | 53.53 | 20 | 10 | 0 | 10.5 | 2670.3283
6719 | 2023-10-07 23:00 | 85.5531 | 53.53 | 20 | 10 | 0 | 20 | 2781.6612
6720 | 2023-10-08 00:00 | 100.2951 | 53.53 | 0 | 0 | 10 | 10 | 0
6721 | 2023-10-08 01:00 | 95.9018 | 53.53 | 0 | 0 | 10 | 0 | 0
6722 | 2023-10-08 02:00 | 61.8731 | 53.53 | 12.1053 | 2.1053 | 0 | 2 | 1396.9847
6723 | 2023-10-08 03:00 | 57.3399 | 53.53 | 20 | 10 | 0 | 11.5 | 2217.3979
6724 | 2023-10-08 04:00 | 69.5962 | 53.53 | 0 | 0 | 10 | 1.5 | 0
6725 | 2023-10-08 05:00 | 53.3723 | 53.53 | 20 | 10 | 0 | 11 | 2138.0463
6726 | 2023-10-08 06:00 | 75.7786 | 53.53 | 0 | 0 | 10 | 1 | 0
6727 | 2023-10-08 07:00 | -31.4785 | 53.53 | 20 | 10 | 0 | 10.5 | 441.0304
6728 | 2023-10-08 08:00 | -42.4446 | 53.53 | 20 | 10 | 0 | 20 | 221.7089
6729 | 2023-10-08 09:00 | 85.7897 | 53.53 | 10 | 0 | 0 | 20 | 1393.1974
6730 | 2023-10-08 10:00 | 103.8262 | 53.53 | 0 | 0 | 10 | 10 | 0
6731 | 2023-10-08 11:00 | 95.1557 | 53.53 | 10 | 0 | 0 | 10 | 1486.8574
6732 | 2023-10-08 12:00 | 93.5347 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1548.0499
6733 | 2023-10-08 13:00 | 87.4738 | 53.53 | 20 | 10 | 0 | 20 | 2820.0752
6734 | 2023-10-08 14:00 | 100.7906 | 53.53 | 10 | 0 | 0 | 20 | 1543.2058
6735 | 2023-10-08 15:00 | 101.5203 | 53.53 | 10 | 0 | 0 | 20 | 1550.5026
6736 | 2023-10-08 16:00 | 113.6075 | 53.53 | 0 | 0 | 10 | 10 | 0
6737 | 2023-10-08 17:00 | 119.7264 | 53.53 | 0 | 0 | 10 | 0 | 0
6738 | 2023-10-08 18:00 | 106.8183 | 53.53 | 10 | 0 | 0 | 0 | 1603.4834
6739 | 2023-10-08 19:00 | -50.6843 | 53.53 | 20 | 10 | 0 | 9.5 | 56.9132
6740 | 2023-10-08 20:00 | -58.0575 | 53.53 | 20 | 10 | 0 | 19 | -90.5504
6741 | 2023-10-08 21:00 | 104.7924 | 53.53 | 0 | 0 | 10 | 9 | 0
6742 | 2023-10-08 22:00 | 85.6932 | 53.53 | 20 | 10 | 0 | 18.5 | 2784.4638
6743 | 2023-10-08 23:00 | 99.8743 | 53.53 | 0 | 0 | 10 | 8.5 | 0
6744 | 2023-10-09 00:00 | 98.1635 | 53.53 | 1.5 | 0 | 8.5 | 0 | 227.5402
6745 | 2023-10-09 01:00 | 96.4992 | 53.53 | 10 | 0 | 0 | 0 | 1500.2916
6746 | 2023-10-09 02:00 | 71.6996 | 53.53 | 20 | 10 | 0 | 9.5 | 2504.5911
6747 | 2023-10-09 03:00 | 79.3785 | 53.53 | 2 | 0 | 8 | 1.5 | 265.817
6748 | 2023-10-09 04:00 | 73.7825 | 53.53 | 10 | 0 | 0 | 1.5 | 1273.1254
6749 | 2023-10-09 05:00 | 71.2771 | 53.53 | 20 | 10 | 0 | 11 | 2496.1411
6750 | 2023-10-09 06:00 | 79.7033 | 53.53 | 0 | 0 | 10 | 1 | 0
6751 | 2023-10-09 07:00 | -22.4254 | 53.53 | 20 | 10 | 0 | 10.5 | 622.0928
6752 | 2023-10-09 08:00 | -14.7125 | 65.03 | 20 | 10 | 0 | 20 | 1006.3504
6753 | 2023-10-09 09:00 | 108.8272 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 86.9286
6754 | 2023-10-09 10:00 | 103.423 | 65.03 | 10 | 0 | 0 | 10.5 | 1684.5299
6755 | 2023-10-09 11:00 | 107.8477 | 65.03 | 10 | 0 | 0 | 10.5 | 1728.7769
6756 | 2023-10-09 12:00 | 100.7159 | 65.03 | 10 | 0 | 0 | 10.5 | 1657.4593
6757 | 2023-10-09 13:00 | 96.2926 | 65.03 | 20 | 10 | 0 | 20 | 3226.451
6758 | 2023-10-09 14:00 | 120.971 | 65.03 | 0 | 0 | 10 | 10 | 0
6759 | 2023-10-09 15:00 | 118.6582 | 65.03 | 10 | 0 | 0 | 10 | 1836.8822
6760 | 2023-10-09 16:00 | 111.4885 | 65.03 | 10 | 0 | 0 | 10 | 1765.185
6761 | 2023-10-09 17:00 | 116.1525 | 66.4 | 10 | 0 | 0 | 10 | 1825.5255
6762 | 2023-10-09 18:00 | 116.7444 | 66.4 | 10 | 0 | 0 | 10 | 1831.4441
6763 | 2023-10-09 19:00 | 131.7462 | 65.03 | 0 | 0 | 10 | 0 | 0
6764 | 2023-10-09 20:00 | 96.3806 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1699.0587
6765 | 2023-10-09 21:00 | 94.5771 | 65.03 | 20 | 10 | 0 | 10 | 3192.1421
6766 | 2023-10-09 22:00 | 117.7383 | 65.03 | 0 | 0 | 10 | 0 | 0
6767 | 2023-10-09 23:00 | 93.5433 | 53.53 | 20 | 10 | 0 | 9.5 | 2941.4654
6768 | 2023-10-10 00:00 | 111.394 | 53.53 | 0.5 | 0 | 9.5 | 0 | 82.462
6769 | 2023-10-10 01:00 | 85.3324 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1461.7095
6770 | 2023-10-10 02:00 | 78.1031 | 53.53 | 20 | 10 | 0 | 10 | 2632.6611
6771 | 2023-10-10 03:00 | 95.4331 | 53.53 | 0 | 0 | 10 | 0 | 0
6772 | 2023-10-10 04:00 | 74.1224 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1410.8953
6773 | 2023-10-10 05:00 | 71.9947 | 53.53 | 20 | 10 | 0 | 10.5 | 2510.4931
6774 | 2023-10-10 06:00 | 66.5098 | 53.53 | 20 | 10 | 0 | 20 | 2400.7955
6775 | 2023-10-10 07:00 | 103.4888 | 53.53 | 10 | 0 | 0 | 20 | 1570.1879
6776 | 2023-10-10 08:00 | 98.741 | 65.03 | 10 | 0 | 0 | 20 | 1637.7103
6777 | 2023-10-10 09:00 | 103.1973 | 65.03 | 10 | 0 | 0 | 20 | 1682.2726
6778 | 2023-10-10 10:00 | 96.1606 | 65.03 | 10 | 0 | 0 | 20 | 1611.9061
6779 | 2023-10-10 11:00 | 118.7811 | 65.03 | 0 | 0 | 10 | 10 | 0
6780 | 2023-10-10 12:00 | 114.2498 | 65.03 | 0 | 0 | 10 | 0 | 0
6781 | 2023-10-10 13:00 | 103.6625 | 65.03 | 20 | 10 | 0 | 9.5 | 3373.8508
6782 | 2023-10-10 14:00 | 96.5818 | 65.03 | 20 | 10 | 0 | 19 | 3232.2358
6783 | 2023-10-10 15:00 | 118.5307 | 65.03 | 0 | 0 | 10 | 9 | 0
6784 | 2023-10-10 16:00 | 101.2991 | 65.03 | 20 | 10 | 0 | 18.5 | 3326.582
6785 | 2023-10-10 17:00 | 111.8434 | 66.4 | 1.5 | 0 | 8.5 | 10 | 267.365
6786 | 2023-10-10 18:00 | 108.6335 | 66.4 | 10 | 0 | 0 | 10 | 1750.3352
6787 | 2023-10-10 19:00 | 114.4941 | 65.03 | 0 | 0 | 10 | 0 | 0
6788 | 2023-10-10 20:00 | 90.0574 | 65.03 | 20 | 10 | 0 | 9.5 | 3101.7485
6789 | 2023-10-10 21:00 | 94.6376 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1680.7115
6790 | 2023-10-10 22:00 | 105.1539 | 65.03 | 0 | 0 | 10 | 0 | 0
6791 | 2023-10-10 23:00 | 91.2356 | 53.53 | 10 | 0 | 0 | 0 | 1447.6556
6792 | 2023-10-11 00:00 | 96.7135 | 53.53 | 10 | 0 | 0 | 0 | 1502.4354
6793 | 2023-10-11 01:00 | 89.0215 | 53.53 | 10 | 0 | 0 | 0 | 1425.5155
6794 | 2023-10-11 02:00 | 74.3919 | 53.53 | 20 | 10 | 0 | 9.5 | 2558.4377
6795 | 2023-10-11 03:00 | 93.383 | 53.53 | 0.5 | 0 | 9.5 | 0 | 73.4565
6796 | 2023-10-11 04:00 | -40.3716 | 53.53 | 20 | 10 | 0 | 9.5 | 263.168
6797 | 2023-10-11 05:00 | 76.9544 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1442.1956
6798 | 2023-10-11 06:00 | -35.0595 | 53.53 | 20 | 10 | 0 | 20 | 369.4099
6799 | 2023-10-11 07:00 | 108.3433 | 53.53 | 10 | 0 | 0 | 20 | 1618.7332
6800 | 2023-10-11 08:00 | 100.5636 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 82.7968
6801 | 2023-10-11 09:00 | -70.2891 | 65.03 | 20 | 10 | 0 | 20 | -105.181
6802 | 2023-10-11 10:00 | 102.9913 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 84.0107
6803 | 2023-10-11 11:00 | -38.6545 | 65.03 | 20 | 10 | 0 | 20 | 527.5108
6804 | 2023-10-11 12:00 | 109.4732 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.2516
6805 | 2023-10-11 13:00 | 100.7252 | 65.03 | 20 | 10 | 0 | 20 | 3315.1044
6806 | 2023-10-11 14:00 | 113.5882 | 65.03 | 0 | 0 | 10 | 10 | 0
6807 | 2023-10-11 15:00 | 98.8075 | 65.03 | 20 | 10 | 0 | 19.5 | 3276.7495
6808 | 2023-10-11 16:00 | 110.4698 | 65.03 | 1 | 0 | 9 | 10.5 | 175.4998
6809 | 2023-10-11 17:00 | 116.1366 | 66.4 | 0 | 0 | 10 | 0.5 | 0
6810 | 2023-10-11 18:00 | -79.1945 | 66.4 | 20 | 10 | 0 | 10 | -255.8892
6811 | 2023-10-11 19:00 | 115.6628 | 65.03 | 0 | 0 | 10 | 0 | 0
6812 | 2023-10-11 20:00 | 99.2759 | 65.03 | 10 | 0 | 0 | 0 | 1643.0595
6813 | 2023-10-11 21:00 | 92.0084 | 65.03 | 20 | 10 | 0 | 9.5 | 3140.7674
6814 | 2023-10-11 22:00 | 100.8257 | 65.03 | 0.5 | 0 | 9.5 | 0 | 82.9278
6815 | 2023-10-11 23:00 | -64.0663 | 53.53 | 20 | 10 | 0 | 9.5 | -210.727
6816 | 2023-10-12 00:00 | -9.1732 | 53.53 | 20 | 10 | 0 | 19 | 887.1361
6817 | 2023-10-12 01:00 | 93.489 | 53.53 | 0 | 0 | 10 | 9 | 0
6818 | 2023-10-12 02:00 | 74.9238 | 53.53 | 10 | 0 | 0 | 9 | 1284.5381
6819 | 2023-10-12 03:00 | 69.6778 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1426.6171
6820 | 2023-10-12 04:00 | 72.951 | 53.53 | 10 | 0 | 0 | 10.5 | 1264.8103
6821 | 2023-10-12 05:00 | 67.3879 | 53.53 | 20 | 10 | 0 | 20 | 2418.3588
6822 | 2023-10-12 06:00 | 99.4297 | 53.53 | 10 | 0 | 0 | 20 | 1529.5975
6823 | 2023-10-12 07:00 | 103.2486 | 53.53 | 10 | 0 | 0 | 20 | 1567.7863
6824 | 2023-10-12 08:00 | 106.0328 | 65.03 | 0 | 0 | 10 | 10 | 0
6825 | 2023-10-12 09:00 | 114.433 | 65.03 | 0 | 0 | 10 | 0 | 0
6826 | 2023-10-12 10:00 | 92.7043 | 65.03 | 10 | 0 | 0 | 0 | 1577.3426
6827 | 2023-10-12 11:00 | 90.5049 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1719.0698
6828 | 2023-10-12 12:00 | -25.674 | 65.03 | 20 | 10 | 0 | 10.5 | 787.1197
6829 | 2023-10-12 13:00 | -30.1301 | 65.03 | 20 | 10 | 0 | 20 | 697.9973
6830 | 2023-10-12 14:00 | 102.1853 | 65.03 | 10 | 0 | 0 | 20 | 1672.1528
6831 | 2023-10-12 15:00 | 105.4893 | 65.03 | 10 | 0 | 0 | 20 | 1705.1931
6832 | 2023-10-12 16:00 | 111.8486 | 65.03 | 10 | 0 | 0 | 20 | 1768.786
6833 | 2023-10-12 17:00 | 111.6663 | 66.4 | 10 | 0 | 0 | 20 | 1780.6626
6834 | 2023-10-12 18:00 | 122.0826 | 66.4 | 0 | 0 | 10 | 10 | 0
6835 | 2023-10-12 19:00 | 119.0065 | 65.03 | 0 | 0 | 10 | 0 | 0
6836 | 2023-10-12 20:00 | 101.6453 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1754.4772
6837 | 2023-10-12 21:00 | -17.8614 | 65.03 | 20 | 10 | 0 | 10 | 943.3712
6838 | 2023-10-12 22:00 | 111.7553 | 65.03 | 0 | 0 | 10 | 0 | 0
6839 | 2023-10-12 23:00 | -59.0132 | 53.53 | 20 | 10 | 0 | 9.5 | -109.6648
6840 | 2023-10-13 00:00 | 111.4675 | 53.53 | 0.5 | 0 | 9.5 | 0 | 82.4987
6841 | 2023-10-13 01:00 | 88.6208 | 53.53 | 10 | 0 | 0 | 0 | 1421.5079
6842 | 2023-10-13 02:00 | 80.1391 | 53.53 | 10 | 0 | 0 | 0 | 1336.6908
6843 | 2023-10-13 03:00 | 73.4548 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1403.5159
6844 | 2023-10-13 04:00 | 71.5572 | 53.53 | 20 | 10 | 0 | 10.5 | 2501.7443
6845 | 2023-10-13 05:00 | 79.1203 | 53.53 | 10 | 0 | 0 | 10.5 | 1326.5031
6846 | 2023-10-13 06:00 | 71.7523 | 53.53 | 20 | 10 | 0 | 20 | 2505.645
6847 | 2023-10-13 07:00 | 80.1474 | 53.53 | 10 | 0 | 0 | 20 | 1336.7738
6848 | 2023-10-13 08:00 | 88.8726 | 65.03 | 10 | 0 | 0 | 20 | 1539.0264
6849 | 2023-10-13 09:00 | 115.5186 | 65.03 | 0 | 0 | 10 | 10 | 0
6850 | 2023-10-13 10:00 | 115.0583 | 65.03 | 10 | 0 | 0 | 10 | 1800.883
6851 | 2023-10-13 11:00 | 122.9374 | 65.03 | 0 | 0 | 10 | 0 | 0
6852 | 2023-10-13 12:00 | 103.7672 | 65.03 | 10 | 0 | 0 | 0 | 1687.9719
6853 | 2023-10-13 13:00 | 95.8622 | 65.03 | 20 | 10 | 0 | 9.5 | 3217.8434
6854 | 2023-10-13 14:00 | 100.9414 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1834.4211
6855 | 2023-10-13 15:00 | 103.9841 | 65.03 | 10 | 0 | 0 | 10.5 | 1690.1414
6856 | 2023-10-13 16:00 | 97.3797 | 65.03 | 20 | 10 | 0 | 20 | 3248.1939
6857 | 2023-10-13 17:00 | 134.8932 | 66.4 | 0 | 0 | 10 | 10 | 0
6858 | 2023-10-13 18:00 | 142.8447 | 66.4 | 0 | 0 | 10 | 0 | 0
6859 | 2023-10-13 19:00 | 122.7555 | 65.03 | 10 | 0 | 0 | 0 | 1877.8552
6860 | 2023-10-13 20:00 | 98.817 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1724.7048
6861 | 2023-10-13 21:00 | 90.8503 | 65.03 | 20 | 10 | 0 | 10 | 3117.6061
6862 | 2023-10-13 22:00 | 113.6561 | 65.03 | 0 | 0 | 10 | 0 | 0
6863 | 2023-10-13 23:00 | 94.4772 | 53.53 | 10 | 0 | 0 | 0 | 1480.0721
6864 | 2023-10-14 00:00 | 83.821 | 53.53 | 10 | 0 | 0 | 0 | 1373.5098
6865 | 2023-10-14 01:00 | 89.7806 | 53.53 | 10 | 0 | 0 | 0 | 1433.1058
6866 | 2023-10-14 02:00 | 61.8698 | 53.53 | 20 | 10 | 0 | 9.5 | 2307.9953
6867 | 2023-10-14 03:00 | 67.0245 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1332.4445
6868 | 2023-10-14 04:00 | 57.1165 | 53.53 | 20 | 10 | 0 | 20 | 2212.9307
6869 | 2023-10-14 05:00 | 75.5381 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 64.534
6870 | 2023-10-14 06:00 | 65.1274 | 53.53 | 20 | 10 | 0 | 20 | 2373.1472
6871 | 2023-10-14 07:00 | 96.2914 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 74.9107
6872 | 2023-10-14 08:00 | 94.4344 | 53.53 | 10 | 0 | 0 | 10.5 | 1479.644
6873 | 2023-10-14 09:00 | 94.8974 | 53.53 | 10 | 0 | 0 | 10.5 | 1484.274
6874 | 2023-10-14 10:00 | 88.2759 | 53.53 | 20 | 10 | 0 | 20 | 2836.1176
6875 | 2023-10-14 11:00 | 102.2981 | 53.53 | 0 | 0 | 10 | 10 | 0
6876 | 2023-10-14 12:00 | 90.1216 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1512.1223
6877 | 2023-10-14 13:00 | 92.5038 | 53.53 | 10 | 0 | 0 | 10.5 | 1460.3383
6878 | 2023-10-14 14:00 | 95.9062 | 53.53 | 10 | 0 | 0 | 10.5 | 1494.3616
6879 | 2023-10-14 15:00 | 96.8242 | 53.53 | 10 | 0 | 0 | 10.5 | 1503.5422
6880 | 2023-10-14 16:00 | 85.8833 | 53.53 | 20 | 10 | 0 | 20 | 2788.2652
6881 | 2023-10-14 17:00 | 109.2258 | 53.53 | 0 | 0 | 10 | 10 | 0
6882 | 2023-10-14 18:00 | 117.6341 | 53.53 | 0 | 0 | 10 | 0 | 0
6883 | 2023-10-14 19:00 | 108.2159 | 53.53 | 10 | 0 | 0 | 0 | 1617.4588
6884 | 2023-10-14 20:00 | 89.2684 | 53.53 | 10 | 0 | 0 | 0 | 1427.9838
6885 | 2023-10-14 21:00 | 92.1465 | 53.53 | 10 | 0 | 0 | 0 | 1456.7651
6886 | 2023-10-14 22:00 | 89.9712 | 53.53 | 10 | 0 | 0 | 0 | 1435.0123
6887 | 2023-10-14 23:00 | 79.25 | 53.53 | 20 | 10 | 0 | 9.5 | 2655.5997
6888 | 2023-10-15 00:00 | 85.6272 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1464.8125
6889 | 2023-10-15 01:00 | 94.5848 | 53.53 | 0 | 0 | 10 | 0 | 0
6890 | 2023-10-15 02:00 | 59.1366 | 53.53 | 20 | 10 | 0 | 9.5 | 2253.3319
6891 | 2023-10-15 03:00 | 63.2417 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1290.6347
6892 | 2023-10-15 04:00 | 57.4152 | 53.53 | 20 | 10 | 0 | 20 | 2218.9049
6893 | 2023-10-15 05:00 | 74.0565 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 63.7933
6894 | 2023-10-15 06:00 | 65.2151 | 53.53 | 20 | 10 | 0 | 20 | 2374.9026
6895 | 2023-10-15 07:00 | 80.2701 | 53.53 | 10 | 0 | 0 | 20 | 1338.0006
6896 | 2023-10-15 08:00 | 96.6 | 53.53 | 0 | 0 | 10 | 10 | 0
6897 | 2023-10-15 09:00 | 88.3214 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1493.1725
6898 | 2023-10-15 10:00 | 89.2336 | 53.53 | 10 | 0 | 0 | 10.5 | 1427.6359
6899 | 2023-10-15 11:00 | 87.0308 | 53.53 | 20 | 10 | 0 | 20 | 2811.2161
6900 | 2023-10-15 12:00 | 89.0514 | 53.53 | 10 | 0 | 0 | 20 | 1425.8142
6901 | 2023-10-15 13:00 | 108.4635 | 53.53 | 0 | 0 | 10 | 10 | 0
6902 | 2023-10-15 14:00 | 90.9626 | 53.53 | 20 | 10 | 0 | 19.5 | 2889.8514
6903 | 2023-10-15 15:00 | 99.6513 | 53.53 | 1 | 0 | 9 | 10.5 | 153.1813
6904 | 2023-10-15 16:00 | 90.351 | 53.53 | 20 | 10 | 0 | 20 | 2877.6199
6905 | 2023-10-15 17:00 | 117.296 | 53.53 | 0 | 0 | 10 | 10 | 0
6906 | 2023-10-15 18:00 | 104.2744 | 53.53 | 10 | 0 | 0 | 10 | 1578.0441
6907 | 2023-10-15 19:00 | 111.1943 | 53.53 | 0.5 | 0 | 9.5 | 0.5 | 82.3621
6908 | 2023-10-15 20:00 | 91.2978 | 53.53 | 20 | 10 | 0 | 10 | 2896.557
6909 | 2023-10-15 21:00 | 116.1587 | 53.53 | 0 | 0 | 10 | 0 | 0
6910 | 2023-10-15 22:00 | 96.1032 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1575.0861
6911 | 2023-10-15 23:00 | 81.8246 | 53.53 | 20 | 10 | 0 | 10 | 2707.0912
6912 | 2023-10-16 00:00 | 99.6022 | 53.53 | 10 | 0 | 0 | 10 | 1531.3223
6913 | 2023-10-16 01:00 | 116.3792 | 53.53 | 0 | 0 | 10 | 0 | 0
6914 | 2023-10-16 02:00 | 64.231 | 53.53 | 20 | 10 | 0 | 9.5 | 2355.2193
6915 | 2023-10-16 03:00 | 68.315 | 53.53 | 20 | 10 | 0 | 19 | 2436.8992
6916 | 2023-10-16 04:00 | 72.1832 | 53.53 | 10 | 0 | 0 | 19 | 1257.1324
6917 | 2023-10-16 05:00 | 70.9579 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1375.9193
6918 | 2023-10-16 06:00 | 71.5232 | 53.53 | 10 | 0 | 0 | 20 | 1250.5316
6919 | 2023-10-16 07:00 | 85.8033 | 53.53 | 10 | 0 | 0 | 20 | 1393.3325
6920 | 2023-10-16 08:00 | 116.9925 | 65.03 | 0 | 0 | 10 | 10 | 0
6921 | 2023-10-16 09:00 | 95.2134 | 65.03 | 20 | 10 | 0 | 19.5 | 3204.8688
6922 | 2023-10-16 10:00 | 102.4409 | 65.03 | 10 | 0 | 0 | 19.5 | 1674.7092
6923 | 2023-10-16 11:00 | 113.112 | 65.03 | 0 | 0 | 10 | 9.5 | 0
6924 | 2023-10-16 12:00 | 103.6729 | 65.03 | 10 | 0 | 0 | 9.5 | 1687.0294
6925 | 2023-10-16 13:00 | 97.5336 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1796.7556
6926 | 2023-10-16 14:00 | 95.5794 | 65.03 | 20 | 10 | 0 | 20 | 3212.187
6927 | 2023-10-16 15:00 | 102.2315 | 65.03 | 10 | 0 | 0 | 20 | 1672.6148
6928 | 2023-10-16 16:00 | 98.8192 | 65.03 | 10 | 0 | 0 | 20 | 1638.4916
6929 | 2023-10-16 17:00 | 120.4859 | 66.4 | 0 | 0 | 10 | 10 | 0
6930 | 2023-10-16 18:00 | 110.3173 | 66.4 | 10 | 0 | 0 | 10 | 1767.1733
6931 | 2023-10-16 19:00 | 125.8041 | 65.03 | 0 | 0 | 10 | 0 | 0
6932 | 2023-10-16 20:00 | 99.7801 | 65.03 | 20 | 10 | 0 | 9.5 | 3296.2025
6933 | 2023-10-16 21:00 | 100.3634 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1740.9832
6934 | 2023-10-16 22:00 | 112.4191 | 65.03 | 0 | 0 | 10 | 0 | 0
6935 | 2023-10-16 23:00 | -54.3999 | 53.53 | 20 | 10 | 0 | 9.5 | -17.3974
6936 | 2023-10-17 00:00 | -31.8685 | 53.53 | 20 | 10 | 0 | 19 | 433.2296
6937 | 2023-10-17 01:00 | 90.1099 | 53.53 | 0 | 0 | 10 | 9 | 0
6938 | 2023-10-17 02:00 | 72.4953 | 53.53 | 10 | 0 | 0 | 9 | 1260.2527
6939 | 2023-10-17 03:00 | 73.2253 | 53.53 | 10 | 0 | 0 | 9 | 1267.5529
6940 | 2023-10-17 04:00 | 68.3837 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1411.6326
6941 | 2023-10-17 05:00 | 62.5239 | 53.53 | 20 | 10 | 0 | 20 | 2321.0781
6942 | 2023-10-17 06:00 | 70.0263 | 53.53 | 10 | 0 | 0 | 20 | 1235.5626
6943 | 2023-10-17 07:00 | 96.748 | 53.53 | 10 | 0 | 0 | 20 | 1502.7804
6944 | 2023-10-17 08:00 | 104.9414 | 65.03 | 10 | 0 | 0 | 20 | 1699.7142
6945 | 2023-10-17 09:00 | 114.7268 | 65.03 | 10 | 0 | 0 | 20 | 1797.5675
6946 | 2023-10-17 10:00 | 123.847 | 65.03 | 0 | 0 | 10 | 10 | 0
6947 | 2023-10-17 11:00 | 110.2942 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1845.5175
6948 | 2023-10-17 12:00 | 116.7483 | 65.03 | 10 | 0 | 0 | 10.5 | 1817.7835
6949 | 2023-10-17 13:00 | 110.3643 | 65.03 | 10 | 0 | 0 | 10.5 | 1753.9432
6950 | 2023-10-17 14:00 | -39.8056 | 65.03 | 20 | 10 | 0 | 20 | 504.4876
6951 | 2023-10-17 15:00 | 122.458 | 65.03 | 0 | 0 | 10 | 10 | 0
6952 | 2023-10-17 16:00 | 112.154 | 65.03 | 10 | 0 | 0 | 10 | 1771.8398
6953 | 2023-10-17 17:00 | 124.7993 | 66.4 | 0 | 0 | 10 | 0 | 0
6954 | 2023-10-17 18:00 | 117.4055 | 66.4 | 10 | 0 | 0 | 0 | 1838.0549
6955 | 2023-10-17 19:00 | 118.5902 | 65.03 | 10 | 0 | 0 | 0 | 1836.2019
6956 | 2023-10-17 20:00 | 96.4887 | 65.03 | 10 | 0 | 0 | 0 | 1615.187
6957 | 2023-10-17 21:00 | 104.0202 | 65.03 | 10 | 0 | 0 | 0 | 1690.5017
6958 | 2023-10-17 22:00 | 94.0396 | 65.03 | 10 | 0 | 0 | 0 | 1590.6959
6959 | 2023-10-17 23:00 | 92.5053 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1537.2139
6960 | 2023-10-18 00:00 | 81.2319 | 53.53 | 20 | 10 | 0 | 10 | 2695.2375
6961 | 2023-10-18 01:00 | 110.82 | 53.53 | 0 | 0 | 10 | 0 | 0
6962 | 2023-10-18 02:00 | 72.2982 | 53.53 | 20 | 10 | 0 | 9.5 | 2516.5649
6963 | 2023-10-18 03:00 | 77.5597 | 53.53 | 20 | 10 | 0 | 19 | 2621.7934
6964 | 2023-10-18 04:00 | 87.6127 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 211.7141
6965 | 2023-10-18 05:00 | -61.999 | 53.53 | 20 | 10 | 0 | 20 | -169.3801
6966 | 2023-10-18 06:00 | 87.4569 | 53.53 | 10 | 0 | 0 | 20 | 1409.869
6967 | 2023-10-18 07:00 | 86.1232 | 53.53 | 10 | 0 | 0 | 20 | 1396.5318
6968 | 2023-10-18 08:00 | 130.2187 | 65.03 | 0 | 0 | 10 | 10 | 0
6969 | 2023-10-18 09:00 | 113.5383 | 65.03 | 10 | 0 | 0 | 10 | 1785.683
6970 | 2023-10-18 10:00 | 105.5176 | 65.03 | 10 | 0 | 0 | 10 | 1705.4761
6971 | 2023-10-18 11:00 | 117.2347 | 65.03 | 0 | 0 | 10 | 0 | 0
6972 | 2023-10-18 12:00 | 96.5051 | 65.03 | 20 | 10 | 0 | 9.5 | 3230.7022
6973 | 2023-10-18 13:00 | 101.8248 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1756.3659
6974 | 2023-10-18 14:00 | 117.4558 | 65.03 | 0 | 0 | 10 | 0 | 0
6975 | 2023-10-18 15:00 | 93.1768 | 65.03 | 10 | 0 | 0 | 0 | 1582.0685
6976 | 2023-10-18 16:00 | -13.9668 | 65.03 | 20 | 10 | 0 | 9.5 | 1021.2649
6977 | 2023-10-18 17:00 | -7.8782 | 66.4 | 11.0526 | 1.0526 | 0 | 10.5 | 646.8194
6978 | 2023-10-18 18:00 | -78.2331 | 66.4 | 20 | 10 | 0 | 20 | -236.6626
6979 | 2023-10-18 19:00 | 109.4472 | 65.03 | 0 | 0 | 10 | 10 | 0
6980 | 2023-10-18 20:00 | 114.4171 | 65.03 | 0 | 0 | 10 | 0 | 0
6981 | 2023-10-18 21:00 | 95.0355 | 65.03 | 10 | 0 | 0 | 0 | 1600.6551
6982 | 2023-10-18 22:00 | 95.7608 | 65.03 | 10 | 0 | 0 | 0 | 1607.9081
6983 | 2023-10-18 23:00 | 86.2255 | 53.53 | 20 | 10 | 0 | 9.5 | 2795.1091
6984 | 2023-10-19 00:00 | 86.937 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1478.6002
6985 | 2023-10-19 01:00 | 97.1155 | 53.53 | 0 | 0 | 10 | 0 | 0
6986 | 2023-10-19 02:00 | 66.805 | 53.53 | 20 | 10 | 0 | 9.5 | 2406.7006
6987 | 2023-10-19 03:00 | 80.1153 | 53.53 | 0.5 | 0 | 9.5 | 0 | 66.8226
6988 | 2023-10-19 04:00 | 69.3893 | 53.53 | 20 | 10 | 0 | 9.5 | 2458.3862
6989 | 2023-10-19 05:00 | 66.2721 | 53.53 | 20 | 10 | 0 | 19 | 2396.0429
6990 | 2023-10-19 06:00 | 70.2372 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1367.9537
6991 | 2023-10-19 07:00 | 96.5556 | 53.53 | 10 | 0 | 0 | 20 | 1500.8556
6992 | 2023-10-19 08:00 | 101.9023 | 65.03 | 10 | 0 | 0 | 20 | 1669.3235
6993 | 2023-10-19 09:00 | 104.1562 | 65.03 | 10 | 0 | 0 | 20 | 1691.862
6994 | 2023-10-19 10:00 | 109.7052 | 65.03 | 1 | 0 | 9 | 11 | 174.7352
6995 | 2023-10-19 11:00 | 113.4896 | 65.03 | 0 | 0 | 10 | 1 | 0
6996 | 2023-10-19 12:00 | 101.6775 | 65.03 | 10 | 0 | 0 | 1 | 1667.0749
6997 | 2023-10-19 13:00 | 97.1747 | 65.03 | 20 | 10 | 0 | 10.5 | 3244.0936
6998 | 2023-10-19 14:00 | 104.4756 | 65.03 | 10 | 0 | 0 | 10.5 | 1695.0558
6999 | 2023-10-19 15:00 | 107.6895 | 65.03 | 10 | 0 | 0 | 10.5 | 1727.1953
7000 | 2023-10-19 16:00 | 95.0279 | 65.03 | 20 | 10 | 0 | 20 | 3201.1588
7001 | 2023-10-19 17:00 | 113.0366 | 66.4 | 10 | 0 | 0 | 20 | 1794.3664
7002 | 2023-10-19 18:00 | 114.0466 | 66.4 | 0 | 0 | 10 | 10 | 0
7003 | 2023-10-19 19:00 | 117.3872 | 65.03 | 0 | 0 | 10 | 0 | 0
7004 | 2023-10-19 20:00 | 93.7952 | 65.03 | 20 | 10 | 0 | 9.5 | 3176.5048
7005 | 2023-10-19 21:00 | 104.8055 | 65.03 | 0.5 | 0 | 9.5 | 0 | 84.9177
7006 | 2023-10-19 22:00 | 89.3441 | 65.03 | 10 | 0 | 0 | 0 | 1543.7409
7007 | 2023-10-19 23:00 | 84.4623 | 53.53 | 20 | 10 | 0 | 9.5 | 2759.846
7008 | 2023-10-20 00:00 | 91.5155 | 53.53 | 10 | 0 | 0 | 9.5 | 1450.4547
7009 | 2023-10-20 01:00 | 92.615 | 53.53 | 0.5 | 0 | 9.5 | 0 | 73.0725
7010 | 2023-10-20 02:00 | -7.6095 | 53.53 | 20 | 10 | 0 | 9.5 | 918.4107
7011 | 2023-10-20 03:00 | 69.7378 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1362.4339
7012 | 2023-10-20 04:00 | -33.0057 | 53.53 | 20 | 10 | 0 | 20 | 410.4865
7013 | 2023-10-20 05:00 | 71.1159 | 53.53 | 10 | 0 | 0 | 20 | 1246.4594
7014 | 2023-10-20 06:00 | 75.0638 | 53.53 | 10 | 0 | 0 | 20 | 1285.9377
7015 | 2023-10-20 07:00 | 89.3978 | 53.53 | 10 | 0 | 0 | 20 | 1429.2784
7016 | 2023-10-20 08:00 | 117.8463 | 65.03 | 0 | 0 | 10 | 10 | 0
7017 | 2023-10-20 09:00 | 107.8416 | 65.03 | 10 | 0 | 0 | 10 | 1728.7156
7018 | 2023-10-20 10:00 | 98.5221 | 65.03 | 20 | 10 | 0 | 19.5 | 3271.0416
7019 | 2023-10-20 11:00 | 104.6173 | 65.03 | 10 | 0 | 0 | 19.5 | 1696.4729
7020 | 2023-10-20 12:00 | 104.8459 | 65.03 | 10 | 0 | 0 | 19.5 | 1698.7594
7021 | 2023-10-20 13:00 | 114.8901 | 65.03 | 0 | 0 | 10 | 9.5 | 0
7022 | 2023-10-20 14:00 | 99.7777 | 65.03 | 20 | 10 | 0 | 19 | 3296.1533
7023 | 2023-10-20 15:00 | 110.3697 | 65.03 | 10 | 0 | 0 | 19 | 1753.9965
7024 | 2023-10-20 16:00 | 104.2142 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1870.5937
7025 | 2023-10-20 17:00 | 133.007 | 66.4 | 0 | 0 | 10 | 10 | 0
7026 | 2023-10-20 18:00 | 130.7221 | 66.4 | 0 | 0 | 10 | 0 | 0
7027 | 2023-10-20 19:00 | 120.4202 | 65.03 | 10 | 0 | 0 | 0 | 1854.5017
7028 | 2023-10-20 20:00 | 97.0066 | 65.03 | 10 | 0 | 0 | 0 | 1620.3659
7029 | 2023-10-20 21:00 | 103.0018 | 65.03 | 10 | 0 | 0 | 0 | 1680.3178
7030 | 2023-10-20 22:00 | 97.5809 | 65.03 | 10 | 0 | 0 | 0 | 1626.1091
7031 | 2023-10-20 23:00 | 110.2854 | 53.53 | 10 | 0 | 0 | 0 | 1638.1535
7032 | 2023-10-21 00:00 | 86.4938 | 53.53 | 10 | 0 | 0 | 0 | 1400.2381
7033 | 2023-10-21 01:00 | 83.0338 | 53.53 | 10 | 0 | 0 | 0 | 1365.6381
7034 | 2023-10-21 02:00 | 62.6783 | 53.53 | 20 | 10 | 0 | 9.5 | 2324.1658
7035 | 2023-10-21 03:00 | 58.2721 | 53.53 | 20 | 10 | 0 | 19 | 2236.0428
7036 | 2023-10-21 04:00 | 70.4412 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 185.9568
7037 | 2023-10-21 05:00 | 60.4463 | 53.53 | 20 | 10 | 0 | 20 | 2279.5259
7038 | 2023-10-21 06:00 | 75.6532 | 53.53 | 10 | 0 | 0 | 20 | 1291.832
7039 | 2023-10-21 07:00 | 77.8606 | 53.53 | 10 | 0 | 0 | 20 | 1313.9064
7040 | 2023-10-21 08:00 | 96.8711 | 53.53 | 10 | 0 | 0 | 20 | 1504.0107
7041 | 2023-10-21 09:00 | 106.2004 | 53.53 | 0 | 0 | 10 | 10 | 0
7042 | 2023-10-21 10:00 | 84.006 | 53.53 | 20 | 10 | 0 | 19.5 | 2750.7206
7043 | 2023-10-21 11:00 | 116.7016 | 53.53 | 0 | 0 | 10 | 9.5 | 0
7044 | 2023-10-21 12:00 | 92.9038 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1618.4784
7045 | 2023-10-21 13:00 | 96.9792 | 53.53 | 10 | 0 | 0 | 10.5 | 1505.0924
7046 | 2023-10-21 14:00 | -23.5295 | 53.53 | 20 | 10 | 0 | 20 | 600.01
7047 | 2023-10-21 15:00 | 101.983 | 53.53 | 10 | 0 | 0 | 20 | 1555.1297
7048 | 2023-10-21 16:00 | 98.0392 | 53.53 | 10 | 0 | 0 | 20 | 1515.6918
7049 | 2023-10-21 17:00 | 119.6183 | 53.53 | 0 | 0 | 10 | 10 | 0
7050 | 2023-10-21 18:00 | 115.1108 | 53.53 | 10 | 0 | 0 | 10 | 1686.4082
7051 | 2023-10-21 19:00 | 128.298 | 53.53 | 0 | 0 | 10 | 0 | 0
7052 | 2023-10-21 20:00 | 95.1394 | 53.53 | 20 | 10 | 0 | 9.5 | 2973.3874
7053 | 2023-10-21 21:00 | 110.9705 | 53.53 | 0.5 | 0 | 9.5 | 0 | 82.2503
7054 | 2023-10-21 22:00 | 98.658 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1601.9791
7055 | 2023-10-21 23:00 | 75.4419 | 53.53 | 20 | 10 | 0 | 10 | 2579.438
7056 | 2023-10-22 00:00 | 115.6171 | 53.53 | 0 | 0 | 10 | 0 | 0
7057 | 2023-10-22 01:00 | 81.9414 | 53.53 | 10 | 0 | 0 | 0 | 1354.714
7058 | 2023-10-22 02:00 | 80.0537 | 53.53 | 10 | 0 | 0 | 0 | 1335.8373
7059 | 2023-10-22 03:00 | 66.1001 | 53.53 | 20 | 10 | 0 | 9.5 | 2392.6013
7060 | 2023-10-22 04:00 | 75.269 | 53.53 | 10 | 0 | 0 | 9.5 | 1287.9895
7061 | 2023-10-22 05:00 | 61.2331 | 53.53 | 20 | 10 | 0 | 19 | 2295.2615
7062 | 2023-10-22 06:00 | 71.0608 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1377.0562
7063 | 2023-10-22 07:00 | 84.0697 | 53.53 | 10 | 0 | 0 | 20 | 1375.997
7064 | 2023-10-22 08:00 | 111.0465 | 53.53 | 0 | 0 | 10 | 10 | 0
7065 | 2023-10-22 09:00 | 99.4146 | 53.53 | 10 | 0 | 0 | 10 | 1529.4462
7066 | 2023-10-22 10:00 | 104.0025 | 53.53 | 1 | 0 | 9 | 1 | 157.5325
7067 | 2023-10-22 11:00 | 83.9596 | 53.53 | 20 | 10 | 0 | 10.5 | 2749.7919
7068 | 2023-10-22 12:00 | 95.2647 | 53.53 | 20 | 10 | 0 | 20 | 2975.8936
7069 | 2023-10-22 13:00 | 99.1751 | 53.53 | 10 | 0 | 0 | 20 | 1527.051
7070 | 2023-10-22 14:00 | 97.633 | 53.53 | 10 | 0 | 0 | 20 | 1511.6295
7071 | 2023-10-22 15:00 | 104.2538 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 78.8919
7072 | 2023-10-22 16:00 | 93.2993 | 53.53 | 20 | 10 | 0 | 20 | 2936.5857
7073 | 2023-10-22 17:00 | 111.2669 | 53.53 | 0 | 0 | 10 | 10 | 0
7074 | 2023-10-22 18:00 | 121.5303 | 53.53 | 0 | 0 | 10 | 0 | 0
7075 | 2023-10-22 19:00 | 98.5181 | 53.53 | 10 | 0 | 0 | 0 | 1520.4813
7076 | 2023-10-22 20:00 | 95.7333 | 53.53 | 10 | 0 | 0 | 0 | 1492.6327
7077 | 2023-10-22 21:00 | 88.5155 | 53.53 | 20 | 10 | 0 | 9.5 | 2840.91
7078 | 2023-10-22 22:00 | 84.9124 | 53.53 | 20 | 10 | 0 | 19 | 2768.848
7079 | 2023-10-22 23:00 | 88.5542 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1570.4044
7080 | 2023-10-23 00:00 | 105.0279 | 53.53 | 0 | 0 | 10 | 10 | 0
7081 | 2023-10-23 01:00 | 103.0434 | 53.53 | 0 | 0 | 10 | 0 | 0
7082 | 2023-10-23 02:00 | 72.9052 | 53.53 | 20 | 10 | 0 | 9.5 | 2528.7044
7083 | 2023-10-23 03:00 | 81.4099 | 53.53 | 1.5 | 0 | 8.5 | 1 | 202.4099
7084 | 2023-10-23 04:00 | 81.3352 | 53.53 | 10 | 0 | 0 | 1 | 1348.6519
7085 | 2023-10-23 05:00 | 73.2515 | 53.53 | 20 | 10 | 0 | 10.5 | 2535.6307
7086 | 2023-10-23 06:00 | 69.205 | 53.53 | 20 | 10 | 0 | 20 | 2454.7004
7087 | 2023-10-23 07:00 | 89.5605 | 53.53 | 10 | 0 | 0 | 20 | 1430.905
7088 | 2023-10-23 08:00 | 111.0425 | 65.03 | 0 | 0 | 10 | 10 | 0
7089 | 2023-10-23 09:00 | 103.5842 | 65.03 | 10 | 0 | 0 | 10 | 1686.1419
7090 | 2023-10-23 10:00 | 97.1639 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1707.3046
7091 | 2023-10-23 11:00 | 93.979 | 65.03 | 20 | 10 | 0 | 20 | 3180.1805
7092 | 2023-10-23 12:00 | 110.9845 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 88.0072
7093 | 2023-10-23 13:00 | 100.1161 | 65.03 | 20 | 10 | 0 | 20 | 3302.9229
7094 | 2023-10-23 14:00 | 106.5032 | 65.03 | 10 | 0 | 0 | 20 | 1715.3317
7095 | 2023-10-23 15:00 | 115.1609 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 90.0955
7096 | 2023-10-23 16:00 | 95.7795 | 65.03 | 20 | 10 | 0 | 20 | 3216.1894
7097 | 2023-10-23 17:00 | 118.5621 | 66.4 | 0 | 0 | 10 | 10 | 0
7098 | 2023-10-23 18:00 | 117.6503 | 66.4 | 10 | 0 | 0 | 10 | 1840.5033
7099 | 2023-10-23 19:00 | 121.9149 | 65.03 | 0 | 0 | 10 | 0 | 0
7100 | 2023-10-23 20:00 | 110.155 | 65.03 | 10 | 0 | 0 | 0 | 1751.8499
7101 | 2023-10-23 21:00 | 90.6758 | 65.03 | 20 | 10 | 0 | 9.5 | 3114.1166
7102 | 2023-10-23 22:00 | 103.5588 | 65.03 | 0.5 | 0 | 9.5 | 0 | 84.2944
7103 | 2023-10-23 23:00 | 102.9654 | 53.53 | 10 | 0 | 0 | 0 | 1564.9543
7104 | 2023-10-24 00:00 | 92.5388 | 53.53 | 10 | 0 | 0 | 0 | 1460.6884
7105 | 2023-10-24 01:00 | 92.8884 | 53.53 | 10 | 0 | 0 | 0 | 1464.1842
7106 | 2023-10-24 02:00 | 77.2422 | 53.53 | 10 | 0 | 0 | 0 | 1307.7217
7107 | 2023-10-24 03:00 | 76.6229 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1438.5324
7108 | 2023-10-24 04:00 | 78.6707 | 53.53 | 10 | 0 | 0 | 1 | 1322.007
7109 | 2023-10-24 05:00 | -73.3335 | 53.53 | 20 | 10 | 0 | 10.5 | -396.0699
7110 | 2023-10-24 06:00 | -68.2374 | 53.53 | 20 | 10 | 0 | 20 | -294.1476
7111 | 2023-10-24 07:00 | 102.5464 | 53.53 | 10 | 0 | 0 | 20 | 1560.7638
7112 | 2023-10-24 08:00 | 114.3762 | 65.03 | 0 | 0 | 10 | 10 | 0
7113 | 2023-10-24 09:00 | 105.3336 | 65.03 | 1.5 | 0 | 8.5 | 1.5 | 255.5454
7114 | 2023-10-24 10:00 | 94.867 | 65.03 | 20 | 10 | 0 | 11 | 3197.9397
7115 | 2023-10-24 11:00 | 103.0524 | 65.03 | 10 | 0 | 0 | 11 | 1680.8236
7116 | 2023-10-24 12:00 | 105.3997 | 65.03 | 0 | 0 | 10 | 1 | 0
7117 | 2023-10-24 13:00 | -47.2161 | 65.03 | 20 | 10 | 0 | 10.5 | 356.2779
7118 | 2023-10-24 14:00 | 101.3381 | 65.03 | 10 | 0 | 0 | 10.5 | 1663.6807
7119 | 2023-10-24 15:00 | 95.2784 | 65.03 | 20 | 10 | 0 | 20 | 3206.1674
7120 | 2023-10-24 16:00 | 108.8943 | 65.03 | 10 | 0 | 0 | 20 | 1739.2429
7121 | 2023-10-24 17:00 | 120.1745 | 66.4 | 0 | 0 | 10 | 10 | 0
7122 | 2023-10-24 18:00 | 109.1569 | 66.4 | 10 | 0 | 0 | 10 | 1755.5687
7123 | 2023-10-24 19:00 | 121.6783 | 65.03 | 0 | 0 | 10 | 0 | 0
7124 | 2023-10-24 20:00 | 98.4781 | 65.03 | 10 | 0 | 0 | 0 | 1635.0806
7125 | 2023-10-24 21:00 | 103.0875 | 65.03 | 10 | 0 | 0 | 0 | 1681.1754
7126 | 2023-10-24 22:00 | 96.1277 | 65.03 | 10 | 0 | 0 | 0 | 1611.5771
7127 | 2023-10-24 23:00 | 88.5553 | 53.53 | 10 | 0 | 0 | 0 | 1420.8528
7128 | 2023-10-25 00:00 | 88.7368 | 53.53 | 10 | 0 | 0 | 0 | 1422.6677
7129 | 2023-10-25 01:00 | 90.171 | 53.53 | 10 | 0 | 0 | 0 | 1437.0101
7130 | 2023-10-25 02:00 | 74.0399 | 53.53 | 10 | 0 | 0 | 0 | 1275.6989
7131 | 2023-10-25 03:00 | 75.033 | 53.53 | 10 | 0 | 0 | 0 | 1285.6299
7132 | 2023-10-25 04:00 | 72.5081 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1393.0522
7133 | 2023-10-25 05:00 | 70.9167 | 53.53 | 20 | 10 | 0 | 10.5 | 2488.9348
7134 | 2023-10-25 06:00 | 71.3969 | 53.53 | 20 | 10 | 0 | 20 | 2498.5389
7135 | 2023-10-25 07:00 | 121.9461 | 53.53 | 0 | 0 | 10 | 10 | 0
7136 | 2023-10-25 08:00 | 98.7375 | 65.03 | 20 | 10 | 0 | 19.5 | 3275.3495
7137 | 2023-10-25 09:00 | 100.045 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1737.6317
7138 | 2023-10-25 10:00 | 146.0552 | 65.03 | 0 | 0 | 10 | 10 | 0
7139 | 2023-10-25 11:00 | 107.264 | 65.03 | 10 | 0 | 0 | 10 | 1722.9398
7140 | 2023-10-25 12:00 | 95.4234 | 65.03 | 20 | 10 | 0 | 19.5 | 3209.0685
7141 | 2023-10-25 13:00 | 111.0891 | 65.03 | 1 | 0 | 9 | 10.5 | 176.1191
7142 | 2023-10-25 14:00 | 97.9254 | 65.03 | 20 | 10 | 0 | 20 | 3259.1081
7143 | 2023-10-25 15:00 | 111.7366 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 88.3833
7144 | 2023-10-25 16:00 | 102.3651 | 65.03 | 20 | 10 | 0 | 20 | 3347.9023
7145 | 2023-10-25 17:00 | 115.8082 | 66.4 | 10 | 0 | 0 | 20 | 1822.0817
7146 | 2023-10-25 18:00 | 134.4114 | 66.4 | 0 | 0 | 10 | 10 | 0
7147 | 2023-10-25 19:00 | 123.5286 | 65.03 | 0 | 0 | 10 | 0 | 0
7148 | 2023-10-25 20:00 | 107.3724 | 65.03 | 10 | 0 | 0 | 0 | 1724.0243
7149 | 2023-10-25 21:00 | 102.3826 | 65.03 | 10 | 0 | 0 | 0 | 1674.1257
7150 | 2023-10-25 22:00 | 95.7776 | 65.03 | 10 | 0 | 0 | 0 | 1608.0764
7151 | 2023-10-25 23:00 | 98.9309 | 53.53 | 10 | 0 | 0 | 0 | 1524.6087
7152 | 2023-10-26 00:00 | 104.8307 | 53.53 | 10 | 0 | 0 | 0 | 1583.6074
7153 | 2023-10-26 01:00 | 94.9295 | 53.53 | 10 | 0 | 0 | 0 | 1484.5954
7154 | 2023-10-26 02:00 | 91.8196 | 53.53 | 10 | 0 | 0 | 0 | 1453.4962
7155 | 2023-10-26 03:00 | 81.1646 | 53.53 | 10 | 0 | 0 | 0 | 1346.9456
7156 | 2023-10-26 04:00 | 75.5398 | 53.53 | 20 | 10 | 0 | 9.5 | 2581.3964
7157 | 2023-10-26 05:00 | 75.8574 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1430.0716
7158 | 2023-10-26 06:00 | 74.9491 | 53.53 | 20 | 10 | 0 | 20 | 2569.5813
7159 | 2023-10-26 07:00 | 86.0742 | 53.53 | 10 | 0 | 0 | 20 | 1396.0415
7160 | 2023-10-26 08:00 | 103.2318 | 65.03 | 10 | 0 | 0 | 20 | 1682.6181
7161 | 2023-10-26 09:00 | 105.6135 | 65.03 | 10 | 0 | 0 | 20 | 1706.4348
7162 | 2023-10-26 10:00 | 100.9646 | 65.03 | 10 | 0 | 0 | 20 | 1659.9458
7163 | 2023-10-26 11:00 | 106.5636 | 65.03 | 10 | 0 | 0 | 20 | 1715.9361
7164 | 2023-10-26 12:00 | 104.0586 | 65.03 | 10 | 0 | 0 | 20 | 1690.8862
7165 | 2023-10-26 13:00 | 110.4297 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.7298
7166 | 2023-10-26 14:00 | 109.4008 | 65.03 | 10 | 0 | 0 | 10.5 | 1744.3083
7167 | 2023-10-26 15:00 | 105.1839 | 65.03 | 10 | 0 | 0 | 10.5 | 1702.1392
7168 | 2023-10-26 16:00 | 95.4868 | 65.03 | 20 | 10 | 0 | 20 | 3210.3369
7169 | 2023-10-26 17:00 | 136.6792 | 66.4 | 0 | 0 | 10 | 10 | 0
7170 | 2023-10-26 18:00 | 117.8565 | 66.4 | 0 | 0 | 10 | 0 | 0
7171 | 2023-10-26 19:00 | 118.299 | 65.03 | 10 | 0 | 0 | 0 | 1833.2896
7172 | 2023-10-26 20:00 | 96.457 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1699.8629
7173 | 2023-10-26 21:00 | 95.4909 | 65.03 | 20 | 10 | 0 | 10 | 3210.4188
7174 | 2023-10-26 22:00 | 113.6278 | 65.03 | 0 | 0 | 10 | 0 | 0
7175 | 2023-10-26 23:00 | 106.7884 | 53.53 | 10 | 0 | 0 | 0 | 1603.1838
7176 | 2023-10-27 00:00 | 97.4636 | 53.53 | 10 | 0 | 0 | 0 | 1509.9364
7177 | 2023-10-27 01:00 | 93.1049 | 53.53 | 10 | 0 | 0 | 0 | 1466.3492
7178 | 2023-10-27 02:00 | 79.0009 | 53.53 | 10 | 0 | 0 | 0 | 1325.309
7179 | 2023-10-27 03:00 | 74.458 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1414.6037
7180 | 2023-10-27 04:00 | 72.5116 | 53.53 | 20 | 10 | 0 | 10.5 | 2520.8316
7181 | 2023-10-27 05:00 | 76.5672 | 53.53 | 10 | 0 | 0 | 10.5 | 1300.9717
7182 | 2023-10-27 06:00 | 70.7992 | 53.53 | 20 | 10 | 0 | 20 | 2486.5845
7183 | 2023-10-27 07:00 | 95.8637 | 53.53 | 10 | 0 | 0 | 20 | 1493.9372
7184 | 2023-10-27 08:00 | 105.4779 | 65.03 | 10 | 0 | 0 | 20 | 1705.0786
7185 | 2023-10-27 09:00 | 108.8551 | 65.03 | 0 | 0 | 10 | 10 | 0
7186 | 2023-10-27 10:00 | 99.6605 | 65.03 | 11.0526 | 1.0526 | 0 | 11 | 1820.2637
7187 | 2023-10-27 11:00 | 109.8342 | 65.03 | 0 | 0 | 10 | 1 | 0
7188 | 2023-10-27 12:00 | 97.9467 | 65.03 | 20 | 10 | 0 | 10.5 | 3259.5338
7189 | 2023-10-27 13:00 | 99.9526 | 65.03 | 10 | 0 | 0 | 10.5 | 1649.8263
7190 | 2023-10-27 14:00 | 100.2301 | 65.03 | 10 | 0 | 0 | 10.5 | 1652.6009
7191 | 2023-10-27 15:00 | 97.0227 | 65.03 | 20 | 10 | 0 | 20 | 3241.0546
7192 | 2023-10-27 16:00 | 112.8037 | 65.03 | 10 | 0 | 0 | 20 | 1778.3371
7193 | 2023-10-27 17:00 | 112.5915 | 66.4 | 10 | 0 | 0 | 20 | 1789.9151
7194 | 2023-10-27 18:00 | 114.1695 | 66.4 | 0 | 0 | 10 | 10 | 0
7195 | 2023-10-27 19:00 | 130.3322 | 65.03 | 0 | 0 | 10 | 0 | 0
7196 | 2023-10-27 20:00 | 94.9652 | 65.03 | 10 | 0 | 0 | 0 | 1599.9516
7197 | 2023-10-27 21:00 | 97.5263 | 65.03 | 10 | 0 | 0 | 0 | 1625.5632
7198 | 2023-10-27 22:00 | 92.352 | 65.03 | 10 | 0 | 0 | 0 | 1573.8205
7199 | 2023-10-27 23:00 | 100.9953 | 53.53 | 10 | 0 | 0 | 0 | 1545.2526
7200 | 2023-10-28 00:00 | 93.1283 | 53.53 | 10 | 0 | 0 | 0 | 1466.5827
7201 | 2023-10-28 01:00 | 92.1027 | 53.53 | 10 | 0 | 0 | 0 | 1456.3272
7202 | 2023-10-28 02:00 | 70.273 | 53.53 | 10 | 0 | 0 | 0 | 1238.0304
7203 | 2023-10-28 03:00 | 66.4564 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1326.1651
7204 | 2023-10-28 04:00 | 62.2592 | 53.53 | 20 | 10 | 0 | 10.5 | 2315.7844
7205 | 2023-10-28 05:00 | 60.4759 | 53.53 | 20 | 10 | 0 | 20 | 2280.1177
7206 | 2023-10-28 06:00 | 77.7112 | 53.53 | 10 | 0 | 0 | 20 | 1312.4117
7207 | 2023-10-28 07:00 | 92.3457 | 53.53 | 10 | 0 | 0 | 20 | 1458.7573
7208 | 2023-10-28 08:00 | 91.2037 | 53.53 | 10 | 0 | 0 | 20 | 1447.3366
7209 | 2023-10-28 09:00 | 96.1988 | 53.53 | 1 | 0 | 9 | 11 | 149.7288
7210 | 2023-10-28 10:00 | 93.7458 | 53.53 | 10 | 0 | 0 | 11 | 1472.758
7211 | 2023-10-28 11:00 | 88.7199 | 53.53 | 10 | 0 | 0 | 11 | 1422.4993
7212 | 2023-10-28 12:00 | 97.2668 | 53.53 | 0 | 0 | 10 | 1 | 0
7213 | 2023-10-28 13:00 | 92.9685 | 53.53 | 10 | 0 | 0 | 1 | 1464.985
7214 | 2023-10-28 14:00 | 89.6844 | 53.53 | 10 | 0 | 0 | 1 | 1432.1436
7215 | 2023-10-28 15:00 | 86.9391 | 53.53 | 20 | 10 | 0 | 10.5 | 2809.3823
7216 | 2023-10-28 16:00 | 86.5368 | 53.53 | 20 | 10 | 0 | 20 | 2801.3358
7217 | 2023-10-28 17:00 | 108.2622 | 53.53 | 0 | 0 | 10 | 10 | 0
7218 | 2023-10-28 18:00 | 110.2682 | 53.53 | 0 | 0 | 10 | 0 | 0
7219 | 2023-10-28 19:00 | 105.1247 | 53.53 | 10 | 0 | 0 | 0 | 1586.5473
7220 | 2023-10-28 20:00 | 96.2878 | 53.53 | 10 | 0 | 0 | 0 | 1498.1782
7221 | 2023-10-28 21:00 | 90.4115 | 53.53 | 10 | 0 | 0 | 0 | 1439.4151
7222 | 2023-10-28 22:00 | 95.6219 | 53.53 | 10 | 0 | 0 | 0 | 1491.5191
7223 | 2023-10-28 23:00 | 84.5634 | 53.53 | 10 | 0 | 0 | 0 | 1380.9343
7224 | 2023-10-29 00:00 | 80.6402 | 53.53 | 10 | 0 | 0 | 0 | 1341.7015
7225 | 2023-10-29 01:00 | 86.769 | 53.53 | 10 | 0 | 0 | 0 | 1402.9901
7226 | 2023-10-29 02:00 | 58.0153 | 53.53 | 20 | 10 | 0 | 9.5 | 2230.9066
7227 | 2023-10-29 03:00 | 70.2899 | 53.53 | 10 | 0 | 0 | 9.5 | 1238.1986
7228 | 2023-10-29 04:00 | 59.7713 | 53.53 | 20 | 10 | 0 | 19 | 2266.0256
7229 | 2023-10-29 05:00 | 73.827 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 191.0356
7230 | 2023-10-29 06:00 | 63.4845 | 53.53 | 20 | 10 | 0 | 20 | 2340.2901
7231 | 2023-10-29 07:00 | 95.2838 | 53.53 | 10 | 0 | 0 | 20 | 1488.1384
7232 | 2023-10-29 08:00 | 88.7498 | 53.53 | 10 | 0 | 0 | 20 | 1422.7983
7233 | 2023-10-29 09:00 | 91.2985 | 53.53 | 10 | 0 | 0 | 20 | 1448.2851
7234 | 2023-10-29 10:00 | 98.925 | 53.53 | 10 | 0 | 0 | 20 | 1524.5497
7235 | 2023-10-29 11:00 | 106.4158 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 79.9729
7236 | 2023-10-29 12:00 | 112.1156 | 53.53 | 0 | 0 | 10 | 0.5 | 0
7237 | 2023-10-29 13:00 | 96.2105 | 53.53 | 20 | 10 | 0 | 10 | 2994.8097
7238 | 2023-10-29 14:00 | 114.287 | 53.53 | 0 | 0 | 10 | 0 | 0
7239 | 2023-10-29 15:00 | -5.7121 | 53.53 | 20 | 10 | 0 | 9.5 | 956.3585
7240 | 2023-10-29 16:00 | -18.7655 | 53.53 | 20 | 10 | 0 | 19 | 695.2893
7241 | 2023-10-29 17:00 | 104.7428 | 53.53 | 1 | 0 | 9 | 10 | 158.2728
7242 | 2023-10-29 18:00 | 114.2571 | 53.53 | 0 | 0 | 10 | 0 | 0
7243 | 2023-10-29 19:00 | -62.7961 | 53.53 | 20 | 10 | 0 | 9.5 | -185.3228
7244 | 2023-10-29 20:00 | -31.9487 | 53.53 | 20 | 10 | 0 | 19 | 431.6268
7245 | 2023-10-29 21:00 | 94.6552 | 53.53 | 0 | 0 | 10 | 9 | 0
7246 | 2023-10-29 22:00 | 82.7617 | 53.53 | 20 | 10 | 0 | 18.5 | 2725.8336
7247 | 2023-10-29 23:00 | 89.3145 | 53.53 | 10 | 0 | 0 | 18.5 | 1428.4454
7248 | 2023-10-30 00:00 | 101.7109 | 53.53 | 0 | 0 | 10 | 8.5 | 0
7249 | 2023-10-30 01:00 | 90.4075 | 53.53 | 1.5 | 0 | 8.5 | 0 | 215.9062
7250 | 2023-10-30 02:00 | 67.5921 | 53.53 | 20 | 10 | 0 | 9.5 | 2422.4414
7251 | 2023-10-30 03:00 | 70.5833 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1371.7784
7252 | 2023-10-30 04:00 | 67.6097 | 53.53 | 20 | 10 | 0 | 20 | 2422.7938
7253 | 2023-10-30 05:00 | 73.1506 | 53.53 | 10 | 0 | 0 | 20 | 1266.8061
7254 | 2023-10-30 06:00 | 74.6758 | 53.53 | 10 | 0 | 0 | 20 | 1282.0583
7255 | 2023-10-30 07:00 | 91.7054 | 53.53 | 10 | 0 | 0 | 20 | 1452.3543
7256 | 2023-10-30 08:00 | 120.2116 | 65.03 | 0 | 0 | 10 | 10 | 0
7257 | 2023-10-30 09:00 | 99.0453 | 65.03 | 20 | 10 | 0 | 19.5 | 3281.5058
7258 | 2023-10-30 10:00 | 116.8497 | 65.03 | 0 | 0 | 10 | 9.5 | 0
7259 | 2023-10-30 11:00 | 97.191 | 65.03 | 20 | 10 | 0 | 19 | 3244.4208
7260 | 2023-10-30 12:00 | 104.4501 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1873.2015
7261 | 2023-10-30 13:00 | 114.5504 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 89.7902
7262 | 2023-10-30 14:00 | 114.0012 | 65.03 | 10 | 0 | 0 | 10.5 | 1790.3118
7263 | 2023-10-30 15:00 | 100.937 | 65.03 | 20 | 10 | 0 | 20 | 3319.3394
7264 | 2023-10-30 16:00 | 108.428 | 65.03 | 10 | 0 | 0 | 20 | 1734.5801
7265 | 2023-10-30 17:00 | 122.2654 | 66.4 | 0 | 0 | 10 | 10 | 0
7266 | 2023-10-30 18:00 | 115.1597 | 66.4 | 10 | 0 | 0 | 10 | 1815.5972
7267 | 2023-10-30 19:00 | 123.9723 | 65.03 | 0 | 0 | 10 | 0 | 0
7268 | 2023-10-30 20:00 | 117.6103 | 65.03 | 10 | 0 | 0 | 0 | 1826.4034
7269 | 2023-10-30 21:00 | 102.6986 | 65.03 | 10 | 0 | 0 | 0 | 1677.2861
7270 | 2023-10-30 22:00 | 103.5282 | 65.03 | 10 | 0 | 0 | 0 | 1685.5817
7271 | 2023-10-30 23:00 | 99.4837 | 53.53 | 10 | 0 | 0 | 0 | 1530.1369
7272 | 2023-10-31 00:00 | 85.0267 | 53.53 | 10 | 0 | 0 | 0 | 1385.5672
7273 | 2023-10-31 01:00 | -29.7146 | 53.53 | 20 | 10 | 0 | 9.5 | 476.3075
7274 | 2023-10-31 02:00 | 67.3259 | 53.53 | 20 | 10 | 0 | 19 | 2417.1175
7275 | 2023-10-31 03:00 | 69.8435 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1363.602
7276 | 2023-10-31 04:00 | 96.719 | 53.53 | 0 | 0 | 10 | 10 | 0
7277 | 2023-10-31 05:00 | 72.0692 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1322.0969
7278 | 2023-10-31 06:00 | 68.9201 | 53.53 | 20 | 10 | 0 | 20 | 2449.0029
7279 | 2023-10-31 07:00 | 104.2254 | 53.53 | 10 | 0 | 0 | 20 | 1577.5541
7280 | 2023-10-31 08:00 | 97.7118 | 65.03 | 10 | 0 | 0 | 20 | 1627.4177
7281 | 2023-10-31 09:00 | 100.7581 | 65.03 | 10 | 0 | 0 | 20 | 1657.8812
7282 | 2023-10-31 10:00 | 115.2627 | 65.03 | 0 | 0 | 10 | 10 | 0
7283 | 2023-10-31 11:00 | 104.2211 | 65.03 | 10 | 0 | 0 | 10 | 1692.5113
7284 | 2023-10-31 12:00 | 94.5471 | 65.03 | 20 | 10 | 0 | 19.5 | 3191.5429
7285 | 2023-10-31 13:00 | 108.33 | 65.03 | 10 | 0 | 0 | 19.5 | 1733.6002
7286 | 2023-10-31 14:00 | 101.0948 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1748.6825
7287 | 2023-10-31 15:00 | 118.5777 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 91.8038
7288 | 2023-10-31 16:00 | 99.7413 | 65.03 | 20 | 10 | 0 | 20 | 3295.4268
7289 | 2023-10-31 17:00 | 128.1674 | 66.4 | 0 | 0 | 10 | 10 | 0
7290 | 2023-10-31 18:00 | 136.4868 | 66.4 | 0 | 0 | 10 | 0 | 0
7291 | 2023-10-31 19:00 | 113.2657 | 65.03 | 10 | 0 | 0 | 0 | 1782.9574
7292 | 2023-10-31 20:00 | 97.4904 | 65.03 | 10 | 0 | 0 | 0 | 1625.2041
7293 | 2023-10-31 21:00 | 101.9897 | 65.03 | 10 | 0 | 0 | 0 | 1670.197
7294 | 2023-10-31 22:00 | 93.2286 | 65.03 | 10 | 0 | 0 | 0 | 1582.5857
7295 | 2023-10-31 23:00 | 96.01 | 53.53 | 10 | 0 | 0 | 0 | 1495.3998
7296 | 2023-11-01 00:00 | 97.2671 | 53.53 | 10 | 0 | 0 | 0 | 1507.9706
7297 | 2023-11-01 01:00 | 97.1262 | 53.53 | 10 | 0 | 0 | 0 | 1506.5624
7298 | 2023-11-01 02:00 | 79.2681 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1467.7679
7299 | 2023-11-01 03:00 | 79.4385 | 53.53 | 10 | 0 | 0 | 1 | 1329.6855
7300 | 2023-11-01 04:00 | 80.1581 | 53.53 | 10 | 0 | 0 | 1 | 1336.8813
7301 | 2023-11-01 05:00 | 74.7874 | 53.53 | 20 | 10 | 0 | 10.5 | 2566.3483
7302 | 2023-11-01 06:00 | 75.0628 | 53.53 | 20 | 10 | 0 | 20 | 2571.8557
7303 | 2023-11-01 07:00 | 98.0245 | 53.53 | 10 | 0 | 0 | 20 | 1515.5453
7304 | 2023-11-01 08:00 | 108.5649 | 65.03 | 10 | 0 | 0 | 20 | 1735.9487
7305 | 2023-11-01 09:00 | 105.8144 | 65.03 | 10 | 0 | 0 | 20 | 1708.4439
7306 | 2023-11-01 10:00 | 111.4498 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 88.2399
7307 | 2023-11-01 11:00 | 98.4026 | 65.03 | 20 | 10 | 0 | 20 | 3268.6527
7308 | 2023-11-01 12:00 | 103.9785 | 65.03 | 10 | 0 | 0 | 20 | 1690.0854
7309 | 2023-11-01 13:00 | 106.8846 | 65.03 | 10 | 0 | 0 | 20 | 1719.1459
7310 | 2023-11-01 14:00 | 103.2357 | 65.03 | 10 | 0 | 0 | 20 | 1682.6571
7311 | 2023-11-01 15:00 | 124.6556 | 65.03 | 0 | 0 | 10 | 10 | 0
7312 | 2023-11-01 16:00 | 109.0402 | 65.03 | 20 | 10 | 0 | 19.5 | 3481.4034
7313 | 2023-11-01 17:00 | 125.2599 | 66.4 | 0 | 0 | 10 | 9.5 | 0
7314 | 2023-11-01 18:00 | 120.5245 | 66.4 | 10 | 0 | 0 | 9.5 | 1869.2453
7315 | 2023-11-01 19:00 | 123.7802 | 65.03 | 0.5 | 0 | 9.5 | 0 | 94.4051
7316 | 2023-11-01 20:00 | 96.2606 | 65.03 | 10 | 0 | 0 | 0 | 1612.9058
7317 | 2023-11-01 21:00 | 102.6566 | 65.03 | 10 | 0 | 0 | 0 | 1676.8658
7318 | 2023-11-01 22:00 | 97.7721 | 65.03 | 10 | 0 | 0 | 0 | 1628.0208
7319 | 2023-11-01 23:00 | 96.902 | 53.53 | 10 | 0 | 0 | 0 | 1504.32
7320 | 2023-11-02 00:00 | 85.4971 | 53.53 | 20 | 10 | 0 | 9.5 | 2780.5419
7321 | 2023-11-02 01:00 | 91.721 | 53.53 | 10 | 0 | 0 | 9.5 | 1452.5104
7322 | 2023-11-02 02:00 | 92.6841 | 53.53 | 10 | 0 | 0 | 9.5 | 1462.1409
7323 | 2023-11-02 03:00 | 85.9707 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1541.8497
7324 | 2023-11-02 04:00 | 91.0343 | 53.53 | 10 | 0 | 0 | 10.5 | 1445.6433
7325 | 2023-11-02 05:00 | 91.8074 | 53.53 | 10 | 0 | 0 | 10.5 | 1453.3744
7326 | 2023-11-02 06:00 | 84.4913 | 53.53 | 20 | 10 | 0 | 20 | 2760.4266
7327 | 2023-11-02 07:00 | 95.7224 | 53.53 | 10 | 0 | 0 | 20 | 1492.5241
7328 | 2023-11-02 08:00 | 102.2129 | 65.03 | 10 | 0 | 0 | 20 | 1672.4294
7329 | 2023-11-02 09:00 | 119.1636 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 92.0968
7330 | 2023-11-02 10:00 | 109.3873 | 65.03 | 20 | 10 | 0 | 20 | 3488.3457
7331 | 2023-11-02 11:00 | 136.7285 | 65.03 | 0 | 0 | 10 | 10 | 0
7332 | 2023-11-02 12:00 | 106.3047 | 65.03 | 20 | 10 | 0 | 19.5 | 3426.694
7333 | 2023-11-02 13:00 | 129.0824 | 65.03 | 0 | 0 | 10 | 9.5 | 0
7334 | 2023-11-02 14:00 | 107.7496 | 65.03 | 20 | 10 | 0 | 19 | 3455.5919
7335 | 2023-11-02 15:00 | 121.2243 | 65.03 | 10 | 0 | 0 | 19 | 1862.5432
7336 | 2023-11-02 16:00 | 125.4893 | 65.03 | 0 | 0 | 10 | 9 | 0
7337 | 2023-11-02 17:00 | 117.2917 | 66.4 | 10 | 0 | 0 | 9 | 1836.9169
7338 | 2023-11-02 18:00 | 120.5131 | 66.4 | 1 | 0 | 9 | 0 | 186.9131
7339 | 2023-11-02 19:00 | 117.2364 | 65.03 | 10 | 0 | 0 | 0 | 1822.6643
7340 | 2023-11-02 20:00 | 96.1842 | 65.03 | 20 | 10 | 0 | 9.5 | 3224.2846
7341 | 2023-11-02 21:00 | 109.437 | 65.03 | 0.5 | 0 | 9.5 | 0 | 87.2335
7342 | 2023-11-02 22:00 | 102.4662 | 65.03 | 10 | 0 | 0 | 0 | 1674.9625
7343 | 2023-11-02 23:00 | 99.2942 | 53.53 | 10 | 0 | 0 | 0 | 1528.2415
7344 | 2023-11-03 00:00 | 103.4384 | 53.53 | 10 | 0 | 0 | 0 | 1569.6837
7345 | 2023-11-03 01:00 | 88.2183 | 53.53 | 10 | 0 | 0 | 0 | 1417.4834
7346 | 2023-11-03 02:00 | 90.6765 | 53.53 | 10 | 0 | 0 | 0 | 1442.0652
7347 | 2023-11-03 03:00 | 76.4125 | 53.53 | 20 | 10 | 0 | 9.5 | 2598.8507
7348 | 2023-11-03 04:00 | 83.2279 | 53.53 | 20 | 10 | 0 | 19 | 2735.1575
7349 | 2023-11-03 05:00 | 84.0153 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1520.2376
7350 | 2023-11-03 06:00 | 91.6155 | 53.53 | 10 | 0 | 0 | 20 | 1451.4545
7351 | 2023-11-03 07:00 | 98.1241 | 53.53 | 10 | 0 | 0 | 20 | 1516.5412
7352 | 2023-11-03 08:00 | 97.119 | 65.03 | 10 | 0 | 0 | 20 | 1621.4902
7353 | 2023-11-03 09:00 | 109.3305 | 65.03 | 10 | 0 | 0 | 20 | 1743.6046
7354 | 2023-11-03 10:00 | 110.4498 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.7399
7355 | 2023-11-03 11:00 | 102.2294 | 65.03 | 10 | 0 | 0 | 10.5 | 1672.5938
7356 | 2023-11-03 12:00 | 110.0293 | 65.03 | 10 | 0 | 0 | 10.5 | 1750.5932
7357 | 2023-11-03 13:00 | 106.3321 | 65.03 | 10 | 0 | 0 | 10.5 | 1713.6214
7358 | 2023-11-03 14:00 | 100.609 | 65.03 | 20 | 10 | 0 | 20 | 3312.7803
7359 | 2023-11-03 15:00 | 114.4775 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 89.7538
7360 | 2023-11-03 16:00 | 105.0085 | 65.03 | 20 | 10 | 0 | 20 | 3400.7709
7361 | 2023-11-03 17:00 | 121.0289 | 66.4 | 0 | 0 | 10 | 10 | 0
7362 | 2023-11-03 18:00 | 120.6589 | 66.4 | 10 | 0 | 0 | 10 | 1870.5893
7363 | 2023-11-03 19:00 | 135.115 | 65.03 | 0 | 0 | 10 | 0 | 0
7364 | 2023-11-03 20:00 | 103.5933 | 65.03 | 10 | 0 | 0 | 0 | 1686.2331
7365 | 2023-11-03 21:00 | 104.4986 | 65.03 | 10 | 0 | 0 | 0 | 1695.2865
7366 | 2023-11-03 22:00 | 100.8027 | 65.03 | 10 | 0 | 0 | 0 | 1658.3265
7367 | 2023-11-03 23:00 | 102.6224 | 53.53 | 10 | 0 | 0 | 0 | 1561.5239
7368 | 2023-11-04 00:00 | 103.3732 | 53.53 | 10 | 0 | 0 | 0 | 1569.032
7369 | 2023-11-04 01:00 | 96.2616 | 53.53 | 10 | 0 | 0 | 0 | 1497.9159
7370 | 2023-11-04 02:00 | 76.619 | 53.53 | 10 | 0 | 0 | 0 | 1301.4898
7371 | 2023-11-04 03:00 | 75.8847 | 53.53 | 10 | 0 | 0 | 0 | 1294.1473
7372 | 2023-11-04 04:00 | 62.4221 | 53.53 | 20 | 10 | 0 | 9.5 | 2319.0425
7373 | 2023-11-04 05:00 | -9.6077 | 53.53 | 20 | 10 | 0 | 19 | 878.4452
7374 | 2023-11-04 06:00 | 69.4072 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1358.7798
7375 | 2023-11-04 07:00 | 86.0063 | 53.53 | 10 | 0 | 0 | 20 | 1395.3628
7376 | 2023-11-04 08:00 | 94.0636 | 53.53 | 10 | 0 | 0 | 20 | 1475.9363
7377 | 2023-11-04 09:00 | 90.155 | 53.53 | 10 | 0 | 0 | 20 | 1436.8495
7378 | 2023-11-04 10:00 | 92.5901 | 53.53 | 10 | 0 | 0 | 20 | 1461.201
7379 | 2023-11-04 11:00 | 99.0465 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 76.2883
7380 | 2023-11-04 12:00 | -22.0097 | 53.53 | 20 | 10 | 0 | 20 | 630.4051
7381 | 2023-11-04 13:00 | 95.605 | 53.53 | 10 | 0 | 0 | 20 | 1491.3503
7382 | 2023-11-04 14:00 | 101.4973 | 53.53 | 10 | 0 | 0 | 20 | 1550.2731
7383 | 2023-11-04 15:00 | 97.8474 | 53.53 | 10 | 0 | 0 | 20 | 1513.774
7384 | 2023-11-04 16:00 | 110.5743 | 53.53 | 10 | 0 | 0 | 20 | 1641.0431
7385 | 2023-11-04 17:00 | 114.715 | 53.53 | 10 | 0 | 0 | 20 | 1682.4503
7386 | 2023-11-04 18:00 | 121.7063 | 53.53 | 0 | 0 | 10 | 10 | 0
7387 | 2023-11-04 19:00 | 117.4698 | 53.53 | 0 | 0 | 10 | 0 | 0
7388 | 2023-11-04 20:00 | 87.3143 | 53.53 | 20 | 10 | 0 | 9.5 | 2816.8855
7389 | 2023-11-04 21:00 | 95.2275 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.3788
7390 | 2023-11-04 22:00 | 88.1548 | 53.53 | 10 | 0 | 0 | 0 | 1416.848
7391 | 2023-11-04 23:00 | 90.1004 | 53.53 | 10 | 0 | 0 | 0 | 1436.3041
7392 | 2023-11-05 00:00 | 85.8904 | 53.53 | 20 | 10 | 0 | 9.5 | 2788.4079
7393 | 2023-11-05 01:00 | 93.9336 | 53.53 | 0.5 | 0 | 9.5 | 0 | 73.7318
7394 | 2023-11-05 02:00 | 62.611 | 53.53 | 20 | 10 | 0 | 9.5 | 2322.8203
7395 | 2023-11-05 03:00 | -34.3355 | 53.53 | 20 | 10 | 0 | 19 | 383.8902
7396 | 2023-11-05 04:00 | 75.5821 | 53.53 | 10 | 0 | 0 | 19 | 1291.1208
7397 | 2023-11-05 05:00 | 78.7221 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 198.3782
7398 | 2023-11-05 06:00 | 65.7765 | 53.53 | 20 | 10 | 0 | 20 | 2386.1309
7399 | 2023-11-05 07:00 | 91.0318 | 53.53 | 10 | 0 | 0 | 20 | 1445.6179
7400 | 2023-11-05 08:00 | 102.3183 | 53.53 | 1.5 | 0 | 8.5 | 11.5 | 233.7724
7401 | 2023-11-05 09:00 | 115.6644 | 53.53 | 0 | 0 | 10 | 1.5 | 0
7402 | 2023-11-05 10:00 | 91.9285 | 53.53 | 20 | 10 | 0 | 11 | 2909.1709
7403 | 2023-11-05 11:00 | 94.9193 | 53.53 | 10 | 0 | 0 | 11 | 1484.4933
7404 | 2023-11-05 12:00 | 133.8851 | 53.53 | 0 | 0 | 10 | 1 | 0
7405 | 2023-11-05 13:00 | 98.9317 | 53.53 | 10 | 0 | 0 | 1 | 1524.6174
7406 | 2023-11-05 14:00 | 90.0747 | 53.53 | 20 | 10 | 0 | 10.5 | 2872.0939
7407 | 2023-11-05 15:00 | 96.8897 | 53.53 | 10 | 0 | 0 | 10.5 | 1504.1966
7408 | 2023-11-05 16:00 | 86.7923 | 53.53 | 20 | 10 | 0 | 20 | 2806.4465
7409 | 2023-11-05 17:00 | 117.7721 | 53.53 | 0 | 0 | 10 | 10 | 0
7410 | 2023-11-05 18:00 | 122.773 | 53.53 | 0 | 0 | 10 | 0 | 0
7411 | 2023-11-05 19:00 | 109.9161 | 53.53 | 10 | 0 | 0 | 0 | 1634.4614
7412 | 2023-11-05 20:00 | 92.6058 | 53.53 | 20 | 10 | 0 | 9.5 | 2922.7165
7413 | 2023-11-05 21:00 | 103.8806 | 53.53 | 0.5 | 0 | 9.5 | 0 | 78.7053
7414 | 2023-11-05 22:00 | 85.6862 | 53.53 | 20 | 10 | 0 | 9.5 | 2784.3247
7415 | 2023-11-05 23:00 | 82.7155 | 53.53 | 20 | 10 | 0 | 19 | 2724.9109
7416 | 2023-11-06 00:00 | 97.2447 | 53.53 | 0 | 0 | 10 | 9 | 0
7417 | 2023-11-06 01:00 | 93.8472 | 53.53 | 1 | 0 | 9 | 0 | 147.3772
7418 | 2023-11-06 02:00 | 76.7887 | 53.53 | 20 | 10 | 0 | 9.5 | 2606.3733
7419 | 2023-11-06 03:00 | 71.0098 | 53.53 | 20 | 10 | 0 | 19 | 2490.7961
7420 | 2023-11-06 04:00 | 80.5585 | 53.53 | 10 | 0 | 0 | 19 | 1340.8845
7421 | 2023-11-06 05:00 | 77.8037 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1451.5835
7422 | 2023-11-06 06:00 | 83.376 | 53.53 | 10 | 0 | 0 | 20 | 1369.0597
7423 | 2023-11-06 07:00 | 100.4474 | 53.53 | 10 | 0 | 0 | 20 | 1539.774
7424 | 2023-11-06 08:00 | 110.4976 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.7638
7425 | 2023-11-06 09:00 | 100.0979 | 65.03 | 20 | 10 | 0 | 20 | 3302.5572
7426 | 2023-11-06 10:00 | 112.8797 | 65.03 | 10 | 0 | 0 | 20 | 1779.0968
7427 | 2023-11-06 11:00 | 106.536 | 65.03 | 10 | 0 | 0 | 20 | 1715.6599
7428 | 2023-11-06 12:00 | 107.6795 | 65.03 | 10 | 0 | 0 | 20 | 1727.0953
7429 | 2023-11-06 13:00 | 118.137 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 91.5835
7430 | 2023-11-06 14:00 | 104.0451 | 65.03 | 20 | 10 | 0 | 20 | 3381.502
7431 | 2023-11-06 15:00 | 121.3942 | 65.03 | 10 | 0 | 0 | 20 | 1864.2419
7432 | 2023-11-06 16:00 | 122.4584 | 65.03 | 0 | 0 | 10 | 10 | 0
7433 | 2023-11-06 17:00 | 130.2325 | 66.4 | 0 | 0 | 10 | 0 | 0
7434 | 2023-11-06 18:00 | 117.5267 | 66.4 | 10 | 0 | 0 | 0 | 1839.2675
7435 | 2023-11-06 19:00 | 111.8728 | 65.03 | 10 | 0 | 0 | 0 | 1769.0283
7436 | 2023-11-06 20:00 | 113.4524 | 65.03 | 10 | 0 | 0 | 0 | 1784.8241
7437 | 2023-11-06 21:00 | 104.7478 | 65.03 | 10 | 0 | 0 | 0 | 1697.7781
7438 | 2023-11-06 22:00 | 98.89 | 65.03 | 10 | 0 | 0 | 0 | 1639.1999
7439 | 2023-11-06 23:00 | 109.4485 | 53.53 | 10 | 0 | 0 | 0 | 1629.7846
7440 | 2023-11-07 00:00 | 93.2042 | 53.53 | 10 | 0 | 0 | 0 | 1467.3416
7441 | 2023-11-07 01:00 | 95.9112 | 53.53 | 10 | 0 | 0 | 0 | 1494.4122
7442 | 2023-11-07 02:00 | 83.1619 | 53.53 | 10 | 0 | 0 | 0 | 1366.9186
7443 | 2023-11-07 03:00 | 71.7982 | 53.53 | 20 | 10 | 0 | 9.5 | 2506.5641
7444 | 2023-11-07 04:00 | 78.0905 | 53.53 | 20 | 10 | 0 | 19 | 2632.4107
7445 | 2023-11-07 05:00 | 88.5594 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 213.1341
7446 | 2023-11-07 06:00 | 80.5329 | 53.53 | 20 | 10 | 0 | 20 | 2681.257
7447 | 2023-11-07 07:00 | 110.245 | 53.53 | 10 | 0 | 0 | 20 | 1637.7502
7448 | 2023-11-07 08:00 | 119.0248 | 65.03 | 0 | 0 | 10 | 10 | 0
7449 | 2023-11-07 09:00 | 108.9564 | 65.03 | 10 | 0 | 0 | 10 | 1739.8641
7450 | 2023-11-07 10:00 | 96.3003 | 65.03 | 20 | 10 | 0 | 19.5 | 3226.605
7451 | 2023-11-07 11:00 | 101.8403 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1756.5295
7452 | 2023-11-07 12:00 | 115.3319 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 90.1809
7453 | 2023-11-07 13:00 | 99.6005 | 65.03 | 20 | 10 | 0 | 20 | 3292.61
7454 | 2023-11-07 14:00 | 106.5644 | 65.03 | 10 | 0 | 0 | 20 | 1715.9435
7455 | 2023-11-07 15:00 | 111.5703 | 65.03 | 10 | 0 | 0 | 20 | 1766.0028
7456 | 2023-11-07 16:00 | 122.7498 | 65.03 | 0 | 0 | 10 | 10 | 0
7457 | 2023-11-07 17:00 | 119.9371 | 66.4 | 0 | 0 | 10 | 0 | 0
7458 | 2023-11-07 18:00 | 119.5094 | 66.4 | 10 | 0 | 0 | 0 | 1859.094
7459 | 2023-11-07 19:00 | -41.9971 | 65.03 | 20 | 10 | 0 | 9.5 | 460.6577
7460 | 2023-11-07 20:00 | 106.6737 | 65.03 | 10 | 0 | 0 | 9.5 | 1717.0368
7461 | 2023-11-07 21:00 | 102.7678 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1766.2928
7462 | 2023-11-07 22:00 | 113.1473 | 65.03 | 0 | 0 | 10 | 0 | 0
7463 | 2023-11-07 23:00 | 93.5691 | 53.53 | 20 | 10 | 0 | 9.5 | 2941.9811
7464 | 2023-11-08 00:00 | 99.816 | 53.53 | 10 | 0 | 0 | 9.5 | 1533.4595
7465 | 2023-11-08 01:00 | 102.4707 | 53.53 | 0.5 | 0 | 9.5 | 0 | 78.0003
7466 | 2023-11-08 02:00 | 76.0698 | 53.53 | 20 | 10 | 0 | 9.5 | 2591.9954
7467 | 2023-11-08 03:00 | 86.0604 | 53.53 | 10 | 0 | 0 | 9.5 | 1395.9041
7468 | 2023-11-08 04:00 | 80.0408 | 53.53 | 20 | 10 | 0 | 19 | 2671.4167
7469 | 2023-11-08 05:00 | 85.5734 | 53.53 | 10 | 0 | 0 | 19 | 1391.0336
7470 | 2023-11-08 06:00 | 80.3973 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1480.2492
7471 | 2023-11-08 07:00 | 101.8869 | 53.53 | 10 | 0 | 0 | 20 | 1554.169
7472 | 2023-11-08 08:00 | 104.5781 | 65.03 | 10 | 0 | 0 | 20 | 1696.0813
7473 | 2023-11-08 09:00 | 104.5882 | 65.03 | 10 | 0 | 0 | 20 | 1696.1818
7474 | 2023-11-08 10:00 | 119.9948 | 65.03 | 0 | 0 | 10 | 10 | 0
7475 | 2023-11-08 11:00 | 114.1493 | 65.03 | 0 | 0 | 10 | 0 | 0
7476 | 2023-11-08 12:00 | 102.2916 | 65.03 | 20 | 10 | 0 | 9.5 | 3346.432
7477 | 2023-11-08 13:00 | 110.2923 | 65.03 | 10 | 0 | 0 | 9.5 | 1753.2226
7478 | 2023-11-08 14:00 | 96.1632 | 65.03 | 20 | 10 | 0 | 19 | 3223.8645
7479 | 2023-11-08 15:00 | 104.944 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1878.6595
7480 | 2023-11-08 16:00 | 117.2525 | 65.03 | 10 | 0 | 0 | 20 | 1822.8252
7481 | 2023-11-08 17:00 | 122.9771 | 66.4 | 0 | 0 | 10 | 10 | 0
7482 | 2023-11-08 18:00 | 124.7985 | 66.4 | 0 | 0 | 10 | 0 | 0
7483 | 2023-11-08 19:00 | 109.0127 | 65.03 | 10 | 0 | 0 | 0 | 1740.4272
7484 | 2023-11-08 20:00 | 101.1229 | 65.03 | 10 | 0 | 0 | 0 | 1661.5291
7485 | 2023-11-08 21:00 | 106.5685 | 65.03 | 10 | 0 | 0 | 0 | 1715.9855
7486 | 2023-11-08 22:00 | 107.6433 | 65.03 | 10 | 0 | 0 | 0 | 1726.7328
7487 | 2023-11-08 23:00 | 107.2658 | 53.53 | 10 | 0 | 0 | 0 | 1607.9581
7488 | 2023-11-09 00:00 | 97.3701 | 53.53 | 10 | 0 | 0 | 0 | 1509.0008
7489 | 2023-11-09 01:00 | 97.6863 | 53.53 | 10 | 0 | 0 | 0 | 1512.1625
7490 | 2023-11-09 02:00 | 70.6624 | 53.53 | 20 | 10 | 0 | 9.5 | 2483.8484
7491 | 2023-11-09 03:00 | 77.4105 | 53.53 | 10 | 0 | 0 | 9.5 | 1309.405
7492 | 2023-11-09 04:00 | 71.021 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1376.616
7493 | 2023-11-09 05:00 | -10.3389 | 53.53 | 20 | 10 | 0 | 20 | 863.8215
7494 | 2023-11-09 06:00 | 71.9515 | 53.53 | 10 | 0 | 0 | 20 | 1254.8149
7495 | 2023-11-09 07:00 | 113.2084 | 53.53 | 10 | 0 | 0 | 20 | 1667.384
7496 | 2023-11-09 08:00 | 106.9493 | 65.03 | 10 | 0 | 0 | 20 | 1719.7927
7497 | 2023-11-09 09:00 | 110.603 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.8165
7498 | 2023-11-09 10:00 | 105.3291 | 65.03 | 10 | 0 | 0 | 10.5 | 1703.5906
7499 | 2023-11-09 11:00 | 98.5084 | 65.03 | 20 | 10 | 0 | 20 | 3270.7674
7500 | 2023-11-09 12:00 | 117.0041 | 65.03 | 0 | 0 | 10 | 10 | 0
7501 | 2023-11-09 13:00 | 96.9278 | 65.03 | 20 | 10 | 0 | 19.5 | 3239.1562
7502 | 2023-11-09 14:00 | 105.0652 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1790.4757
7503 | 2023-11-09 15:00 | 108.492 | 65.03 | 10 | 0 | 0 | 20 | 1735.2203
7504 | 2023-11-09 16:00 | 110.6881 | 65.03 | 10 | 0 | 0 | 20 | 1757.1815
7505 | 2023-11-09 17:00 | 119.0026 | 66.4 | 0 | 0 | 10 | 10 | 0
7506 | 2023-11-09 18:00 | 113.302 | 66.4 | 10 | 0 | 0 | 10 | 1797.0204
7507 | 2023-11-09 19:00 | 118.5576 | 65.03 | 0 | 0 | 10 | 0 | 0
7508 | 2023-11-09 20:00 | 98.8687 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1725.249
7509 | 2023-11-09 21:00 | 98.7234 | 65.03 | 20 | 10 | 0 | 10 | 3275.0677
7510 | 2023-11-09 22:00 | 112.343 | 65.03 | 0 | 0 | 10 | 0 | 0
7511 | 2023-11-09 23:00 | 91.2692 | 53.53 | 20 | 10 | 0 | 9.5 | 2895.9836
7512 | 2023-11-10 00:00 | 101.2607 | 53.53 | 0.5 | 0 | 9.5 | 0 | 77.3954
7513 | 2023-11-10 01:00 | 100.1142 | 53.53 | 10 | 0 | 0 | 0 | 1536.4418
7514 | 2023-11-10 02:00 | 87.2468 | 53.53 | 10 | 0 | 0 | 0 | 1407.7679
7515 | 2023-11-10 03:00 | 77.9195 | 53.53 | 20 | 10 | 0 | 9.5 | 2628.9899
7516 | 2023-11-10 04:00 | 85.5951 | 53.53 | 10 | 0 | 0 | 9.5 | 1391.2509
7517 | 2023-11-10 05:00 | 77.6395 | 53.53 | 20 | 10 | 0 | 19 | 2623.3891
7518 | 2023-11-10 06:00 | 82.3781 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1502.1418
7519 | 2023-11-10 07:00 | 89.825 | 53.53 | 10 | 0 | 0 | 20 | 1433.5495
7520 | 2023-11-10 08:00 | 95.2276 | 65.03 | 10 | 0 | 0 | 20 | 1602.5761
7521 | 2023-11-10 09:00 | 111.8965 | 65.03 | 10 | 0 | 0 | 20 | 1769.265
7522 | 2023-11-10 10:00 | 112.3507 | 65.03 | 10 | 0 | 0 | 20 | 1773.8066
7523 | 2023-11-10 11:00 | 112.7315 | 65.03 | 10 | 0 | 0 | 20 | 1777.6148
7524 | 2023-11-10 12:00 | 105.2557 | 65.03 | 10 | 0 | 0 | 20 | 1702.8566
7525 | 2023-11-10 13:00 | 122.9854 | 65.03 | 0 | 0 | 10 | 10 | 0
7526 | 2023-11-10 14:00 | 105.6766 | 65.03 | 20 | 10 | 0 | 19.5 | 3414.1314
7527 | 2023-11-10 15:00 | 112.2628 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1866.2404
7528 | 2023-11-10 16:00 | 113.7806 | 65.03 | 10 | 0 | 0 | 20 | 1788.1062
7529 | 2023-11-10 17:00 | 140.7653 | 66.4 | 0 | 0 | 10 | 10 | 0
7530 | 2023-11-10 18:00 | 121.6302 | 66.4 | 0 | 0 | 10 | 0 | 0
7531 | 2023-11-10 19:00 | 119.4495 | 65.03 | 10 | 0 | 0 | 0 | 1844.7948
7532 | 2023-11-10 20:00 | 94.8479 | 65.03 | 20 | 10 | 0 | 9.5 | 3197.5576
7533 | 2023-11-10 21:00 | 118.7269 | 65.03 | 0.5 | 0 | 9.5 | 0 | 91.8785
7534 | 2023-11-10 22:00 | 107.2674 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1813.6565
7535 | 2023-11-10 23:00 | 102.538 | 53.53 | 20 | 10 | 0 | 10 | 3121.3603
7536 | 2023-11-11 00:00 | 129.5794 | 53.53 | 0 | 0 | 10 | 0 | 0
7537 | 2023-11-11 01:00 | 93.459 | 53.53 | 10 | 0 | 0 | 0 | 1469.8896
7538 | 2023-11-11 02:00 | 62.8129 | 53.53 | 20 | 10 | 0 | 9.5 | 2326.8589
7539 | 2023-11-11 03:00 | 69.4714 | 53.53 | 10 | 0 | 0 | 9.5 | 1230.0137
7540 | 2023-11-11 04:00 | 64.5594 | 53.53 | 20 | 10 | 0 | 19 | 2361.7881
7541 | 2023-11-11 05:00 | 68.0988 | 53.53 | 10 | 0 | 0 | 19 | 1216.2882
7542 | 2023-11-11 06:00 | 68.0541 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1343.8242
7543 | 2023-11-11 07:00 | 86.8615 | 53.53 | 10 | 0 | 0 | 20 | 1403.9151
7544 | 2023-11-11 08:00 | 92.3576 | 53.53 | 10 | 0 | 0 | 20 | 1458.8761
7545 | 2023-11-11 09:00 | 116.2094 | 53.53 | 0 | 0 | 10 | 10 | 0
7546 | 2023-11-11 10:00 | 103.2432 | 53.53 | 10 | 0 | 0 | 10 | 1567.7321
7547 | 2023-11-11 11:00 | 99.2632 | 53.53 | 20 | 10 | 0 | 19.5 | 3055.8638
7548 | 2023-11-11 12:00 | 107.2782 | 53.53 | 10 | 0 | 0 | 19.5 | 1608.0819
7549 | 2023-11-11 13:00 | 104.6931 | 53.53 | 10 | 0 | 0 | 19.5 | 1582.2314
7550 | 2023-11-11 14:00 | 103.0539 | 53.53 | 10 | 0 | 0 | 19.5 | 1565.839
7551 | 2023-11-11 15:00 | 106.6018 | 53.53 | 10 | 0 | 0 | 19.5 | 1601.3176
7552 | 2023-11-11 16:00 | 101.9233 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1636.3502
7553 | 2023-11-11 17:00 | 121.466 | 53.53 | 0 | 0 | 10 | 10 | 0
7554 | 2023-11-11 18:00 | 122.2356 | 53.53 | 0 | 0 | 10 | 0 | 0
7555 | 2023-11-11 19:00 | 117.149 | 53.53 | 10 | 0 | 0 | 0 | 1706.7897
7556 | 2023-11-11 20:00 | 94.2988 | 53.53 | 20 | 10 | 0 | 9.5 | 2956.5762
7557 | 2023-11-11 21:00 | 110.4653 | 53.53 | 0.5 | 0 | 9.5 | 0 | 81.9976
7558 | 2023-11-11 22:00 | 92.5591 | 53.53 | 10 | 0 | 0 | 0 | 1460.8913
7559 | 2023-11-11 23:00 | 94.0124 | 53.53 | 10 | 0 | 0 | 0 | 1475.4237
7560 | 2023-11-12 00:00 | 94.2036 | 53.53 | 10 | 0 | 0 | 0 | 1477.3359
7561 | 2023-11-12 01:00 | 86.7203 | 53.53 | 10 | 0 | 0 | 0 | 1402.5027
7562 | 2023-11-12 02:00 | 65.5179 | 53.53 | 20 | 10 | 0 | 9.5 | 2380.9581
7563 | 2023-11-12 03:00 | 68.3804 | 53.53 | 10 | 0 | 0 | 9.5 | 1219.1042
7564 | 2023-11-12 04:00 | 67.4663 | 53.53 | 10 | 0 | 0 | 9.5 | 1209.9631
7565 | 2023-11-12 05:00 | 62.0405 | 53.53 | 20 | 10 | 0 | 19 | 2311.41
7566 | 2023-11-12 06:00 | 66.4599 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1326.2047
7567 | 2023-11-12 07:00 | 92.9769 | 53.53 | 10 | 0 | 0 | 20 | 1465.0688
7568 | 2023-11-12 08:00 | 112.4475 | 53.53 | 0 | 0 | 10 | 10 | 0
7569 | 2023-11-12 09:00 | 105.422 | 53.53 | 10 | 0 | 0 | 10 | 1589.52
7570 | 2023-11-12 10:00 | 87.3601 | 53.53 | 20 | 10 | 0 | 19.5 | 2817.8011
7571 | 2023-11-12 11:00 | 106.2019 | 53.53 | 1 | 0 | 9 | 10.5 | 159.7319
7572 | 2023-11-12 12:00 | 97.0439 | 53.53 | 20 | 10 | 0 | 20 | 3011.4775
7573 | 2023-11-12 13:00 | 104.5382 | 53.53 | 10 | 0 | 0 | 20 | 1580.6818
7574 | 2023-11-12 14:00 | 100.7925 | 53.53 | 10 | 0 | 0 | 20 | 1543.2252
7575 | 2023-11-12 15:00 | 99.4941 | 53.53 | 10 | 0 | 0 | 20 | 1530.2413
7576 | 2023-11-12 16:00 | 100.1432 | 53.53 | 10 | 0 | 0 | 20 | 1536.7318
7577 | 2023-11-12 17:00 | 115.7307 | 53.53 | 10 | 0 | 0 | 20 | 1692.6069
7578 | 2023-11-12 18:00 | 128.318 | 53.53 | 0 | 0 | 10 | 10 | 0
7579 | 2023-11-12 19:00 | 115.7513 | 53.53 | 0 | 0 | 10 | 0 | 0
7580 | 2023-11-12 20:00 | 105.5219 | 53.53 | 10 | 0 | 0 | 0 | 1590.5195
7581 | 2023-11-12 21:00 | 104.0418 | 53.53 | 10 | 0 | 0 | 0 | 1575.7184
7582 | 2023-11-12 22:00 | 101.4368 | 53.53 | 10 | 0 | 0 | 0 | 1549.6685
7583 | 2023-11-12 23:00 | 80.5256 | 53.53 | 20 | 10 | 0 | 9.5 | 2681.1123
7584 | 2023-11-13 00:00 | 108.8465 | 53.53 | 0.5 | 0 | 9.5 | 0 | 81.1882
7585 | 2023-11-13 01:00 | 95.6895 | 53.53 | 10 | 0 | 0 | 0 | 1492.1949
7586 | 2023-11-13 02:00 | 84.8861 | 53.53 | 10 | 0 | 0 | 0 | 1384.1612
7587 | 2023-11-13 03:00 | 72.572 | 53.53 | 10 | 0 | 0 | 0 | 1261.02
7588 | 2023-11-13 04:00 | 71.4185 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1381.0096
7589 | 2023-11-13 05:00 | -50.395 | 53.53 | 20 | 10 | 0 | 10.5 | 62.7001
7590 | 2023-11-13 06:00 | -9.7258 | 53.53 | 20 | 10 | 0 | 20 | 876.0842
7591 | 2023-11-13 07:00 | 109.1568 | 53.53 | 10 | 0 | 0 | 20 | 1626.8685
7592 | 2023-11-13 08:00 | 109.8024 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.4162
7593 | 2023-11-13 09:00 | 105.9379 | 65.03 | 10 | 0 | 0 | 10.5 | 1709.6788
7594 | 2023-11-13 10:00 | 108.5643 | 65.03 | 10 | 0 | 0 | 10.5 | 1735.9434
7595 | 2023-11-13 11:00 | 100.8192 | 65.03 | 20 | 10 | 0 | 20 | 3316.9834
7596 | 2023-11-13 12:00 | 108.7954 | 65.03 | 10 | 0 | 0 | 20 | 1738.2536
7597 | 2023-11-13 13:00 | 101.9647 | 65.03 | 10 | 0 | 0 | 20 | 1669.947
7598 | 2023-11-13 14:00 | 106.1016 | 65.03 | 10 | 0 | 0 | 20 | 1711.3165
7599 | 2023-11-13 15:00 | 116.8969 | 65.03 | 10 | 0 | 0 | 20 | 1819.2692
7600 | 2023-11-13 16:00 | 110.8793 | 65.03 | 10 | 0 | 0 | 20 | 1759.0931
7601 | 2023-11-13 17:00 | 114.9245 | 66.4 | 10 | 0 | 0 | 20 | 1813.245
7602 | 2023-11-13 18:00 | 131.1743 | 66.4 | 0 | 0 | 10 | 10 | 0
7603 | 2023-11-13 19:00 | 123.8451 | 65.03 | 0 | 0 | 10 | 0 | 0
7604 | 2023-11-13 20:00 | 100.1454 | 65.03 | 20 | 10 | 0 | 9.5 | 3303.508
7605 | 2023-11-13 21:00 | 110.1752 | 65.03 | 0.5 | 0 | 9.5 | 0 | 87.6026
7606 | 2023-11-13 22:00 | 102.6752 | 65.03 | 10 | 0 | 0 | 0 | 1677.0519
7607 | 2023-11-13 23:00 | 91.5208 | 53.53 | 20 | 10 | 0 | 9.5 | 2901.0164
7608 | 2023-11-14 00:00 | 117.4182 | 53.53 | 0.5 | 0 | 9.5 | 0 | 85.4741
7609 | 2023-11-14 01:00 | -12.4048 | 53.53 | 20 | 10 | 0 | 9.5 | 822.5035
7610 | 2023-11-14 02:00 | 78.2953 | 53.53 | 0.5 | 0 | 9.5 | 0 | 65.9127
7611 | 2023-11-14 03:00 | -29.7817 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 262.4816
7612 | 2023-11-14 04:00 | -47.671 | 53.53 | 20 | 10 | 0 | 10.5 | 117.1794
7613 | 2023-11-14 05:00 | -78.7086 | 53.53 | 20 | 10 | 0 | 20 | -503.5717
7614 | 2023-11-14 06:00 | 69.6254 | 53.53 | 10 | 0 | 0 | 20 | 1231.5535
7615 | 2023-11-14 07:00 | 94.293 | 53.53 | 10 | 0 | 0 | 20 | 1478.2295
7616 | 2023-11-14 08:00 | 121.1206 | 65.03 | 0 | 0 | 10 | 10 | 0
7617 | 2023-11-14 09:00 | 115.9874 | 65.03 | 10 | 0 | 0 | 10 | 1810.1738
7618 | 2023-11-14 10:00 | 107.057 | 65.03 | 11.0526 | 1.0526 | 0 | 11 | 1902.0144
7619 | 2023-11-14 11:00 | 121.6433 | 65.03 | 0 | 0 | 10 | 1 | 0
7620 | 2023-11-14 12:00 | 115.1871 | 65.03 | 10 | 0 | 0 | 1 | 1802.1705
7621 | 2023-11-14 13:00 | 106.9767 | 65.03 | 20 | 10 | 0 | 10.5 | 3440.135
7622 | 2023-11-14 14:00 | 107.6844 | 65.03 | 10 | 0 | 0 | 10.5 | 1727.1444
7623 | 2023-11-14 15:00 | 111.4943 | 65.03 | 10 | 0 | 0 | 10.5 | 1765.2431
7624 | 2023-11-14 16:00 | 103.3768 | 65.03 | 20 | 10 | 0 | 20 | 3368.1355
7625 | 2023-11-14 17:00 | 123.9321 | 66.4 | 0 | 0 | 10 | 10 | 0
7626 | 2023-11-14 18:00 | 126.3226 | 66.4 | 0 | 0 | 10 | 0 | 0
7627 | 2023-11-14 19:00 | 113.9695 | 65.03 | 10 | 0 | 0 | 0 | 1789.9951
7628 | 2023-11-14 20:00 | 102.518 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1763.6629
7629 | 2023-11-14 21:00 | 101.7256 | 65.03 | 20 | 10 | 0 | 10 | 3335.1129
7630 | 2023-11-14 22:00 | 112.9301 | 65.03 | 0 | 0 | 10 | 0 | 0
7631 | 2023-11-14 23:00 | 88.2738 | 53.53 | 20 | 10 | 0 | 9.5 | 2836.0765
7632 | 2023-11-15 00:00 | 96.1947 | 53.53 | 0.5 | 0 | 9.5 | 0 | 74.8623
7633 | 2023-11-15 01:00 | 95.5341 | 53.53 | 10 | 0 | 0 | 0 | 1490.6411
7634 | 2023-11-15 02:00 | 87.2429 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1630.0026
7635 | 2023-11-15 03:00 | 78.5738 | 53.53 | 20 | 10 | 0 | 11 | 2642.0766
7636 | 2023-11-15 04:00 | 96.7482 | 53.53 | 0 | 0 | 10 | 1 | 0
7637 | 2023-11-15 05:00 | 84.3926 | 53.53 | 20 | 10 | 0 | 10.5 | 2758.4522
7638 | 2023-11-15 06:00 | -23.2591 | 53.53 | 20 | 10 | 0 | 20 | 605.4175
7639 | 2023-11-15 07:00 | 100.7619 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 77.146
7640 | 2023-11-15 08:00 | -41.7235 | 65.03 | 20 | 10 | 0 | 20 | 466.1308
7641 | 2023-11-15 09:00 | 116.2509 | 65.03 | 0 | 0 | 10 | 10 | 0
7642 | 2023-11-15 10:00 | 100.662 | 65.03 | 20 | 10 | 0 | 19.5 | 3313.8403
7643 | 2023-11-15 11:00 | 103.4247 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1773.2074
7644 | 2023-11-15 12:00 | 112.5606 | 65.03 | 10 | 0 | 0 | 20 | 1775.9061
7645 | 2023-11-15 13:00 | 120.0095 | 65.03 | 0 | 0 | 10 | 10 | 0
7646 | 2023-11-15 14:00 | 96.812 | 65.03 | 20 | 10 | 0 | 19.5 | 3236.8392
7647 | 2023-11-15 15:00 | 121.6571 | 65.03 | 0 | 0 | 10 | 9.5 | 0
7648 | 2023-11-15 16:00 | 107.8691 | 65.03 | 10 | 0 | 0 | 9.5 | 1728.9908
7649 | 2023-11-15 17:00 | 113.105 | 66.4 | 10 | 0 | 0 | 9.5 | 1795.05
7650 | 2023-11-15 18:00 | 109.0573 | 66.4 | 10 | 0 | 0 | 9.5 | 1754.5728
7651 | 2023-11-15 19:00 | 114.6991 | 65.03 | 0.5 | 0 | 9.5 | 0 | 89.8645
7652 | 2023-11-15 20:00 | 103.751 | 65.03 | 10 | 0 | 0 | 0 | 1687.8096
7653 | 2023-11-15 21:00 | 103.4089 | 65.03 | 10 | 0 | 0 | 0 | 1684.3892
7654 | 2023-11-15 22:00 | -11.3215 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 593.6207
7655 | 2023-11-15 23:00 | -12.2249 | 53.53 | 20 | 10 | 0 | 10.5 | 826.1021
7656 | 2023-11-16 00:00 | -62.5773 | 53.53 | 20 | 10 | 0 | 20 | -180.9455
7657 | 2023-11-16 01:00 | 95.9844 | 53.53 | 0 | 0 | 10 | 10 | 0
7658 | 2023-11-16 02:00 | 79.1517 | 53.53 | 0 | 0 | 10 | 0 | 0
7659 | 2023-11-16 03:00 | -38.7018 | 53.53 | 10 | 0 | 0 | 0 | 148.2822
7660 | 2023-11-16 04:00 | -56.759 | 53.53 | 11.5 | 10 | 8.5 | 1 | -37.1336
7661 | 2023-11-16 05:00 | -73.7828 | 53.53 | 20 | 10 | 0 | 10.5 | -405.0554
7662 | 2023-11-16 06:00 | -76.176 | 53.53 | 20 | 10 | 0 | 20 | -452.9199
7663 | 2023-11-16 07:00 | -26.0084 | 53.53 | 10 | 0 | 0 | 20 | 275.2159
7664 | 2023-11-16 08:00 | 105.1441 | 65.03 | 10 | 0 | 0 | 20 | 1701.7409
7665 | 2023-11-16 09:00 | 118.411 | 65.03 | 0 | 0 | 10 | 10 | 0
7666 | 2023-11-16 10:00 | 107.9219 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1820.5464
7667 | 2023-11-16 11:00 | 104.1963 | 65.03 | 20 | 10 | 0 | 20 | 3384.5259
7668 | 2023-11-16 12:00 | 116.9049 | 65.03 | 10 | 0 | 0 | 20 | 1819.3493
7669 | 2023-11-16 13:00 | 131.4444 | 65.03 | 0 | 0 | 10 | 10 | 0
7670 | 2023-11-16 14:00 | 110.5214 | 65.03 | 20 | 10 | 0 | 19.5 | 3511.0288
7671 | 2023-11-16 15:00 | 120.0972 | 65.03 | 10 | 0 | 0 | 19.5 | 1851.272
7672 | 2023-11-16 16:00 | 118.012 | 65.03 | 10 | 0 | 0 | 19.5 | 1830.4201
7673 | 2023-11-16 17:00 | 119.7448 | 66.4 | 0.5 | 0 | 9.5 | 10 | 93.0724
7674 | 2023-11-16 18:00 | 124.0989 | 66.4 | 0 | 0 | 10 | 0 | 0
7675 | 2023-11-16 19:00 | 115.9136 | 65.03 | 10 | 0 | 0 | 0 | 1809.436
7676 | 2023-11-16 20:00 | 102.4075 | 65.03 | 10 | 0 | 0 | 0 | 1674.3754
7677 | 2023-11-16 21:00 | 99.6166 | 65.03 | 10 | 0 | 0 | 0 | 1646.4663
7678 | 2023-11-16 22:00 | 101.0521 | 65.03 | 10 | 0 | 0 | 0 | 1660.8213
7679 | 2023-11-16 23:00 | 93.8618 | 53.53 | 20 | 10 | 0 | 9.5 | 2947.8368
7680 | 2023-11-17 00:00 | 96.8352 | 53.53 | 10 | 0 | 0 | 9.5 | 1503.652
7681 | 2023-11-17 01:00 | 103.2264 | 53.53 | 0.5 | 0 | 9.5 | 0 | 78.3782
7682 | 2023-11-17 02:00 | 78.018 | 53.53 | 10 | 0 | 0 | 0 | 1315.4799
7683 | 2023-11-17 03:00 | 68.1884 | 53.53 | 20 | 10 | 0 | 9.5 | 2434.3672
7684 | 2023-11-17 04:00 | 73.8845 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1408.2651
7685 | 2023-11-17 05:00 | 69.7465 | 53.53 | 20 | 10 | 0 | 20 | 2465.5301
7686 | 2023-11-17 06:00 | 80.7974 | 53.53 | 10 | 0 | 0 | 20 | 1343.2743
7687 | 2023-11-17 07:00 | 102.9731 | 53.53 | 10 | 0 | 0 | 20 | 1565.0308
7688 | 2023-11-17 08:00 | 110.8984 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 87.9642
7689 | 2023-11-17 09:00 | 103.6385 | 65.03 | 10 | 0 | 0 | 10.5 | 1686.6845
7690 | 2023-11-17 10:00 | 110.82 | 65.03 | 10 | 0 | 0 | 10.5 | 1758.4999
7691 | 2023-11-17 11:00 | 105.6098 | 65.03 | 10 | 0 | 0 | 10.5 | 1706.3979
7692 | 2023-11-17 12:00 | 101.6665 | 65.03 | 20 | 10 | 0 | 20 | 3333.9294
7693 | 2023-11-17 13:00 | 115.1307 | 65.03 | 10 | 0 | 0 | 20 | 1801.6067
7694 | 2023-11-17 14:00 | 115.8519 | 65.03 | 10 | 0 | 0 | 20 | 1808.8188
7695 | 2023-11-17 15:00 | 117.1313 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 91.0807
7696 | 2023-11-17 16:00 | 104.7278 | 65.03 | 20 | 10 | 0 | 20 | 3395.1565
7697 | 2023-11-17 17:00 | 134.5104 | 66.4 | 0 | 0 | 10 | 10 | 0
7698 | 2023-11-17 18:00 | 120.4575 | 66.4 | 10 | 0 | 0 | 10 | 1868.5747
7699 | 2023-11-17 19:00 | 129.313 | 65.03 | 0 | 0 | 10 | 0 | 0
7700 | 2023-11-17 20:00 | 100.3457 | 65.03 | 10 | 0 | 0 | 0 | 1653.7568
7701 | 2023-11-17 21:00 | 102.2736 | 65.03 | 10 | 0 | 0 | 0 | 1673.0364
7702 | 2023-11-17 22:00 | 90.99 | 65.03 | 10 | 0 | 0 | 0 | 1560.2004
7703 | 2023-11-17 23:00 | 96.7335 | 53.53 | 10 | 0 | 0 | 0 | 1502.6348
7704 | 2023-11-18 00:00 | 91.5909 | 53.53 | 10 | 0 | 0 | 0 | 1451.209
7705 | 2023-11-18 01:00 | 88.0046 | 53.53 | 10 | 0 | 0 | 0 | 1415.3457
7706 | 2023-11-18 02:00 | 88.2383 | 53.53 | 10 | 0 | 0 | 0 | 1417.6831
7707 | 2023-11-18 03:00 | 63.5377 | 53.53 | 20 | 10 | 0 | 9.5 | 2341.3545
7708 | 2023-11-18 04:00 | 67.0095 | 53.53 | 10 | 0 | 0 | 9.5 | 1205.3946
7709 | 2023-11-18 05:00 | 64.9549 | 53.53 | 20 | 10 | 0 | 19 | 2369.6983
7710 | 2023-11-18 06:00 | 67.0082 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1332.2645
7711 | 2023-11-18 07:00 | 99.9643 | 53.53 | 10 | 0 | 0 | 20 | 1534.943
7712 | 2023-11-18 08:00 | 114.8486 | 53.53 | 0 | 0 | 10 | 10 | 0
7713 | 2023-11-18 09:00 | 96.1581 | 53.53 | 10 | 0 | 0 | 10 | 1496.8809
7714 | 2023-11-18 10:00 | 96.0235 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1574.2476
7715 | 2023-11-18 11:00 | 93.566 | 53.53 | 20 | 10 | 0 | 20 | 2941.9198
7716 | 2023-11-18 12:00 | 112.8925 | 53.53 | 0 | 0 | 10 | 10 | 0
7717 | 2023-11-18 13:00 | 110.8923 | 53.53 | 0 | 0 | 10 | 0 | 0
7718 | 2023-11-18 14:00 | 100.1159 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1698.192
7719 | 2023-11-18 15:00 | 92.3437 | 53.53 | 20 | 10 | 0 | 10.5 | 2917.4742
7720 | 2023-11-18 16:00 | 92.7909 | 53.53 | 20 | 10 | 0 | 20 | 2926.4186
7721 | 2023-11-18 17:00 | 117.2113 | 53.53 | 0 | 0 | 10 | 10 | 0
7722 | 2023-11-18 18:00 | 120.3773 | 53.53 | 0 | 0 | 10 | 0 | 0
7723 | 2023-11-18 19:00 | 104.349 | 53.53 | 10 | 0 | 0 | 0 | 1578.7902
7724 | 2023-11-18 20:00 | 93.601 | 53.53 | 20 | 10 | 0 | 9.5 | 2942.6197
7725 | 2023-11-18 21:00 | 111.5225 | 53.53 | 0.5 | 0 | 9.5 | 0 | 82.5263
7726 | 2023-11-18 22:00 | 94.3191 | 53.53 | 20 | 10 | 0 | 9.5 | 2956.9814
7727 | 2023-11-18 23:00 | 104.9844 | 53.53 | 0.5 | 0 | 9.5 | 0 | 79.2572
7728 | 2023-11-19 00:00 | 96.2724 | 53.53 | 10 | 0 | 0 | 0 | 1498.0239
7729 | 2023-11-19 01:00 | 83.9564 | 53.53 | 10 | 0 | 0 | 0 | 1374.8636
7730 | 2023-11-19 02:00 | 68.7969 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1352.0339
7731 | 2023-11-19 03:00 | 69.9515 | 53.53 | 10 | 0 | 0 | 1 | 1234.8149
7732 | 2023-11-19 04:00 | 64.6845 | 53.53 | 20 | 10 | 0 | 10.5 | 2364.29
7733 | 2023-11-19 05:00 | 64.5869 | 53.53 | 20 | 10 | 0 | 20 | 2362.3388
7734 | 2023-11-19 06:00 | 85.1858 | 53.53 | 10 | 0 | 0 | 20 | 1387.1581
7735 | 2023-11-19 07:00 | 84.545 | 53.53 | 10 | 0 | 0 | 20 | 1380.7498
7736 | 2023-11-19 08:00 | 110.4483 | 53.53 | 0 | 0 | 10 | 10 | 0
7737 | 2023-11-19 09:00 | 97.8299 | 53.53 | 10 | 0 | 0 | 10 | 1513.5995
7738 | 2023-11-19 10:00 | 100.7067 | 53.53 | 10 | 0 | 0 | 10 | 1542.3675
7739 | 2023-11-19 11:00 | 105.4881 | 53.53 | 1.5 | 0 | 8.5 | 1.5 | 238.5271
7740 | 2023-11-19 12:00 | 96.7891 | 53.53 | 20 | 10 | 0 | 11 | 3006.3818
7741 | 2023-11-19 13:00 | 105.5419 | 53.53 | 0 | 0 | 10 | 1 | 0
7742 | 2023-11-19 14:00 | 89.4288 | 53.53 | 20 | 10 | 0 | 10.5 | 2859.1763
7743 | 2023-11-19 15:00 | 104.4235 | 53.53 | 10 | 0 | 0 | 10.5 | 1579.5351
7744 | 2023-11-19 16:00 | 87.8195 | 53.53 | 20 | 10 | 0 | 20 | 2826.9898
7745 | 2023-11-19 17:00 | 114.2536 | 53.53 | 10 | 0 | 0 | 20 | 1677.8356
7746 | 2023-11-19 18:00 | 123.2009 | 53.53 | 0 | 0 | 10 | 10 | 0
7747 | 2023-11-19 19:00 | 121.0296 | 53.53 | 0 | 0 | 10 | 0 | 0
7748 | 2023-11-19 20:00 | 87.8328 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1488.0295
7749 | 2023-11-19 21:00 | 88.4997 | 53.53 | 10 | 0 | 0 | 0.5 | 1420.2967
7750 | 2023-11-19 22:00 | 91.2319 | 53.53 | 10 | 0 | 0 | 0.5 | 1447.619
7751 | 2023-11-19 23:00 | 92.3347 | 53.53 | 10 | 0 | 0 | 0.5 | 1458.6467
7752 | 2023-11-20 00:00 | 87.4878 | 53.53 | 20 | 10 | 0 | 10 | 2820.3557
7753 | 2023-11-20 01:00 | 98.7993 | 53.53 | 0 | 0 | 10 | 0 | 0
7754 | 2023-11-20 02:00 | 81.3466 | 53.53 | 10 | 0 | 0 | 0 | 1348.7662
7755 | 2023-11-20 03:00 | 76.8632 | 53.53 | 20 | 10 | 0 | 9.5 | 2607.8631
7756 | 2023-11-20 04:00 | 83.1656 | 53.53 | 10 | 0 | 0 | 9.5 | 1366.9564
7757 | 2023-11-20 05:00 | 80.6338 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1482.8634
7758 | 2023-11-20 06:00 | 75.1488 | 53.53 | 20 | 10 | 0 | 20 | 2573.5757
7759 | 2023-11-20 07:00 | 87.8838 | 53.53 | 10 | 0 | 0 | 20 | 1414.1378
7760 | 2023-11-20 08:00 | 109.9192 | 65.03 | 10 | 0 | 0 | 20 | 1749.492
7761 | 2023-11-20 09:00 | 102.6813 | 65.03 | 10 | 0 | 0 | 20 | 1677.1132
7762 | 2023-11-20 10:00 | 104.9162 | 65.03 | 10 | 0 | 0 | 20 | 1699.4618
7763 | 2023-11-20 11:00 | 112.7628 | 65.03 | 10 | 0 | 0 | 20 | 1777.9282
7764 | 2023-11-20 12:00 | 122.1457 | 65.03 | 0 | 0 | 10 | 10 | 0
7765 | 2023-11-20 13:00 | 108.6145 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1827.8366
7766 | 2023-11-20 14:00 | 113.4191 | 65.03 | 10 | 0 | 0 | 10.5 | 1784.4911
7767 | 2023-11-20 15:00 | 100.1067 | 65.03 | 20 | 10 | 0 | 20 | 3302.7349
7768 | 2023-11-20 16:00 | 110.8092 | 65.03 | 10 | 0 | 0 | 20 | 1758.3925
7769 | 2023-11-20 17:00 | 123.453 | 66.4 | 0 | 0 | 10 | 10 | 0
7770 | 2023-11-20 18:00 | 135.0471 | 66.4 | 0 | 0 | 10 | 0 | 0
7771 | 2023-11-20 19:00 | 120.1564 | 65.03 | 10 | 0 | 0 | 0 | 1851.8641
7772 | 2023-11-20 20:00 | 102.1502 | 65.03 | 20 | 10 | 0 | 9.5 | 3343.603
7773 | 2023-11-20 21:00 | 113.2455 | 65.03 | 0.5 | 0 | 9.5 | 0 | 89.1377
7774 | 2023-11-20 22:00 | 103.2175 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1771.0263
7775 | 2023-11-20 23:00 | 91.8238 | 53.53 | 20 | 10 | 0 | 10 | 2907.0758
7776 | 2023-11-21 00:00 | 127.6495 | 53.53 | 0 | 0 | 10 | 0 | 0
7777 | 2023-11-21 01:00 | 91.9872 | 53.53 | 10 | 0 | 0 | 0 | 1455.172
7778 | 2023-11-21 02:00 | 78.4177 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1458.3697
7779 | 2023-11-21 03:00 | 81.6385 | 53.53 | 10 | 0 | 0 | 1 | 1351.685
7780 | 2023-11-21 04:00 | 80.9882 | 53.53 | 10 | 0 | 0 | 1 | 1345.1821
7781 | 2023-11-21 05:00 | 77.515 | 53.53 | 20 | 10 | 0 | 10.5 | 2620.8995
7782 | 2023-11-21 06:00 | 77.5503 | 53.53 | 20 | 10 | 0 | 20 | 2621.6061
7783 | 2023-11-21 07:00 | 97.197 | 53.53 | 10 | 0 | 0 | 20 | 1507.2698
7784 | 2023-11-21 08:00 | 101.7857 | 65.03 | 10 | 0 | 0 | 20 | 1668.1569
7785 | 2023-11-21 09:00 | 131.5511 | 65.03 | 0 | 0 | 10 | 10 | 0
7786 | 2023-11-21 10:00 | 107.3016 | 65.03 | 10 | 0 | 0 | 10 | 1723.3164
7787 | 2023-11-21 11:00 | 113.8012 | 65.03 | 10 | 0 | 0 | 10 | 1788.312
7788 | 2023-11-21 12:00 | 106.5103 | 65.03 | 10 | 0 | 0 | 10 | 1715.4029
7789 | 2023-11-21 13:00 | 106.3743 | 65.03 | 10 | 0 | 0 | 10 | 1714.0428
7790 | 2023-11-21 14:00 | 105.7056 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1797.2164
7791 | 2023-11-21 15:00 | 99.6024 | 65.03 | 20 | 10 | 0 | 20 | 3292.6482
7792 | 2023-11-21 16:00 | 107.7222 | 65.03 | 10 | 0 | 0 | 20 | 1727.5221
7793 | 2023-11-21 17:00 | 121.0248 | 66.4 | 0 | 0 | 10 | 10 | 0
7794 | 2023-11-21 18:00 | 134.4267 | 66.4 | 0 | 0 | 10 | 0 | 0
7795 | 2023-11-21 19:00 | 116.3575 | 65.03 | 10 | 0 | 0 | 0 | 1813.8749
7796 | 2023-11-21 20:00 | 99.9237 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1736.3549
7797 | 2023-11-21 21:00 | 97.9917 | 65.03 | 20 | 10 | 0 | 10 | 3260.4345
7798 | 2023-11-21 22:00 | 117.4359 | 65.03 | 0 | 0 | 10 | 0 | 0
7799 | 2023-11-21 23:00 | 93.1587 | 53.53 | 20 | 10 | 0 | 9.5 | 2933.7749
7800 | 2023-11-22 00:00 | 103.4921 | 53.53 | 10 | 0 | 0 | 9.5 | 1570.2213
7801 | 2023-11-22 01:00 | 107.344 | 53.53 | 0.5 | 0 | 9.5 | 0 | 80.437
7802 | 2023-11-22 02:00 | 77.8261 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1451.8301
7803 | 2023-11-22 03:00 | 70.4391 | 53.53 | 20 | 10 | 0 | 10.5 | 2479.3829
7804 | 2023-11-22 04:00 | 70.5021 | 53.53 | 20 | 10 | 0 | 20 | 2480.6415
7805 | 2023-11-22 05:00 | 86.2545 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 69.8922
7806 | 2023-11-22 06:00 | 71.026 | 53.53 | 20 | 10 | 0 | 20 | 2491.1203
7807 | 2023-11-22 07:00 | 102.0184 | 53.53 | 10 | 0 | 0 | 20 | 1555.4838
7808 | 2023-11-22 08:00 | 109.7708 | 65.03 | 10 | 0 | 0 | 20 | 1748.008
7809 | 2023-11-22 09:00 | 111.893 | 65.03 | 1 | 0 | 9 | 11 | 176.923
7810 | 2023-11-22 10:00 | 112.6976 | 65.03 | 0 | 0 | 10 | 1 | 0
7811 | 2023-11-22 11:00 | 102.791 | 65.03 | 20 | 10 | 0 | 10.5 | 3356.4197
7812 | 2023-11-22 12:00 | -19.3055 | 65.03 | 20 | 10 | 0 | 20 | 914.4899
7813 | 2023-11-22 13:00 | 114.8787 | 65.03 | 0 | 0 | 10 | 10 | 0
7814 | 2023-11-22 14:00 | 104.597 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1785.5478
7815 | 2023-11-22 15:00 | 94.8537 | 65.03 | 20 | 10 | 0 | 20 | 3197.6739
7816 | 2023-11-22 16:00 | 114.2697 | 65.03 | 10 | 0 | 0 | 20 | 1792.9974
7817 | 2023-11-22 17:00 | 117.2184 | 66.4 | 10 | 0 | 0 | 20 | 1836.1838
7818 | 2023-11-22 18:00 | 127.6592 | 66.4 | 0 | 0 | 10 | 10 | 0
7819 | 2023-11-22 19:00 | 136.8655 | 65.03 | 0 | 0 | 10 | 0 | 0
7820 | 2023-11-22 20:00 | 104.0243 | 65.03 | 10 | 0 | 0 | 0 | 1690.5434
7821 | 2023-11-22 21:00 | 112.6019 | 65.03 | 10 | 0 | 0 | 0 | 1776.3194
7822 | 2023-11-22 22:00 | 105.0788 | 65.03 | 10 | 0 | 0 | 0 | 1701.0881
7823 | 2023-11-22 23:00 | 114.1481 | 53.53 | 10 | 0 | 0 | 0 | 1676.7809
7824 | 2023-11-23 00:00 | 92.0769 | 53.53 | 10 | 0 | 0 | 0 | 1456.0688
7825 | 2023-11-23 01:00 | 98.8368 | 53.53 | 10 | 0 | 0 | 0 | 1523.6677
7826 | 2023-11-23 02:00 | 84.4929 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1525.5166
7827 | 2023-11-23 03:00 | 77.5102 | 53.53 | 20 | 10 | 0 | 10.5 | 2620.8048
7828 | 2023-11-23 04:00 | 89.2216 | 53.53 | 10 | 0 | 0 | 10.5 | 1427.5156
7829 | 2023-11-23 05:00 | 75.8592 | 53.53 | 20 | 10 | 0 | 20 | 2587.7843
7830 | 2023-11-23 06:00 | 100.4092 | 53.53 | 10 | 0 | 0 | 20 | 1539.3923
7831 | 2023-11-23 07:00 | 121.1522 | 53.53 | 10 | 0 | 0 | 20 | 1746.822
7832 | 2023-11-23 08:00 | 111.1059 | 65.03 | 10 | 0 | 0 | 20 | 1761.3594
7833 | 2023-11-23 09:00 | 113.4062 | 65.03 | 1 | 0 | 9 | 11 | 178.4362
7834 | 2023-11-23 10:00 | 119.6421 | 65.03 | 0 | 0 | 10 | 1 | 0
7835 | 2023-11-23 11:00 | 101.4073 | 65.03 | 20 | 10 | 0 | 10.5 | 3328.7467
7836 | 2023-11-23 12:00 | 100.7639 | 65.03 | 20 | 10 | 0 | 20 | 3315.878
7837 | 2023-11-23 13:00 | 120.3432 | 65.03 | 0 | 0 | 10 | 10 | 0
7838 | 2023-11-23 14:00 | 111.04 | 65.03 | 10 | 0 | 0 | 10 | 1760.7004
7839 | 2023-11-23 15:00 | 107.2559 | 65.03 | 20 | 10 | 0 | 19.5 | 3445.719
7840 | 2023-11-23 16:00 | 108.9819 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1831.7039
7841 | 2023-11-23 17:00 | 111.1182 | 66.4 | 10 | 0 | 0 | 20 | 1775.1818
7842 | 2023-11-23 18:00 | 122.5092 | 66.4 | 0 | 0 | 10 | 10 | 0
7843 | 2023-11-23 19:00 | 118.843 | 65.03 | 0 | 0 | 10 | 0 | 0
7844 | 2023-11-23 20:00 | 111.8254 | 65.03 | 10 | 0 | 0 | 0 | 1768.5545
7845 | 2023-11-23 21:00 | 112.5945 | 65.03 | 10 | 0 | 0 | 0 | 1776.2451
7846 | 2023-11-23 22:00 | 108.6201 | 65.03 | 10 | 0 | 0 | 0 | 1736.5008
7847 | 2023-11-23 23:00 | 102.0474 | 53.53 | 10 | 0 | 0 | 0 | 1555.7735
7848 | 2023-11-24 00:00 | 89.8517 | 53.53 | 20 | 10 | 0 | 9.5 | 2867.6341
7849 | 2023-11-24 01:00 | 103.7448 | 53.53 | 0.5 | 0 | 9.5 | 0 | 78.6374
7850 | 2023-11-24 02:00 | 84.0939 | 53.53 | 20 | 10 | 0 | 9.5 | 2752.4775
7851 | 2023-11-24 03:00 | 90.2207 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1513.1649
7852 | 2023-11-24 04:00 | 101.0957 | 53.53 | 0 | 0 | 10 | 0 | 0
7853 | 2023-11-24 05:00 | 68.9442 | 53.53 | 20 | 10 | 0 | 9.5 | 2449.4848
7854 | 2023-11-24 06:00 | -33.3493 | 53.53 | 20 | 10 | 0 | 19 | 403.6149
7855 | 2023-11-24 07:00 | 93.9076 | 53.53 | 2 | 0 | 8 | 11 | 294.8752
7856 | 2023-11-24 08:00 | 110.2262 | 65.03 | 0 | 0 | 10 | 1 | 0
7857 | 2023-11-24 09:00 | -60.2716 | 65.03 | 20 | 10 | 0 | 10.5 | 95.1685
7858 | 2023-11-24 10:00 | -42.3119 | 65.03 | 20 | 10 | 0 | 20 | 454.3629
7859 | 2023-11-24 11:00 | 117.9254 | 65.03 | 0 | 0 | 10 | 10 | 0
7860 | 2023-11-24 12:00 | 101.8638 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1756.7766
7861 | 2023-11-24 13:00 | 102.1917 | 65.03 | 10 | 0 | 0 | 10.5 | 1672.2169
7862 | 2023-11-24 14:00 | 102.2847 | 65.03 | 10 | 0 | 0 | 10.5 | 1673.1465
7863 | 2023-11-24 15:00 | 106.3368 | 65.03 | 10 | 0 | 0 | 10.5 | 1713.6679
7864 | 2023-11-24 16:00 | 101.1913 | 65.03 | 20 | 10 | 0 | 20 | 3324.4251
7865 | 2023-11-24 17:00 | 123.5367 | 66.4 | 0 | 0 | 10 | 10 | 0
7866 | 2023-11-24 18:00 | 122.6874 | 66.4 | 0 | 0 | 10 | 0 | 0
7867 | 2023-11-24 19:00 | 118.6437 | 65.03 | 10 | 0 | 0 | 0 | 1836.7372
7868 | 2023-11-24 20:00 | 111.3907 | 65.03 | 10 | 0 | 0 | 0 | 1764.2069
7869 | 2023-11-24 21:00 | 103.456 | 65.03 | 20 | 10 | 0 | 9.5 | 3369.7202
7870 | 2023-11-24 22:00 | 113.285 | 65.03 | 0.5 | 0 | 9.5 | 0 | 89.1575
7871 | 2023-11-24 23:00 | 97.4774 | 53.53 | 10 | 0 | 0 | 0 | 1510.0741
7872 | 2023-11-25 00:00 | 90.7175 | 53.53 | 10 | 0 | 0 | 0 | 1442.475
7873 | 2023-11-25 01:00 | 87.0145 | 53.53 | 10 | 0 | 0 | 0 | 1405.4452
7874 | 2023-11-25 02:00 | 70.8455 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1374.6767
7875 | 2023-11-25 03:00 | 76.8536 | 53.53 | 10 | 0 | 0 | 1 | 1303.8364
7876 | 2023-11-25 04:00 | 67.9961 | 53.53 | 20 | 10 | 0 | 10.5 | 2430.521
7877 | 2023-11-25 05:00 | 75.105 | 53.53 | 10 | 0 | 0 | 10.5 | 1286.3504
7878 | 2023-11-25 06:00 | 65.4889 | 53.53 | 20 | 10 | 0 | 20 | 2380.3789
7879 | 2023-11-25 07:00 | 97.2915 | 53.53 | 10 | 0 | 0 | 20 | 1508.215
7880 | 2023-11-25 08:00 | 96.9063 | 53.53 | 10 | 0 | 0 | 20 | 1504.3632
7881 | 2023-11-25 09:00 | 108.1761 | 53.53 | 0 | 0 | 10 | 10 | 0
7882 | 2023-11-25 10:00 | 101.3598 | 53.53 | 10 | 0 | 0 | 10 | 1548.8984
7883 | 2023-11-25 11:00 | 115.3534 | 53.53 | 0 | 0 | 10 | 0 | 0
7884 | 2023-11-25 12:00 | 93.5822 | 53.53 | 10 | 0 | 0 | 0 | 1471.1222
7885 | 2023-11-25 13:00 | 91.9533 | 53.53 | 20 | 10 | 0 | 9.5 | 2909.6669
7886 | 2023-11-25 14:00 | 96.6787 | 53.53 | 10 | 0 | 0 | 9.5 | 1502.0871
7887 | 2023-11-25 15:00 | 92.4005 | 53.53 | 20 | 10 | 0 | 19 | 2918.6097
7888 | 2023-11-25 16:00 | 92.4098 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1613.0186
7889 | 2023-11-25 17:00 | 121.0229 | 53.53 | 0 | 0 | 10 | 10 | 0
7890 | 2023-11-25 18:00 | 115.867 | 53.53 | 0 | 0 | 10 | 0 | 0
7891 | 2023-11-25 19:00 | 112.5476 | 53.53 | 10 | 0 | 0 | 0 | 1660.7757
7892 | 2023-11-25 20:00 | 93.1582 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1544.0864
7893 | 2023-11-25 21:00 | 91.7974 | 53.53 | 20 | 10 | 0 | 10 | 2906.5475
7894 | 2023-11-25 22:00 | 111.9153 | 53.53 | 0 | 0 | 10 | 0 | 0
7895 | 2023-11-25 23:00 | 85.9482 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1468.1916
7896 | 2023-11-26 00:00 | 82.7127 | 53.53 | 20 | 10 | 0 | 10 | 2724.8541
7897 | 2023-11-26 01:00 | 97.6419 | 53.53 | 0 | 0 | 10 | 0 | 0
7898 | 2023-11-26 02:00 | -14.1941 | 53.53 | 20 | 10 | 0 | 9.5 | 786.7175
7899 | 2023-11-26 03:00 | 91.9842 | 53.53 | 0.5 | 0 | 9.5 | 0 | 72.7571
7900 | 2023-11-26 04:00 | -76.4304 | 53.53 | 20 | 10 | 0 | 9.5 | -458.0071
7901 | 2023-11-26 05:00 | 78.121 | 53.53 | 20 | 10 | 0 | 19 | 2633.0201
7902 | 2023-11-26 06:00 | 80.4873 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1481.2436
7903 | 2023-11-26 07:00 | 87.2787 | 53.53 | 10 | 0 | 0 | 20 | 1408.0872
7904 | 2023-11-26 08:00 | 95.9037 | 53.53 | 10 | 0 | 0 | 20 | 1494.3365
7905 | 2023-11-26 09:00 | 107.1254 | 53.53 | 0 | 0 | 10 | 10 | 0
7906 | 2023-11-26 10:00 | 105.6041 | 53.53 | 0 | 0 | 10 | 0 | 0
7907 | 2023-11-26 11:00 | 92.2723 | 53.53 | 20 | 10 | 0 | 9.5 | 2916.0455
7908 | 2023-11-26 12:00 | 93.7187 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1627.4859
7909 | 2023-11-26 13:00 | 87.5791 | 53.53 | 20 | 10 | 0 | 20 | 2822.1822
7910 | 2023-11-26 14:00 | 105.7873 | 53.53 | 10 | 0 | 0 | 20 | 1593.1735
7911 | 2023-11-26 15:00 | 99.0097 | 53.53 | 10 | 0 | 0 | 20 | 1525.3974
7912 | 2023-11-26 16:00 | 99.7113 | 53.53 | 10 | 0 | 0 | 20 | 1532.4128
7913 | 2023-11-26 17:00 | 105.9493 | 53.53 | 10 | 0 | 0 | 20 | 1594.7928
7914 | 2023-11-26 18:00 | 108.8816 | 53.53 | 0 | 0 | 10 | 10 | 0
7915 | 2023-11-26 19:00 | 112.5588 | 53.53 | 0 | 0 | 10 | 0 | 0
7916 | 2023-11-26 20:00 | 91.3319 | 53.53 | 20 | 10 | 0 | 9.5 | 2897.2371
7917 | 2023-11-26 21:00 | 96.7979 | 53.53 | 20 | 10 | 0 | 19 | 3006.5577
7918 | 2023-11-26 22:00 | 100.6807 | 53.53 | 10 | 0 | 0 | 19 | 1542.1067
7919 | 2023-11-26 23:00 | 115.2889 | 53.53 | 0 | 0 | 10 | 9 | 0
7920 | 2023-11-27 00:00 | 98.7486 | 53.53 | 11.0526 | 1.0526 | 0 | 10 | 1683.0796
7921 | 2023-11-27 01:00 | 108.8336 | 53.53 | 0 | 0 | 10 | 0 | 0
7922 | 2023-11-27 02:00 | 73.388 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1402.7775
7923 | 2023-11-27 03:00 | 69.024 | 53.53 | 20 | 10 | 0 | 10.5 | 2451.0791
7924 | 2023-11-27 04:00 | 76.3909 | 53.53 | 10 | 0 | 0 | 10.5 | 1299.2088
7925 | 2023-11-27 05:00 | 69.3785 | 53.53 | 20 | 10 | 0 | 20 | 2458.1694
7926 | 2023-11-27 06:00 | 79.0086 | 53.53 | 10 | 0 | 0 | 20 | 1325.386
7927 | 2023-11-27 07:00 | 93.6797 | 53.53 | 10 | 0 | 0 | 20 | 1472.0966
7928 | 2023-11-27 08:00 | 97.8081 | 65.03 | 10 | 0 | 0 | 20 | 1628.3812
7929 | 2023-11-27 09:00 | 125.983 | 65.03 | 0 | 0 | 10 | 10 | 0
7930 | 2023-11-27 10:00 | 105.1749 | 65.03 | 0 | 0 | 10 | 0 | 0
7931 | 2023-11-27 11:00 | -10.9773 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 597.4247
7932 | 2023-11-27 12:00 | -59.0064 | 65.03 | 20 | 10 | 0 | 10.5 | 120.4728
7933 | 2023-11-27 13:00 | -55.4939 | 65.03 | 20 | 10 | 0 | 20 | 190.723
7934 | 2023-11-27 14:00 | 118.5701 | 65.03 | 0 | 0 | 10 | 10 | 0
7935 | 2023-11-27 15:00 | 103.9609 | 65.03 | 20 | 10 | 0 | 19.5 | 3379.8182
7936 | 2023-11-27 16:00 | 105.1536 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1791.4064
7937 | 2023-11-27 17:00 | 126.6231 | 66.4 | 10 | 0 | 0 | 20 | 1930.2305
7938 | 2023-11-27 18:00 | 128.7679 | 66.4 | 0 | 0 | 10 | 10 | 0
7939 | 2023-11-27 19:00 | 130.3805 | 65.03 | 0 | 0 | 10 | 0 | 0
7940 | 2023-11-27 20:00 | 103.2342 | 65.03 | 10 | 0 | 0 | 0 | 1682.6423
7941 | 2023-11-27 21:00 | 108.1946 | 65.03 | 10 | 0 | 0 | 0 | 1732.2459
7942 | 2023-11-27 22:00 | 110.1653 | 65.03 | 10 | 0 | 0 | 0 | 1751.9534
7943 | 2023-11-27 23:00 | 100.4488 | 53.53 | 10 | 0 | 0 | 0 | 1539.7875
7944 | 2023-11-28 00:00 | 97.8509 | 53.53 | 10 | 0 | 0 | 0 | 1513.8094
7945 | 2023-11-28 01:00 | 90.1028 | 53.53 | 10 | 0 | 0 | 0 | 1436.3278
7946 | 2023-11-28 02:00 | 83.8213 | 53.53 | 10 | 0 | 0 | 0 | 1373.5133
7947 | 2023-11-28 03:00 | 79.2166 | 53.53 | 20 | 10 | 0 | 9.5 | 2654.9324
7948 | 2023-11-28 04:00 | -13.4625 | 53.53 | 20 | 10 | 0 | 19 | 801.3491
7949 | 2023-11-28 05:00 | 90.5774 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 216.161
7950 | 2023-11-28 06:00 | 70.1879 | 53.53 | 20 | 10 | 0 | 20 | 2474.3578
7951 | 2023-11-28 07:00 | 114.8375 | 53.53 | 10 | 0 | 0 | 20 | 1683.6745
7952 | 2023-11-28 08:00 | 108.7318 | 65.03 | 10 | 0 | 0 | 20 | 1737.6181
7953 | 2023-11-28 09:00 | 111.3968 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 88.2134
7954 | 2023-11-28 10:00 | 106.1043 | 65.03 | 10 | 0 | 0 | 10.5 | 1711.3431
7955 | 2023-11-28 11:00 | 99.0597 | 65.03 | 20 | 10 | 0 | 20 | 3281.7945
7956 | 2023-11-28 12:00 | 107.8729 | 65.03 | 10 | 0 | 0 | 20 | 1729.0286
7957 | 2023-11-28 13:00 | 111.5393 | 65.03 | 10 | 0 | 0 | 20 | 1765.6928
7958 | 2023-11-28 14:00 | 114.5211 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 89.7755
7959 | 2023-11-28 15:00 | 107.4563 | 65.03 | 10 | 0 | 0 | 10.5 | 1724.8632
7960 | 2023-11-28 16:00 | 96.8485 | 65.03 | 20 | 10 | 0 | 20 | 3237.5708
7961 | 2023-11-28 17:00 | 114.641 | 66.4 | 10 | 0 | 0 | 20 | 1810.4102
7962 | 2023-11-28 18:00 | 145.1677 | 66.4 | 0 | 0 | 10 | 10 | 0
7963 | 2023-11-28 19:00 | 116.9117 | 65.03 | 10 | 0 | 0 | 10 | 1819.4169
7964 | 2023-11-28 20:00 | 117.2574 | 65.03 | 0 | 0 | 10 | 0 | 0
7965 | 2023-11-28 21:00 | 97.7886 | 65.03 | 10 | 0 | 0 | 0 | 1628.1863
7966 | 2023-11-28 22:00 | 102.5667 | 65.03 | 10 | 0 | 0 | 0 | 1675.9666
7967 | 2023-11-28 23:00 | 104.0559 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1658.7994
7968 | 2023-11-29 00:00 | 93.4452 | 53.53 | 20 | 10 | 0 | 10 | 2939.5044
7969 | 2023-11-29 01:00 | 114.2059 | 53.53 | 0 | 0 | 10 | 0 | 0
7970 | 2023-11-29 02:00 | 79.4728 | 53.53 | 20 | 10 | 0 | 9.5 | 2660.0554
7971 | 2023-11-29 03:00 | 82.605 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1504.6502
7972 | 2023-11-29 04:00 | 76.9697 | 53.53 | 20 | 10 | 0 | 20 | 2609.9941
7973 | 2023-11-29 05:00 | 84.3607 | 53.53 | 10 | 0 | 0 | 20 | 1378.9067
7974 | 2023-11-29 06:00 | 94.0439 | 53.53 | 10 | 0 | 0 | 20 | 1475.7394
7975 | 2023-11-29 07:00 | 97.9328 | 53.53 | 10 | 0 | 0 | 20 | 1514.628
7976 | 2023-11-29 08:00 | 125.9033 | 65.03 | 0 | 0 | 10 | 10 | 0
7977 | 2023-11-29 09:00 | 104.7075 | 65.03 | 11.0526 | 1.0526 | 0 | 11 | 1876.0466
7978 | 2023-11-29 10:00 | 115.3391 | 65.03 | 0 | 0 | 10 | 1 | 0
7979 | 2023-11-29 11:00 | 112.8495 | 65.03 | 10 | 0 | 0 | 1 | 1778.7946
7980 | 2023-11-29 12:00 | 102.0416 | 65.03 | 20 | 10 | 0 | 10.5 | 3341.4321
7981 | 2023-11-29 13:00 | 110.5544 | 65.03 | 10 | 0 | 0 | 10.5 | 1755.8443
7982 | 2023-11-29 14:00 | 108.9536 | 65.03 | 10 | 0 | 0 | 10.5 | 1739.8361
7983 | 2023-11-29 15:00 | 103.2527 | 65.03 | 20 | 10 | 0 | 20 | 3365.6535
7984 | 2023-11-29 16:00 | 111.7328 | 65.03 | 10 | 0 | 0 | 20 | 1767.6281
7985 | 2023-11-29 17:00 | 125.0199 | 66.4 | 0 | 0 | 10 | 10 | 0
7986 | 2023-11-29 18:00 | 123.3598 | 66.4 | 0 | 0 | 10 | 0 | 0
7987 | 2023-11-29 19:00 | 123.3892 | 65.03 | 10 | 0 | 0 | 0 | 1884.1923
7988 | 2023-11-29 20:00 | 103.2323 | 65.03 | 10 | 0 | 0 | 0 | 1682.6226
7989 | 2023-11-29 21:00 | 101.2872 | 65.03 | 10.5263 | 0.52632 | 0 | 0.5 | 1750.7076
7990 | 2023-11-29 22:00 | 104.9694 | 65.03 | 10 | 0 | 0 | 0.5 | 1699.9937
7991 | 2023-11-29 23:00 | 94.5068 | 53.53 | 20 | 10 | 0 | 10 | 2960.7353
7992 | 2023-11-30 00:00 | 129.3725 | 53.53 | 0 | 0 | 10 | 0 | 0
7993 | 2023-11-30 01:00 | 90.2785 | 53.53 | 10 | 0 | 0 | 0 | 1438.0855
7994 | 2023-11-30 02:00 | 74.8759 | 53.53 | 20 | 10 | 0 | 9.5 | 2568.118
7995 | 2023-11-30 03:00 | 75.379 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1356.9365
7996 | 2023-11-30 04:00 | 100.008 | 53.53 | 0 | 0 | 10 | 0 | 0
7997 | 2023-11-30 05:00 | 70.7228 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1373.3204
7998 | 2023-11-30 06:00 | -34.8862 | 53.53 | 20 | 10 | 0 | 10.5 | 372.8768
7999 | 2023-11-30 07:00 | -29.9104 | 53.53 | 20 | 10 | 0 | 20 | 472.3922
8000 | 2023-11-30 08:00 | 111.5298 | 65.03 | 10 | 0 | 0 | 20 | 1765.5981
8001 | 2023-11-30 09:00 | 120.1244 | 65.03 | 0 | 0 | 10 | 10 | 0
8002 | 2023-11-30 10:00 | 119.9021 | 65.03 | 0 | 0 | 10 | 0 | 0
8003 | 2023-11-30 11:00 | 105.7349 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1887.4019
8004 | 2023-11-30 12:00 | 110.3966 | 65.03 | 10 | 0 | 0 | 1 | 1754.2662
8005 | 2023-11-30 13:00 | 98.1895 | 65.03 | 20 | 10 | 0 | 10.5 | 3264.3905
8006 | 2023-11-30 14:00 | 109.6527 | 65.03 | 10 | 0 | 0 | 10.5 | 1746.8266
8007 | 2023-11-30 15:00 | 103.5995 | 65.03 | 20 | 10 | 0 | 20 | 3372.5899
8008 | 2023-11-30 16:00 | 107.5388 | 65.03 | 10 | 0 | 0 | 20 | 1725.688
8009 | 2023-11-30 17:00 | 113.9767 | 66.4 | 0 | 0 | 10 | 10 | 0
8010 | 2023-11-30 18:00 | 127.127 | 66.4 | 0 | 0 | 10 | 0 | 0
8011 | 2023-11-30 19:00 | 113.9262 | 65.03 | 10 | 0 | 0 | 0 | 1789.5616
8012 | 2023-11-30 20:00 | 105.0355 | 65.03 | 10 | 0 | 0 | 0 | 1700.6555
8013 | 2023-11-30 21:00 | 96.2021 | 65.03 | 20 | 10 | 0 | 9.5 | 3224.6414
8014 | 2023-11-30 22:00 | 98.2733 | 65.03 | 10 | 0 | 0 | 9.5 | 1633.033
8015 | 2023-11-30 23:00 | 109.2482 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1713.4548
8016 | 2023-12-01 00:00 | 113.7205 | 53.53 | 10 | 0 | 0 | 10 | 1672.5045
8017 | 2023-12-01 01:00 | 119.1896 | 53.53 | 0 | 0 | 10 | 0 | 0
8018 | 2023-12-01 02:00 | 103.815 | 53.53 | 10 | 0 | 0 | 0 | 1573.4497
8019 | 2023-12-01 03:00 | 83.7249 | 53.53 | 20 | 10 | 0 | 9.5 | 2745.098
8020 | 2023-12-01 04:00 | 103.094 | 53.53 | 1.5 | 0 | 8.5 | 1 | 234.936
8021 | 2023-12-01 05:00 | 80.0048 | 53.53 | 20 | 10 | 0 | 10.5 | 2670.6965
8022 | 2023-12-01 06:00 | 95.1698 | 53.53 | 20 | 10 | 0 | 20 | 2973.9954
8023 | 2023-12-01 07:00 | 105.4591 | 53.53 | 10 | 0 | 0 | 20 | 1589.8906
8024 | 2023-12-01 08:00 | 112.8101 | 65.03 | 10 | 0 | 0 | 20 | 1778.401
8025 | 2023-12-01 09:00 | 123.9589 | 65.03 | 10 | 0 | 0 | 20 | 1889.8895
8026 | 2023-12-01 10:00 | 127.092 | 65.03 | 10 | 0 | 0 | 20 | 1921.2205
8027 | 2023-12-01 11:00 | 126.7978 | 65.03 | 10 | 0 | 0 | 20 | 1918.2777
8028 | 2023-12-01 12:00 | 120.5628 | 65.03 | 10 | 0 | 0 | 20 | 1855.9282
8029 | 2023-12-01 13:00 | 119.9078 | 65.03 | 10 | 0 | 0 | 20 | 1849.3784
8030 | 2023-12-01 14:00 | 123.1792 | 65.03 | 10 | 0 | 0 | 20 | 1882.0922
8031 | 2023-12-01 15:00 | 121.2836 | 65.03 | 10 | 0 | 0 | 20 | 1863.1357
8032 | 2023-12-01 16:00 | 123.3068 | 65.03 | 10 | 0 | 0 | 20 | 1883.3677
8033 | 2023-12-01 17:00 | 135.4761 | 66.4 | 0 | 0 | 10 | 10 | 0
8034 | 2023-12-01 18:00 | 141.0901 | 66.4 | 0 | 0 | 10 | 0 | 0
8035 | 2023-12-01 19:00 | 124.2421 | 65.03 | 10 | 0 | 0 | 0 | 1892.7214
8036 | 2023-12-01 20:00 | 112.9329 | 65.03 | 10 | 0 | 0 | 0 | 1779.6289
8037 | 2023-12-01 21:00 | 105.4043 | 65.03 | 20 | 10 | 0 | 9.5 | 3408.6854
8038 | 2023-12-01 22:00 | 116.0621 | 65.03 | 0.5 | 0 | 9.5 | 0 | 90.5461
8039 | 2023-12-01 23:00 | 124.8116 | 53.53 | 10 | 0 | 0 | 0 | 1783.4159
8040 | 2023-12-02 00:00 | 97.5839 | 53.53 | 10 | 0 | 0 | 0 | 1511.1395
8041 | 2023-12-02 01:00 | 101.8711 | 53.53 | 10 | 0 | 0 | 0 | 1554.0115
8042 | 2023-12-02 02:00 | 87.2674 | 53.53 | 10 | 0 | 0 | 0 | 1407.9736
8043 | 2023-12-02 03:00 | 69.3427 | 53.53 | 20 | 10 | 0 | 9.5 | 2457.4531
8044 | 2023-12-02 04:00 | 77.2737 | 53.53 | 1.5 | 0 | 8.5 | 1 | 196.2056
8045 | 2023-12-02 05:00 | -6.7564 | 53.53 | 20 | 10 | 0 | 10.5 | 935.4724
8046 | 2023-12-02 06:00 | -44.63 | 53.53 | 20 | 10 | 0 | 20 | 178.0003
8047 | 2023-12-02 07:00 | 94.5481 | 53.53 | 10 | 0 | 0 | 20 | 1480.7807
8048 | 2023-12-02 08:00 | 120.6815 | 53.53 | 0 | 0 | 10 | 10 | 0
8049 | 2023-12-02 09:00 | 119.6751 | 53.53 | 0 | 0 | 10 | 0 | 0
8050 | 2023-12-02 10:00 | 113.8694 | 53.53 | 10 | 0 | 0 | 0 | 1673.9939
8051 | 2023-12-02 11:00 | 118.473 | 53.53 | 10 | 0 | 0 | 0 | 1720.0298
8052 | 2023-12-02 12:00 | 112.5648 | 53.53 | 10 | 0 | 0 | 0 | 1660.9478
8053 | 2023-12-02 13:00 | 115.4309 | 53.53 | 10 | 0 | 0 | 0 | 1689.6089
8054 | 2023-12-02 14:00 | 108.6395 | 53.53 | 10 | 0 | 0 | 0 | 1621.6954
8055 | 2023-12-02 15:00 | -14.3896 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 432.6047
8056 | 2023-12-02 16:00 | -43.4607 | 53.53 | 20 | 10 | 0 | 10.5 | 201.3855
8057 | 2023-12-02 17:00 | -19.5047 | 53.53 | 20 | 10 | 0 | 20 | 680.5055
8058 | 2023-12-02 18:00 | 140.3605 | 53.53 | 0 | 0 | 10 | 10 | 0
8059 | 2023-12-02 19:00 | 138.7187 | 53.53 | 0 | 0 | 10 | 0 | 0
8060 | 2023-12-02 20:00 | 103.0174 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1647.8678
8061 | 2023-12-02 21:00 | 99.6774 | 53.53 | 20 | 10 | 0 | 10 | 3064.1478
8062 | 2023-12-02 22:00 | 117.5686 | 53.53 | 0 | 0 | 10 | 0 | 0
8063 | 2023-12-02 23:00 | 105.3293 | 53.53 | 10 | 0 | 0 | 0 | 1588.5929
8064 | 2023-12-03 00:00 | 103.4882 | 53.53 | 10 | 0 | 0 | 0 | 1570.1824
8065 | 2023-12-03 01:00 | 96.5704 | 53.53 | 10 | 0 | 0 | 0 | 1501.0043
8066 | 2023-12-03 02:00 | 84.3036 | 53.53 | 20 | 10 | 0 | 9.5 | 2756.6717
8067 | 2023-12-03 03:00 | 73.951 | 53.53 | 20 | 10 | 0 | 19 | 2549.6191
8068 | 2023-12-03 04:00 | 86.1362 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1543.6786
8069 | 2023-12-03 05:00 | 93.7071 | 53.53 | 10 | 0 | 0 | 20 | 1472.371
8070 | 2023-12-03 06:00 | 96.6782 | 53.53 | 10 | 0 | 0 | 20 | 1502.0821
8071 | 2023-12-03 07:00 | 106.8192 | 53.53 | 10 | 0 | 0 | 20 | 1603.4923
8072 | 2023-12-03 08:00 | 102.4133 | 53.53 | 10 | 0 | 0 | 20 | 1559.4331
8073 | 2023-12-03 09:00 | 112.423 | 53.53 | 10 | 0 | 0 | 20 | 1659.5297
8074 | 2023-12-03 10:00 | 133.4007 | 53.53 | 0 | 0 | 10 | 10 | 0
8075 | 2023-12-03 11:00 | 105.1634 | 53.53 | 20 | 10 | 0 | 19.5 | 3173.867
8076 | 2023-12-03 12:00 | 110.4584 | 53.53 | 10.5263 | 0.52632 | 0 | 20 | 1726.1933
8077 | 2023-12-03 13:00 | 124.102 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 88.816
8078 | 2023-12-03 14:00 | 115.983 | 53.53 | 10 | 0 | 0 | 10.5 | 1695.1298
8079 | 2023-12-03 15:00 | 138.5092 | 53.53 | 0 | 0 | 10 | 0.5 | 0
8080 | 2023-12-03 16:00 | 105.9641 | 53.53 | 20 | 10 | 0 | 10 | 3189.8814
8081 | 2023-12-03 17:00 | 119.4758 | 53.53 | 10 | 0 | 0 | 10 | 1730.0577
8082 | 2023-12-03 18:00 | 136.9918 | 53.53 | 0 | 0 | 10 | 0 | 0
8083 | 2023-12-03 19:00 | 118.3618 | 53.53 | 10 | 0 | 0 | 0 | 1718.9179
8084 | 2023-12-03 20:00 | 104.4653 | 53.53 | 20 | 10 | 0 | 9.5 | 3159.9052
8085 | 2023-12-03 21:00 | 105.4108 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1756.7138
8086 | 2023-12-03 22:00 | 115.0111 | 53.53 | 0 | 0 | 10 | 0.5 | 0
8087 | 2023-12-03 23:00 | 105.9571 | 53.53 | 10 | 0 | 0 | 0.5 | 1594.8713
8088 | 2023-12-04 00:00 | 112.5724 | 53.53 | 10 | 0 | 0 | 0.5 | 1661.0244
8089 | 2023-12-04 01:00 | 106.0552 | 53.53 | 10 | 0 | 0 | 0.5 | 1595.8515
8090 | 2023-12-04 02:00 | 99.8932 | 53.53 | 20 | 10 | 0 | 10 | 3068.464
8091 | 2023-12-04 03:00 | 147.5468 | 53.53 | 0 | 0 | 10 | 0 | 0
8092 | 2023-12-04 04:00 | 94.6597 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1637.8862
8093 | 2023-12-04 05:00 | 89.6571 | 53.53 | 20 | 10 | 0 | 10.5 | 2863.7427
8094 | 2023-12-04 06:00 | 80.8356 | 53.53 | 20 | 10 | 0 | 20 | 2687.3117
8095 | 2023-12-04 07:00 | 104.5466 | 53.53 | 10 | 0 | 0 | 20 | 1580.7657
8096 | 2023-12-04 08:00 | 117.3458 | 65.03 | 10 | 0 | 0 | 20 | 1823.7578
8097 | 2023-12-04 09:00 | 115.1938 | 65.03 | 10 | 0 | 0 | 20 | 1802.2381
8098 | 2023-12-04 10:00 | 118.778 | 65.03 | 10 | 0 | 0 | 20 | 1838.0801
8099 | 2023-12-04 11:00 | 136.5165 | 65.03 | 0 | 0 | 10 | 10 | 0
8100 | 2023-12-04 12:00 | 130.2422 | 65.03 | 1 | 0 | 9 | 1 | 195.2722
8101 | 2023-12-04 13:00 | 117.735 | 65.03 | 20 | 10 | 0 | 10.5 | 3655.2999
8102 | 2023-12-04 14:00 | 111.2969 | 65.03 | 20 | 10 | 0 | 20 | 3526.5389
8103 | 2023-12-04 15:00 | 131.2391 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 98.1345
8104 | 2023-12-04 16:00 | 118.5331 | 65.03 | 20 | 10 | 0 | 20 | 3671.2619
8105 | 2023-12-04 17:00 | 123.7918 | 66.4 | 10 | 0 | 0 | 20 | 1901.9182
8106 | 2023-12-04 18:00 | 139.8555 | 66.4 | 0 | 0 | 10 | 10 | 0
8107 | 2023-12-04 19:00 | 142.9058 | 65.03 | 0 | 0 | 10 | 0 | 0
8108 | 2023-12-04 20:00 | 100.9729 | 65.03 | 20 | 10 | 0 | 9.5 | 3320.0579
8109 | 2023-12-04 21:00 | 108.4197 | 65.03 | 10 | 0 | 0 | 9.5 | 1734.4967
8110 | 2023-12-04 22:00 | 113.0835 | 65.03 | 0.5 | 0 | 9.5 | 0 | 89.0567
8111 | 2023-12-04 23:00 | 115.0612 | 53.53 | 10 | 0 | 0 | 0 | 1685.9123
8112 | 2023-12-05 00:00 | 105.3146 | 53.53 | 10 | 0 | 0 | 0 | 1588.446
8113 | 2023-12-05 01:00 | 103.3753 | 53.53 | 10 | 0 | 0 | 0 | 1569.0529
8114 | 2023-12-05 02:00 | 94.9927 | 53.53 | 10 | 0 | 0 | 0 | 1485.2267
8115 | 2023-12-05 03:00 | 85.6215 | 53.53 | 20 | 10 | 0 | 9.5 | 2783.0294
8116 | 2023-12-05 04:00 | 93.3129 | 53.53 | 1.5 | 0 | 8.5 | 1 | 220.2644
8117 | 2023-12-05 05:00 | 81.8094 | 53.53 | 20 | 10 | 0 | 10.5 | 2706.7883
8118 | 2023-12-05 06:00 | 80.5611 | 53.53 | 20 | 10 | 0 | 20 | 2681.8212
8119 | 2023-12-05 07:00 | 115.2559 | 53.53 | 10 | 0 | 0 | 20 | 1687.859
8120 | 2023-12-05 08:00 | 120.8658 | 65.03 | 10 | 0 | 0 | 20 | 1858.9579
8121 | 2023-12-05 09:00 | 126.8688 | 65.03 | 0 | 0 | 10 | 10 | 0
8122 | 2023-12-05 10:00 | 115.2066 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1897.2277
8123 | 2023-12-05 11:00 | 113.5929 | 65.03 | 20 | 10 | 0 | 20 | 3572.458
8124 | 2023-12-05 12:00 | 131.5016 | 65.03 | 0 | 0 | 10 | 10 | 0
8125 | 2023-12-05 13:00 | 109.7296 | 65.03 | 20 | 10 | 0 | 19.5 | 3495.1919
8126 | 2023-12-05 14:00 | 130.289 | 65.03 | 10 | 0 | 0 | 19.5 | 1953.1903
8127 | 2023-12-05 15:00 | 131.0507 | 65.03 | 0.5 | 0 | 9.5 | 10 | 98.0403
8128 | 2023-12-05 16:00 | 126.2576 | 65.03 | 10 | 0 | 0 | 10 | 1912.8765
8129 | 2023-12-05 17:00 | 129.2372 | 66.4 | 10 | 0 | 0 | 10 | 1956.3717
8130 | 2023-12-05 18:00 | 128.4668 | 66.4 | 10 | 0 | 0 | 10 | 1948.6676
8131 | 2023-12-05 19:00 | 132.3715 | 65.03 | 0 | 0 | 10 | 0 | 0
8132 | 2023-12-05 20:00 | 105.8499 | 65.03 | 20 | 10 | 0 | 9.5 | 3417.5987
8133 | 2023-12-05 21:00 | 107.6328 | 65.03 | 10.5263 | 0.52632 | 0 | 10 | 1817.5034
8134 | 2023-12-05 22:00 | 119.2331 | 65.03 | 0 | 0 | 10 | 0 | 0
8135 | 2023-12-05 23:00 | 114.2751 | 53.53 | 10 | 0 | 0 | 0 | 1678.0515
8136 | 2023-12-06 00:00 | 102.1454 | 53.53 | 10 | 0 | 0 | 0 | 1556.7536
8137 | 2023-12-06 01:00 | -72.1805 | 53.53 | 20 | 10 | 0 | 9.5 | -373.0094
8138 | 2023-12-06 02:00 | 92.5487 | 53.53 | 20 | 10 | 0 | 19 | 2921.5738
8139 | 2023-12-06 03:00 | 103.2226 | 53.53 | 0 | 0 | 10 | 9 | 0
8140 | 2023-12-06 04:00 | 93.5529 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1703.0651
8141 | 2023-12-06 05:00 | 98.2431 | 53.53 | 10 | 0 | 0 | 10.5 | 1517.7309
8142 | 2023-12-06 06:00 | 92.7451 | 53.53 | 20 | 10 | 0 | 20 | 2925.5021
8143 | 2023-12-06 07:00 | 117.4422 | 53.53 | 10 | 0 | 0 | 20 | 1709.7219
8144 | 2023-12-06 08:00 | 110.8903 | 65.03 | 10 | 0 | 0 | 20 | 1759.2027
8145 | 2023-12-06 09:00 | 118.0017 | 65.03 | 10 | 0 | 0 | 20 | 1830.317
8146 | 2023-12-06 10:00 | 118.6076 | 65.03 | 10 | 0 | 0 | 20 | 1836.3764
8147 | 2023-12-06 11:00 | 117.1354 | 65.03 | 10 | 0 | 0 | 20 | 1821.6542
8148 | 2023-12-06 12:00 | 122.4593 | 65.03 | 10 | 0 | 0 | 20 | 1874.893
8149 | 2023-12-06 13:00 | 124.139 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 94.5845
8150 | 2023-12-06 14:00 | 122.0203 | 65.03 | 10 | 0 | 0 | 10.5 | 1870.5033
8151 | 2023-12-06 15:00 | 117.6058 | 65.03 | 10 | 0 | 0 | 10.5 | 1826.3583
8152 | 2023-12-06 16:00 | 113.9469 | 65.03 | 20 | 10 | 0 | 20 | 3579.5371
8153 | 2023-12-06 17:00 | 143.6432 | 66.4 | 0 | 0 | 10 | 10 | 0
8154 | 2023-12-06 18:00 | 136.6638 | 66.4 | 0 | 0 | 10 | 0 | 0
8155 | 2023-12-06 19:00 | 127.3156 | 65.03 | 10 | 0 | 0 | 0 | 1923.4563
8156 | 2023-12-06 20:00 | 112.487 | 65.03 | 10 | 0 | 0 | 0 | 1775.1705
8157 | 2023-12-06 21:00 | 103.7169 | 65.03 | 20 | 10 | 0 | 9.5 | 3374.9389
8158 | 2023-12-06 22:00 | 114.165 | 65.03 | 0.5 | 0 | 9.5 | 0 | 89.5975
8159 | 2023-12-06 23:00 | 107.4539 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1694.567
8160 | 2023-12-07 00:00 | 104.9406 | 53.53 | 20 | 10 | 0 | 10 | 3169.4126
8161 | 2023-12-07 01:00 | 124.1139 | 53.53 | 0 | 0 | 10 | 0 | 0
8162 | 2023-12-07 02:00 | 81.5712 | 53.53 | 20 | 10 | 0 | 9.5 | 2702.0231
8163 | 2023-12-07 03:00 | 94.7995 | 53.53 | 20 | 10 | 0 | 19 | 2966.5893
8164 | 2023-12-07 04:00 | 112.0756 | 53.53 | 0 | 0 | 10 | 9 | 0
8165 | 2023-12-07 05:00 | 98.4362 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1759.6083
8166 | 2023-12-07 06:00 | 88.6629 | 53.53 | 20 | 10 | 0 | 20 | 2843.8576
8167 | 2023-12-07 07:00 | 101.6886 | 53.53 | 10 | 0 | 0 | 20 | 1552.1864
8168 | 2023-12-07 08:00 | 110.5125 | 65.03 | 10 | 0 | 0 | 20 | 1755.425
8169 | 2023-12-07 09:00 | 115.9946 | 65.03 | 10 | 0 | 0 | 20 | 1810.2461
8170 | 2023-12-07 10:00 | 114.2421 | 65.03 | 10 | 0 | 0 | 20 | 1792.7209
8171 | 2023-12-07 11:00 | 114.0444 | 65.03 | 10 | 0 | 0 | 20 | 1790.7443
8172 | 2023-12-07 12:00 | 116.5669 | 65.03 | 10 | 0 | 0 | 20 | 1815.9693
8173 | 2023-12-07 13:00 | 118.1431 | 65.03 | 10 | 0 | 0 | 20 | 1831.7309
8174 | 2023-12-07 14:00 | 122.8156 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 93.9228
8175 | 2023-12-07 15:00 | 111.1436 | 65.03 | 20 | 10 | 0 | 20 | 3523.4712
8176 | 2023-12-07 16:00 | 114.2711 | 65.03 | 10 | 0 | 0 | 20 | 1793.0115
8177 | 2023-12-07 17:00 | 132.729 | 66.4 | 0 | 0 | 10 | 10 | 0
8178 | 2023-12-07 18:00 | 132.4743 | 66.4 | 10 | 0 | 0 | 10 | 1988.7433
8179 | 2023-12-07 19:00 | 152.2698 | 65.03 | 0 | 0 | 10 | 0 | 0
8180 | 2023-12-07 20:00 | 115.7023 | 65.03 | 10 | 0 | 0 | 0 | 1807.3227
8181 | 2023-12-07 21:00 | 104.305 | 65.03 | 20 | 10 | 0 | 9.5 | 3386.699
8182 | 2023-12-07 22:00 | 117.2399 | 65.03 | 0.5 | 0 | 9.5 | 0 | 91.1349
8183 | 2023-12-07 23:00 | 113.3448 | 53.53 | 10 | 0 | 0 | 0 | 1668.748
8184 | 2023-12-08 00:00 | 107.9772 | 53.53 | 10 | 0 | 0 | 0 | 1615.0724
8185 | 2023-12-08 01:00 | 101.2703 | 53.53 | 10 | 0 | 0 | 0 | 1548.0026
8186 | 2023-12-08 02:00 | 106.262 | 53.53 | 10 | 0 | 0 | 0 | 1597.9202
8187 | 2023-12-08 03:00 | 82.0345 | 53.53 | 20 | 10 | 0 | 9.5 | 2711.2904
8188 | 2023-12-08 04:00 | 94.3794 | 53.53 | 10 | 0 | 0 | 9.5 | 1479.0943
8189 | 2023-12-08 05:00 | 90.4446 | 53.53 | 20 | 10 | 0 | 19 | 2879.4924
8190 | 2023-12-08 06:00 | 93.836 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1628.7823
8191 | 2023-12-08 07:00 | 125.6163 | 53.53 | 10 | 0 | 0 | 20 | 1791.4633
8192 | 2023-12-08 08:00 | 123.4863 | 65.03 | 1 | 0 | 9 | 11 | 188.5163
8193 | 2023-12-08 09:00 | 115.0406 | 65.03 | 10 | 0 | 0 | 11 | 1800.7062
8194 | 2023-12-08 10:00 | 128.7351 | 65.03 | 0 | 0 | 10 | 1 | 0
8195 | 2023-12-08 11:00 | 114.5861 | 65.03 | 10 | 0 | 0 | 1 | 1796.1614
8196 | 2023-12-08 12:00 | 120.1556 | 65.03 | 10 | 0 | 0 | 1 | 1851.8558
8197 | 2023-12-08 13:00 | 110.8599 | 65.03 | 20 | 10 | 0 | 10.5 | 3517.7977
8198 | 2023-12-08 14:00 | 112.2348 | 65.03 | 20 | 10 | 0 | 20 | 3545.2953
8199 | 2023-12-08 15:00 | 119.2867 | 65.03 | 10 | 0 | 0 | 20 | 1843.1669
8200 | 2023-12-08 16:00 | 121.8171 | 65.03 | 10 | 0 | 0 | 20 | 1868.4715
8201 | 2023-12-08 17:00 | 123.8999 | 66.4 | 10 | 0 | 0 | 20 | 1902.9993
8202 | 2023-12-08 18:00 | 137.9205 | 66.4 | 0 | 0 | 10 | 10 | 0
8203 | 2023-12-08 19:00 | 128.4497 | 65.03 | 0 | 0 | 10 | 0 | 0
8204 | 2023-12-08 20:00 | 125.5985 | 65.03 | 10 | 0 | 0 | 0 | 1906.2851
8205 | 2023-12-08 21:00 | 111.3932 | 65.03 | 10 | 0 | 0 | 0 | 1764.2316
8206 | 2023-12-08 22:00 | 106.7445 | 65.03 | 10 | 0 | 0 | 0 | 1717.7448
8207 | 2023-12-08 23:00 | 109.4734 | 53.53 | 10 | 0 | 0 | 0 | 1630.0335
8208 | 2023-12-09 00:00 | 94.8901 | 53.53 | 10 | 0 | 0 | 0 | 1484.2007
8209 | 2023-12-09 01:00 | -6.4171 | 53.53 | 20 | 10 | 0 | 9.5 | 942.259
8210 | 2023-12-09 02:00 | 80.9023 | 53.53 | 10 | 0 | 0 | 9.5 | 1344.3228
8211 | 2023-12-09 03:00 | 79.7862 | 53.53 | 10 | 0 | 0 | 9.5 | 1333.1622
8212 | 2023-12-09 04:00 | 85.7552 | 53.53 | 1.5 | 0 | 8.5 | 1 | 208.9278
8213 | 2023-12-09 05:00 | 74.3913 | 53.53 | 20 | 10 | 0 | 10.5 | 2558.4259
8214 | 2023-12-09 06:00 | 72.8799 | 53.53 | 20 | 10 | 0 | 20 | 2528.1979
8215 | 2023-12-09 07:00 | 104.1564 | 53.53 | 10 | 0 | 0 | 20 | 1576.8644
8216 | 2023-12-09 08:00 | 103.8732 | 53.53 | 10 | 0 | 0 | 20 | 1574.0317
8217 | 2023-12-09 09:00 | 103.8713 | 53.53 | 10 | 0 | 0 | 20 | 1574.0134
8218 | 2023-12-09 10:00 | 118.0319 | 53.53 | 0 | 0 | 10 | 10 | 0
8219 | 2023-12-09 11:00 | 115.1634 | 53.53 | 0 | 0 | 10 | 0 | 0
8220 | 2023-12-09 12:00 | 103.0608 | 53.53 | 20 | 10 | 0 | 9.5 | 3131.8162
8221 | 2023-12-09 13:00 | 106.6605 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1770.5269
8222 | 2023-12-09 14:00 | 104.9614 | 53.53 | 20 | 10 | 0 | 20 | 3169.8288
8223 | 2023-12-09 15:00 | 128.4948 | 53.53 | 0 | 0 | 10 | 10 | 0
8224 | 2023-12-09 16:00 | 118.7065 | 53.53 | 10 | 0 | 0 | 10 | 1722.3652
8225 | 2023-12-09 17:00 | 122.9331 | 53.53 | 10 | 0 | 0 | 10 | 1764.6309
8226 | 2023-12-09 18:00 | 130.6158 | 53.53 | 0 | 0 | 10 | 0 | 0
8227 | 2023-12-09 19:00 | 117.5418 | 53.53 | 10 | 0 | 0 | 0 | 1710.7181
8228 | 2023-12-09 20:00 | 101.3299 | 53.53 | 20 | 10 | 0 | 9.5 | 3097.1978
8229 | 2023-12-09 21:00 | 106.6973 | 53.53 | 10 | 0 | 0 | 9.5 | 1602.2728
8230 | 2023-12-09 22:00 | 109.5309 | 53.53 | 0.5 | 0 | 9.5 | 0 | 81.5304
8231 | 2023-12-09 23:00 | 100.1779 | 53.53 | 10 | 0 | 0 | 0 | 1537.0794
8232 | 2023-12-10 00:00 | 102.8294 | 53.53 | 10 | 0 | 0 | 0 | 1563.5936
8233 | 2023-12-10 01:00 | 101.4928 | 53.53 | 10 | 0 | 0 | 0 | 1550.2279
8234 | 2023-12-10 02:00 | 79.7011 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1472.5542
8235 | 2023-12-10 03:00 | 78.773 | 53.53 | 20 | 10 | 0 | 10.5 | 2646.0604
8236 | 2023-12-10 04:00 | 77.8973 | 53.53 | 20 | 10 | 0 | 20 | 2628.5458
8237 | 2023-12-10 05:00 | 82.6998 | 53.53 | 10 | 0 | 0 | 20 | 1362.2979
8238 | 2023-12-10 06:00 | 84.1773 | 53.53 | 10 | 0 | 0 | 20 | 1377.0733
8239 | 2023-12-10 07:00 | 102.4312 | 53.53 | 10 | 0 | 0 | 20 | 1559.6116
8240 | 2023-12-10 08:00 | 103.4526 | 53.53 | 10 | 0 | 0 | 20 | 1569.8257
8241 | 2023-12-10 09:00 | 104.4247 | 53.53 | 10 | 0 | 0 | 20 | 1579.5472
8242 | 2023-12-10 10:00 | 114.0763 | 53.53 | 10 | 0 | 0 | 20 | 1676.0627
8243 | 2023-12-10 11:00 | 124.7743 | 53.53 | 0 | 0 | 10 | 10 | 0
8244 | 2023-12-10 12:00 | 112.068 | 53.53 | 10 | 0 | 0 | 10 | 1655.9796
8245 | 2023-12-10 13:00 | 107.9938 | 53.53 | 10.5263 | 0.52632 | 0 | 10.5 | 1700.2509
8246 | 2023-12-10 14:00 | 112.6388 | 53.53 | 10 | 0 | 0 | 10.5 | 1661.6877
8247 | 2023-12-10 15:00 | 103.674 | 53.53 | 20 | 10 | 0 | 20 | 3144.0791
8248 | 2023-12-10 16:00 | 122.922 | 53.53 | 10 | 0 | 0 | 20 | 1764.5203
8249 | 2023-12-10 17:00 | 127.3377 | 53.53 | 0 | 0 | 10 | 10 | 0
8250 | 2023-12-10 18:00 | 121.3494 | 53.53 | 10 | 0 | 0 | 10 | 1748.7945
8251 | 2023-12-10 19:00 | 124.6781 | 53.53 | 0 | 0 | 10 | 0 | 0
8252 | 2023-12-10 20:00 | 102.2422 | 53.53 | 20 | 10 | 0 | 9.5 | 3115.4437
8253 | 2023-12-10 21:00 | 117.9523 | 53.53 | 0.5 | 0 | 9.5 | 0 | 85.7412
8254 | 2023-12-10 22:00 | 104.4266 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1662.7011
8255 | 2023-12-10 23:00 | 102.0911 | 53.53 | 20 | 10 | 0 | 10 | 3112.4226
8256 | 2023-12-11 00:00 | 113.5938 | 53.53 | 0 | 0 | 10 | 0 | 0
8257 | 2023-12-11 01:00 | 103.9166 | 53.53 | 10 | 0 | 0 | 0 | 1574.4659
8258 | 2023-12-11 02:00 | 90.3942 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1590.7408
8259 | 2023-12-11 03:00 | 91.0437 | 53.53 | 10 | 0 | 0 | 1 | 1445.7368
8260 | 2023-12-11 04:00 | 79.5825 | 53.53 | 20 | 10 | 0 | 10.5 | 2662.2496
8261 | 2023-12-11 05:00 | 90.8672 | 53.53 | 10 | 0 | 0 | 10.5 | 1443.9722
8262 | 2023-12-11 06:00 | 88.5574 | 53.53 | 20 | 10 | 0 | 20 | 2841.7487
8263 | 2023-12-11 07:00 | 109.8923 | 53.53 | 10 | 0 | 0 | 20 | 1634.2231
8264 | 2023-12-11 08:00 | 119.167 | 65.03 | 10 | 0 | 0 | 20 | 1841.9696
8265 | 2023-12-11 09:00 | 120.9196 | 65.03 | 0 | 0 | 10 | 10 | 0
8266 | 2023-12-11 10:00 | 131.2388 | 65.03 | 0 | 0 | 10 | 0 | 0
8267 | 2023-12-11 11:00 | 111.4478 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 1950.5438
8268 | 2023-12-11 12:00 | 116.4595 | 65.03 | 10 | 0 | 0 | 1 | 1814.8947
8269 | 2023-12-11 13:00 | -38.8395 | 65.03 | 20 | 10 | 0 | 10.5 | 523.8096
8270 | 2023-12-11 14:00 | -59.1187 | 65.03 | 20 | 10 | 0 | 20 | 118.2256
8271 | 2023-12-11 15:00 | 122.5926 | 65.03 | 10 | 0 | 0 | 20 | 1876.2258
8272 | 2023-12-11 16:00 | 151.0066 | 65.03 | 0 | 0 | 10 | 10 | 0
8273 | 2023-12-11 17:00 | 138.9559 | 66.4 | 10 | 0 | 0 | 10 | 2053.5593
8274 | 2023-12-11 18:00 | 143.9968 | 66.4 | 0 | 0 | 10 | 0 | 0
8275 | 2023-12-11 19:00 | 131.6982 | 65.03 | 10 | 0 | 0 | 0 | 1967.2816
8276 | 2023-12-11 20:00 | 107.4582 | 65.03 | 20 | 10 | 0 | 9.5 | 3449.7637
8277 | 2023-12-11 21:00 | 111.6487 | 65.03 | 10 | 0 | 0 | 9.5 | 1766.7866
8278 | 2023-12-11 22:00 | 119.8511 | 65.03 | 0.5 | 0 | 9.5 | 0 | 92.4406
8279 | 2023-12-11 23:00 | 112.1435 | 53.53 | 10 | 0 | 0 | 0 | 1656.7352
8280 | 2023-12-12 00:00 | 112.1132 | 53.53 | 10 | 0 | 0 | 0 | 1656.4324
8281 | 2023-12-12 01:00 | 107.3413 | 53.53 | 10 | 0 | 0 | 0 | 1608.7132
8282 | 2023-12-12 02:00 | 86.2463 | 53.53 | 20 | 10 | 0 | 9.5 | 2795.5253
8283 | 2023-12-12 03:00 | 87.5851 | 53.53 | 20 | 10 | 0 | 19 | 2822.3025
8284 | 2023-12-12 04:00 | 94.9676 | 53.53 | 10 | 0 | 0 | 19 | 1484.9755
8285 | 2023-12-12 05:00 | 96.0702 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 224.4003
8286 | 2023-12-12 06:00 | 82.3841 | 53.53 | 20 | 10 | 0 | 20 | 2718.2823
8287 | 2023-12-12 07:00 | 115.3225 | 53.53 | 10 | 0 | 0 | 20 | 1688.5252
8288 | 2023-12-12 08:00 | 114.4647 | 65.03 | 10 | 0 | 0 | 20 | 1794.9472
8289 | 2023-12-12 09:00 | 122.6746 | 65.03 | 10 | 0 | 0 | 20 | 1877.0461
8290 | 2023-12-12 10:00 | 117.4992 | 65.03 | 10 | 0 | 0 | 20 | 1825.2924
8291 | 2023-12-12 11:00 | 133.8876 | 65.03 | 0 | 0 | 10 | 10 | 0
8292 | 2023-12-12 12:00 | 115.9514 | 65.03 | 10 | 0 | 0 | 10 | 1809.8141
8293 | 2023-12-12 13:00 | 120.2744 | 65.03 | 10 | 0 | 0 | 10 | 1853.0443
8294 | 2023-12-12 14:00 | 123.888 | 65.03 | 1 | 0 | 9 | 1 | 188.918
8295 | 2023-12-12 15:00 | 113.1325 | 65.03 | 20 | 10 | 0 | 10.5 | 3563.2494
8296 | 2023-12-12 16:00 | -10.9973 | 65.03 | 20 | 10 | 0 | 20 | 1080.6539
8297 | 2023-12-12 17:00 | 131.9768 | 66.4 | 0 | 0 | 10 | 10 | 0
8298 | 2023-12-12 18:00 | 130.327 | 66.4 | 0 | 0 | 10 | 0 | 0
8299 | 2023-12-12 19:00 | 130.8087 | 65.03 | 10 | 0 | 0 | 0 | 1958.3865
8300 | 2023-12-12 20:00 | -22.9744 | 65.03 | 20 | 10 | 0 | 9.5 | 841.1122
8301 | 2023-12-12 21:00 | -29.557 | 65.03 | 20 | 10 | 0 | 19 | 709.4591
8302 | 2023-12-12 22:00 | 118.5286 | 65.03 | 0 | 0 | 10 | 9 | 0
8303 | 2023-12-12 23:00 | 111.3727 | 53.53 | 1.5 | 0 | 8.5 | 0.5 | 247.354
8304 | 2023-12-13 00:00 | 100.3394 | 53.53 | 20 | 10 | 0 | 10 | 3077.3873
8305 | 2023-12-13 01:00 | 113.1117 | 53.53 | 0 | 0 | 10 | 0 | 0
8306 | 2023-12-13 02:00 | 80.258 | 53.53 | 20 | 10 | 0 | 9.5 | 2675.7604
8307 | 2023-12-13 03:00 | 94.082 | 53.53 | 0.5 | 0 | 9.5 | 0 | 73.806
8308 | 2023-12-13 04:00 | 85.3696 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1535.2065
8309 | 2023-12-13 05:00 | -31.4325 | 53.53 | 20 | 10 | 0 | 10.5 | 441.95
8310 | 2023-12-13 06:00 | -52.4332 | 53.53 | 20 | 10 | 0 | 20 | 21.936
8311 | 2023-12-13 07:00 | 109.8332 | 53.53 | 10 | 0 | 0 | 20 | 1633.6323
8312 | 2023-12-13 08:00 | 126.9133 | 65.03 | 0 | 0 | 10 | 10 | 0
8313 | 2023-12-13 09:00 | -55.4996 | 65.03 | 20 | 10 | 0 | 19.5 | 190.6086
8314 | 2023-12-13 10:00 | 114.7352 | 65.03 | 10 | 0 | 0 | 19.5 | 1797.6521
8315 | 2023-12-13 11:00 | 122.5514 | 65.03 | 10 | 0 | 0 | 19.5 | 1875.8142
8316 | 2023-12-13 12:00 | 122.7671 | 65.03 | 1 | 0 | 9 | 10.5 | 187.7971
8317 | 2023-12-13 13:00 | 105.943 | 65.03 | 20 | 10 | 0 | 20 | 3419.4595
8318 | 2023-12-13 14:00 | 139.6623 | 65.03 | 0 | 0 | 10 | 10 | 0
8319 | 2023-12-13 15:00 | 123.194 | 65.03 | 20 | 10 | 0 | 19.5 | 3764.4808
8320 | 2023-12-13 16:00 | 124.7118 | 65.03 | 10 | 0 | 0 | 19.5 | 1897.4176
8321 | 2023-12-13 17:00 | 132.8446 | 66.4 | 0.5 | 0 | 9.5 | 10 | 99.6223
8322 | 2023-12-13 18:00 | 123.2271 | 66.4 | 10 | 0 | 0 | 10 | 1896.2708
8323 | 2023-12-13 19:00 | 139.5073 | 65.03 | 0 | 0 | 10 | 0 | 0
8324 | 2023-12-13 20:00 | -77.9727 | 65.03 | 20 | 10 | 0 | 9.5 | -258.855
8325 | 2023-12-13 21:00 | -48.6222 | 65.03 | 20 | 10 | 0 | 19 | 328.1551
8326 | 2023-12-13 22:00 | 112.31 | 65.03 | 0 | 0 | 10 | 9 | 0
8327 | 2023-12-13 23:00 | 110.7489 | 53.53 | 2 | 0 | 8 | 1 | 328.5578
8328 | 2023-12-14 00:00 | 103.7121 | 53.53 | 10 | 0 | 0 | 1 | 1572.4207
8329 | 2023-12-14 01:00 | -59.2448 | 53.53 | 20 | 10 | 0 | 10.5 | -114.2956
8330 | 2023-12-14 02:00 | -38.3073 | 53.53 | 20 | 10 | 0 | 20 | 304.4536
8331 | 2023-12-14 03:00 | 112.9339 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 83.232
8332 | 2023-12-14 04:00 | 112.8219 | 53.53 | 10 | 0 | 0 | 10.5 | 1663.5193
8333 | 2023-12-14 05:00 | 104.6985 | 53.53 | 10 | 0 | 0 | 10.5 | 1582.2845
8334 | 2023-12-14 06:00 | 100.5522 | 53.53 | 20 | 10 | 0 | 20 | 3081.6439
8335 | 2023-12-14 07:00 | 108.2722 | 53.53 | 10 | 0 | 0 | 20 | 1618.0217
8336 | 2023-12-14 08:00 | 129.3737 | 65.03 | 0 | 0 | 10 | 10 | 0
8337 | 2023-12-14 09:00 | 118.1873 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1928.603
8338 | 2023-12-14 10:00 | 109.5851 | 65.03 | 20 | 10 | 0 | 20 | 3492.3024
8339 | 2023-12-14 11:00 | 133.1438 | 65.03 | 0 | 0 | 10 | 10 | 0
8340 | 2023-12-14 12:00 | 128.9745 | 65.03 | 0 | 0 | 10 | 0 | 0
8341 | 2023-12-14 13:00 | 118.6644 | 65.03 | 10 | 0 | 0 | 0 | 1836.9436
8342 | 2023-12-14 14:00 | 111.2089 | 65.03 | 20 | 10 | 0 | 9.5 | 3524.7786
8343 | 2023-12-14 15:00 | 114.8667 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 1988.3318
8344 | 2023-12-14 16:00 | 108.3749 | 65.03 | 20 | 10 | 0 | 20 | 3468.0977
8345 | 2023-12-14 17:00 | 142.0933 | 66.4 | 0 | 0 | 10 | 10 | 0
8346 | 2023-12-14 18:00 | 124.3525 | 66.4 | 10 | 0 | 0 | 10 | 1907.5254
8347 | 2023-12-14 19:00 | 136.1448 | 65.03 | 0 | 0 | 10 | 0 | 0
8348 | 2023-12-14 20:00 | 108.3079 | 65.03 | 10 | 0 | 0 | 0 | 1733.3791
8349 | 2023-12-14 21:00 | 105.1934 | 65.03 | 20 | 10 | 0 | 9.5 | 3404.4682
8350 | 2023-12-14 22:00 | 115.7514 | 65.03 | 0.5 | 0 | 9.5 | 0 | 90.3907
8351 | 2023-12-14 23:00 | 106.5161 | 53.53 | 20 | 10 | 0 | 9.5 | 3200.9216
8352 | 2023-12-15 00:00 | 116.0457 | 53.53 | 0.5 | 0 | 9.5 | 0 | 84.7879
8353 | 2023-12-15 01:00 | 100.99 | 53.53 | 10 | 0 | 0 | 0 | 1545.2003
8354 | 2023-12-15 02:00 | 83.8175 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1518.0508
8355 | 2023-12-15 03:00 | 76.1123 | 53.53 | 20 | 10 | 0 | 10.5 | 2592.8462
8356 | 2023-12-15 04:00 | 76.8804 | 53.53 | 20 | 10 | 0 | 20 | 2608.2082
8357 | 2023-12-15 05:00 | 106.7752 | 53.53 | 10 | 0 | 0 | 20 | 1603.0522
8358 | 2023-12-15 06:00 | 110.6082 | 53.53 | 10 | 0 | 0 | 20 | 1641.3817
8359 | 2023-12-15 07:00 | 109.6035 | 53.53 | 10 | 0 | 0 | 20 | 1631.3352
8360 | 2023-12-15 08:00 | 113.4239 | 65.03 | 10 | 0 | 0 | 20 | 1784.5392
8361 | 2023-12-15 09:00 | 116.7572 | 65.03 | 10 | 0 | 0 | 20 | 1817.8722
8362 | 2023-12-15 10:00 | 126.3888 | 65.03 | 0 | 0 | 10 | 10 | 0
8363 | 2023-12-15 11:00 | 115.3233 | 65.03 | 10 | 0 | 0 | 10 | 1803.5332
8364 | 2023-12-15 12:00 | 120.7456 | 65.03 | 10 | 0 | 0 | 10 | 1857.7563
8365 | 2023-12-15 13:00 | 118.8028 | 65.03 | 10 | 0 | 0 | 10 | 1838.3282
8366 | 2023-12-15 14:00 | 114.9764 | 65.03 | 20 | 10 | 0 | 19.5 | 3600.127
8367 | 2023-12-15 15:00 | 115.2476 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1897.6588
8368 | 2023-12-15 16:00 | 121.1979 | 65.03 | 10 | 0 | 0 | 20 | 1862.2791
8369 | 2023-12-15 17:00 | 127.5476 | 66.4 | 10 | 0 | 0 | 20 | 1939.4762
8370 | 2023-12-15 18:00 | 137.5266 | 66.4 | 0 | 0 | 10 | 10 | 0
8371 | 2023-12-15 19:00 | 130.6003 | 65.03 | 0 | 0 | 10 | 0 | 0
8372 | 2023-12-15 20:00 | 114.872 | 65.03 | 20 | 10 | 0 | 9.5 | 3598.0409
8373 | 2023-12-15 21:00 | 126.7647 | 65.03 | 0.5 | 0 | 9.5 | 0 | 95.8974
8374 | 2023-12-15 22:00 | -28.5635 | 65.03 | 20 | 10 | 0 | 9.5 | 729.3305
8375 | 2023-12-15 23:00 | -27.8265 | 53.53 | 20 | 10 | 0 | 19 | 514.0702
8376 | 2023-12-16 00:00 | 90.5019 | 53.53 | 1 | 0 | 9 | 10 | 144.0319
8377 | 2023-12-16 01:00 | 97.6082 | 53.53 | 0 | 0 | 10 | 0 | 0
8378 | 2023-12-16 02:00 | 81.1068 | 53.53 | 10 | 0 | 0 | 0 | 1346.3684
8379 | 2023-12-16 03:00 | -15.2664 | 53.53 | 20 | 10 | 0 | 9.5 | 765.2724
8380 | 2023-12-16 04:00 | 69.7844 | 53.53 | 20 | 10 | 0 | 19 | 2466.2886
8381 | 2023-12-16 05:00 | 80.187 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1477.9252
8382 | 2023-12-16 06:00 | 94.6 | 53.53 | 10 | 0 | 0 | 20 | 1481.2997
8383 | 2023-12-16 07:00 | 95.6526 | 53.53 | 10 | 0 | 0 | 20 | 1491.8258
8384 | 2023-12-16 08:00 | 109.3519 | 53.53 | 10 | 0 | 0 | 20 | 1628.8191
8385 | 2023-12-16 09:00 | 113.5144 | 53.53 | 10 | 0 | 0 | 20 | 1670.4437
8386 | 2023-12-16 10:00 | 112.3211 | 53.53 | 10 | 0 | 0 | 20 | 1658.5114
8387 | 2023-12-16 11:00 | 125.8874 | 53.53 | 0 | 0 | 10 | 10 | 0
8388 | 2023-12-16 12:00 | 114.4986 | 53.53 | 10 | 0 | 0 | 10 | 1680.2863
8389 | 2023-12-16 13:00 | 123.1318 | 53.53 | 0 | 0 | 10 | 0 | 0
8390 | 2023-12-16 14:00 | 108.3389 | 53.53 | 20 | 10 | 0 | 9.5 | 3237.3788
8391 | 2023-12-16 15:00 | 105.918 | 53.53 | 20 | 10 | 0 | 19 | 3188.9607
8392 | 2023-12-16 16:00 | 109.2614 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1799.2737
8393 | 2023-12-16 17:00 | 118.5555 | 53.53 | 10 | 0 | 0 | 20 | 1720.8553
8394 | 2023-12-16 18:00 | 129.8008 | 53.53 | 0 | 0 | 10 | 10 | 0
8395 | 2023-12-16 19:00 | 123.1655 | 53.53 | 0 | 0 | 10 | 0 | 0
8396 | 2023-12-16 20:00 | 101.3351 | 53.53 | 20 | 10 | 0 | 9.5 | 3097.3029
8397 | 2023-12-16 21:00 | 109.9325 | 53.53 | 0.5 | 0 | 9.5 | 0 | 81.7312
8398 | 2023-12-16 22:00 | 98.6372 | 53.53 | 20 | 10 | 0 | 9.5 | 3043.3445
8399 | 2023-12-16 23:00 | 107.3995 | 53.53 | 1 | 0 | 9 | 0.5 | 160.9295
8400 | 2023-12-17 00:00 | 97.5563 | 53.53 | 20 | 10 | 0 | 10 | 3021.726
8401 | 2023-12-17 01:00 | 111.2945 | 53.53 | 0 | 0 | 10 | 0 | 0
8402 | 2023-12-17 02:00 | 78.1197 | 53.53 | 20 | 10 | 0 | 9.5 | 2632.9936
8403 | 2023-12-17 03:00 | 86.1166 | 53.53 | 10 | 0 | 0 | 9.5 | 1396.4664
8404 | 2023-12-17 04:00 | 82.282 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1501.0795
8405 | 2023-12-17 05:00 | 87.1492 | 53.53 | 10 | 0 | 0 | 10.5 | 1406.7915
8406 | 2023-12-17 06:00 | 81.7367 | 53.53 | 20 | 10 | 0 | 20 | 2705.3332
8407 | 2023-12-17 07:00 | 91.0765 | 53.53 | 10 | 0 | 0 | 20 | 1446.0645
8408 | 2023-12-17 08:00 | 119.7339 | 53.53 | 0 | 0 | 10 | 10 | 0
8409 | 2023-12-17 09:00 | 110.2493 | 53.53 | 10 | 0 | 0 | 10 | 1637.7926
8410 | 2023-12-17 10:00 | 117.5797 | 53.53 | 0 | 0 | 10 | 0 | 0
8411 | 2023-12-17 11:00 | 116.6501 | 53.53 | 10 | 0 | 0 | 0 | 1701.8014
8412 | 2023-12-17 12:00 | 105.7222 | 53.53 | 20 | 10 | 0 | 9.5 | 3185.0436
8413 | 2023-12-17 13:00 | 104.8983 | 53.53 | 20 | 10 | 0 | 19 | 3168.5654
8414 | 2023-12-17 14:00 | 116.3299 | 53.53 | 10 | 0 | 0 | 19 | 1698.5993
8415 | 2023-12-17 15:00 | 108.7243 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1793.3373
8416 | 2023-12-17 16:00 | 119.0073 | 53.53 | 10 | 0 | 0 | 20 | 1725.3729
8417 | 2023-12-17 17:00 | 124.5969 | 53.53 | 10 | 0 | 0 | 20 | 1781.269
8418 | 2023-12-17 18:00 | 134.8826 | 53.53 | 0 | 0 | 10 | 10 | 0
8419 | 2023-12-17 19:00 | 129.2835 | 53.53 | 0 | 0 | 10 | 0 | 0
8420 | 2023-12-17 20:00 | 108.1542 | 53.53 | 10 | 0 | 0 | 0 | 1616.8416
8421 | 2023-12-17 21:00 | 103.2449 | 53.53 | 20 | 10 | 0 | 9.5 | 3135.4974
8422 | 2023-12-17 22:00 | 107.7037 | 53.53 | 10 | 0 | 0 | 9.5 | 1612.3373
8423 | 2023-12-17 23:00 | 111.6548 | 53.53 | 10 | 0 | 0 | 9.5 | 1651.8479
8424 | 2023-12-18 00:00 | 108.495 | 53.53 | 10 | 0 | 0 | 9.5 | 1620.2498
8425 | 2023-12-18 01:00 | 113.2171 | 53.53 | 0.5 | 0 | 9.5 | 0 | 83.3735
8426 | 2023-12-18 02:00 | -79.824 | 53.53 | 20 | 10 | 0 | 9.5 | -525.8801
8427 | 2023-12-18 03:00 | 89.8505 | 53.53 | 20 | 10 | 0 | 19 | 2867.6105
8428 | 2023-12-18 04:00 | 105.824 | 53.53 | 1.5 | 0 | 8.5 | 10.5 | 239.031
8429 | 2023-12-18 05:00 | 99.7501 | 53.53 | 10 | 0 | 0 | 10.5 | 1532.8014
8430 | 2023-12-18 06:00 | 89.501 | 53.53 | 20 | 10 | 0 | 20 | 2860.6197
8431 | 2023-12-18 07:00 | 110.5596 | 53.53 | 10 | 0 | 0 | 20 | 1640.8958
8432 | 2023-12-18 08:00 | 114.1515 | 65.03 | 10 | 0 | 0 | 20 | 1791.8154
8433 | 2023-12-18 09:00 | 117.6341 | 65.03 | 10 | 0 | 0 | 20 | 1826.641
8434 | 2023-12-18 10:00 | 121.3299 | 65.03 | 10 | 0 | 0 | 20 | 1863.5989
8435 | 2023-12-18 11:00 | 126.1658 | 65.03 | 0 | 0 | 10 | 10 | 0
8436 | 2023-12-18 12:00 | 125.1991 | 65.03 | 1 | 0 | 9 | 1 | 190.2291
8437 | 2023-12-18 13:00 | 111.8215 | 65.03 | 20 | 10 | 0 | 10.5 | 3537.0309
8438 | 2023-12-18 14:00 | 127.4126 | 65.03 | 0 | 0 | 10 | 0.5 | 0
8439 | 2023-12-18 15:00 | 118.2413 | 65.03 | 10 | 0 | 0 | 0.5 | 1832.7129
8440 | 2023-12-18 16:00 | 112.4912 | 65.03 | 20 | 10 | 0 | 10 | 3550.4236
8441 | 2023-12-18 17:00 | 146.2281 | 66.4 | 0 | 0 | 10 | 0 | 0
8442 | 2023-12-18 18:00 | -64.402 | 66.4 | 20 | 10 | 0 | 9.5 | 39.9607
8443 | 2023-12-18 19:00 | -9.1104 | 65.03 | 20 | 10 | 0 | 19 | 1118.3929
8444 | 2023-12-18 20:00 | 119.8217 | 65.03 | 10 | 0 | 0 | 19 | 1848.5173
8445 | 2023-12-18 21:00 | 120.3707 | 65.03 | 1 | 0 | 9 | 10 | 185.4007
8446 | 2023-12-18 22:00 | 126.8991 | 65.03 | 0 | 0 | 10 | 0 | 0
8447 | 2023-12-18 23:00 | 115.0011 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1774.0112
8448 | 2023-12-19 00:00 | 100.6847 | 53.53 | 20 | 10 | 0 | 10 | 3084.2942
8449 | 2023-12-19 01:00 | 129.5855 | 53.53 | 0 | 0 | 10 | 0 | 0
8450 | 2023-12-19 02:00 | 98.3161 | 53.53 | 10 | 0 | 0 | 0 | 1518.4607
8451 | 2023-12-19 03:00 | 85.3546 | 53.53 | 10 | 0 | 0 | 0 | 1388.8461
8452 | 2023-12-19 04:00 | 82.2549 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1500.7804
8453 | 2023-12-19 05:00 | -29.5199 | 53.53 | 20 | 10 | 0 | 10.5 | 480.2016
8454 | 2023-12-19 06:00 | -59.8242 | 53.53 | 20 | 10 | 0 | 20 | -125.8833
8455 | 2023-12-19 07:00 | 111.4999 | 53.53 | 10 | 0 | 0 | 20 | 1650.2993
8456 | 2023-12-19 08:00 | 125.1445 | 65.03 | 0 | 0 | 10 | 10 | 0
8457 | 2023-12-19 09:00 | 114.9913 | 65.03 | 10 | 0 | 0 | 10 | 1800.2135
8458 | 2023-12-19 10:00 | 111.7848 | 65.03 | 20 | 10 | 0 | 19.5 | 3536.2951
8459 | 2023-12-19 11:00 | 121.9661 | 65.03 | 1 | 0 | 9 | 10.5 | 186.9961
8460 | 2023-12-19 12:00 | 115.2016 | 65.03 | 10 | 0 | 0 | 10.5 | 1802.3155
8461 | 2023-12-19 13:00 | 120.0184 | 65.03 | 10 | 0 | 0 | 10.5 | 1850.4839
8462 | 2023-12-19 14:00 | 110.6061 | 65.03 | 20 | 10 | 0 | 20 | 3512.7229
8463 | 2023-12-19 15:00 | 117.0767 | 65.03 | 10 | 0 | 0 | 20 | 1821.0671
8464 | 2023-12-19 16:00 | 124.8789 | 65.03 | 10 | 0 | 0 | 20 | 1899.0891
8465 | 2023-12-19 17:00 | 138.8821 | 66.4 | 0 | 0 | 10 | 10 | 0
8466 | 2023-12-19 18:00 | 128.6328 | 66.4 | 0 | 0 | 10 | 0 | 0
8467 | 2023-12-19 19:00 | 126.5071 | 65.03 | 10 | 0 | 0 | 0 | 1915.3707
8468 | 2023-12-19 20:00 | 114.0168 | 65.03 | 10 | 0 | 0 | 0 | 1790.4681
8469 | 2023-12-19 21:00 | 118.4809 | 65.03 | 10 | 0 | 0 | 0 | 1835.1089
8470 | 2023-12-19 22:00 | 117.1295 | 65.03 | 10 | 0 | 0 | 0 | 1821.5952
8471 | 2023-12-19 23:00 | 105.3377 | 53.53 | 20 | 10 | 0 | 9.5 | 3177.3531
8472 | 2023-12-20 00:00 | 111.2348 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1734.3665
8473 | 2023-12-20 01:00 | 123.1338 | 53.53 | 0 | 0 | 10 | 0 | 0
8474 | 2023-12-20 02:00 | 90.4852 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1591.7472
8475 | 2023-12-20 03:00 | 79.2148 | 53.53 | 20 | 10 | 0 | 10.5 | 2654.8964
8476 | 2023-12-20 04:00 | 90.4697 | 53.53 | 20 | 10 | 0 | 20 | 2879.9944
8477 | 2023-12-20 05:00 | 110.056 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 81.793
8478 | 2023-12-20 06:00 | 80.8889 | 53.53 | 20 | 10 | 0 | 20 | 2688.3776
8479 | 2023-12-20 07:00 | 109.1222 | 53.53 | 10 | 0 | 0 | 20 | 1626.5224
8480 | 2023-12-20 08:00 | 117.2571 | 65.03 | 10 | 0 | 0 | 20 | 1822.8714
8481 | 2023-12-20 09:00 | 119.6279 | 65.03 | 10 | 0 | 0 | 20 | 1846.5787
8482 | 2023-12-20 10:00 | 120.3985 | 65.03 | 10 | 0 | 0 | 20 | 1854.2848
8483 | 2023-12-20 11:00 | 129.092 | 65.03 | 0 | 0 | 10 | 10 | 0
8484 | 2023-12-20 12:00 | 119.5423 | 65.03 | 10 | 0 | 0 | 10 | 1845.7234
8485 | 2023-12-20 13:00 | 130.5718 | 65.03 | 0 | 0 | 10 | 0 | 0
8486 | 2023-12-20 14:00 | 118.0313 | 65.03 | 11.0526 | 1.0526 | 0 | 1 | 2023.3089
8487 | 2023-12-20 15:00 | 116.4055 | 65.03 | 20 | 10 | 0 | 10.5 | 3628.7099
8488 | 2023-12-20 16:00 | 114.3511 | 65.03 | 20 | 10 | 0 | 20 | 3587.6226
8489 | 2023-12-20 17:00 | 123.3925 | 66.4 | 10 | 0 | 0 | 20 | 1897.9252
8490 | 2023-12-20 18:00 | 136.0546 | 66.4 | 0 | 0 | 10 | 10 | 0
8491 | 2023-12-20 19:00 | 155.1952 | 65.03 | 0 | 0 | 10 | 0 | 0
8492 | 2023-12-20 20:00 | 117.5825 | 65.03 | 10 | 0 | 0 | 0 | 1826.1251
8493 | 2023-12-20 21:00 | 119.6179 | 65.03 | 10 | 0 | 0 | 0 | 1846.4788
8494 | 2023-12-20 22:00 | 110.9848 | 65.03 | 10 | 0 | 0 | 0 | 1760.148
8495 | 2023-12-20 23:00 | 107.1314 | 53.53 | 20 | 10 | 0 | 9.5 | 3213.2271
8496 | 2023-12-21 00:00 | 117.4896 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1800.2068
8497 | 2023-12-21 01:00 | 129.5702 | 53.53 | 0 | 0 | 10 | 0 | 0
8498 | 2023-12-21 02:00 | 102.9646 | 53.53 | 10 | 0 | 0 | 0 | 1564.9461
8499 | 2023-12-21 03:00 | 95.7296 | 53.53 | 10 | 0 | 0 | 0 | 1492.5958
8500 | 2023-12-21 04:00 | 89.1633 | 53.53 | 20 | 10 | 0 | 9.5 | 2853.8666
8501 | 2023-12-21 05:00 | 90.5217 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1592.1507
8502 | 2023-12-21 06:00 | 83.8402 | 53.53 | 20 | 10 | 0 | 20 | 2747.4044
8503 | 2023-12-21 07:00 | 100.0888 | 53.53 | 10 | 0 | 0 | 20 | 1536.1882
8504 | 2023-12-21 08:00 | 111.7275 | 65.03 | 10 | 0 | 0 | 20 | 1767.5748
8505 | 2023-12-21 09:00 | 119.2746 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 92.1523
8506 | 2023-12-21 10:00 | 116.8015 | 65.03 | 10 | 0 | 0 | 10.5 | 1818.3154
8507 | 2023-12-21 11:00 | 109.9858 | 65.03 | 20 | 10 | 0 | 20 | 3500.3164
8508 | 2023-12-21 12:00 | 118.6199 | 65.03 | 10 | 0 | 0 | 20 | 1836.4994
8509 | 2023-12-21 13:00 | 116.6206 | 65.03 | 10 | 0 | 0 | 20 | 1816.506
8510 | 2023-12-21 14:00 | 111.4829 | 65.03 | 10 | 0 | 0 | 20 | 1765.1286
8511 | 2023-12-21 15:00 | 116.2706 | 65.03 | 10 | 0 | 0 | 20 | 1813.0057
8512 | 2023-12-21 16:00 | 116.6034 | 65.03 | 10 | 0 | 0 | 20 | 1816.3341
8513 | 2023-12-21 17:00 | 129.6761 | 66.4 | 0 | 0 | 10 | 10 | 0
8514 | 2023-12-21 18:00 | 141.9105 | 66.4 | 0 | 0 | 10 | 0 | 0
8515 | 2023-12-21 19:00 | 123.0241 | 65.03 | 10 | 0 | 0 | 0 | 1880.5414
8516 | 2023-12-21 20:00 | 102.6772 | 65.03 | 20 | 10 | 0 | 9.5 | 3354.1435
8517 | 2023-12-21 21:00 | 113.923 | 65.03 | 10 | 0 | 0 | 9.5 | 1789.5296
8518 | 2023-12-21 22:00 | 114.6298 | 65.03 | 0.5 | 0 | 9.5 | 0 | 89.8299
8519 | 2023-12-21 23:00 | 112.1214 | 53.53 | 10 | 0 | 0 | 0 | 1656.5139
8520 | 2023-12-22 00:00 | 105.1659 | 53.53 | 10 | 0 | 0 | 0 | 1586.9588
8521 | 2023-12-22 01:00 | 102.8804 | 53.53 | 10 | 0 | 0 | 0 | 1564.1045
8522 | 2023-12-22 02:00 | 88.8435 | 53.53 | 11.5789 | 1.5789 | 0 | 1.5 | 1648.5352
8523 | 2023-12-22 03:00 | 85.7965 | 53.53 | 20 | 10 | 0 | 11 | 2786.5292
8524 | 2023-12-22 04:00 | 103.7115 | 53.53 | 0 | 0 | 10 | 1 | 0
8525 | 2023-12-22 05:00 | 86.5811 | 53.53 | 20 | 10 | 0 | 10.5 | 2802.2224
8526 | 2023-12-22 06:00 | 88.5026 | 53.53 | 20 | 10 | 0 | 20 | 2840.6517
8527 | 2023-12-22 07:00 | 136.4344 | 53.53 | 10 | 0 | 0 | 20 | 1899.6444
8528 | 2023-12-22 08:00 | 117.4795 | 65.03 | 10 | 0 | 0 | 20 | 1825.0946
8529 | 2023-12-22 09:00 | 123.4376 | 65.03 | 10 | 0 | 0 | 20 | 1884.6764
8530 | 2023-12-22 10:00 | 124.2475 | 65.03 | 10 | 0 | 0 | 20 | 1892.7746
8531 | 2023-12-22 11:00 | 125.0322 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 95.0311
8532 | 2023-12-22 12:00 | 121.1665 | 65.03 | 10 | 0 | 0 | 10.5 | 1861.9653
8533 | 2023-12-22 13:00 | 120.3952 | 65.03 | 10 | 0 | 0 | 10.5 | 1854.2521
8534 | 2023-12-22 14:00 | 119.6623 | 65.03 | 10 | 0 | 0 | 10.5 | 1846.9225
8535 | 2023-12-22 15:00 | 114.931 | 65.03 | 20 | 10 | 0 | 20 | 3599.2198
8536 | 2023-12-22 16:00 | 121.4629 | 65.03 | 10 | 0 | 0 | 20 | 1864.9288
8537 | 2023-12-22 17:00 | 154.8444 | 66.4 | 0 | 0 | 10 | 10 | 0
8538 | 2023-12-22 18:00 | 144.8466 | 66.4 | 0 | 0 | 10 | 0 | 0
8539 | 2023-12-22 19:00 | 136.2848 | 65.03 | 10 | 0 | 0 | 0 | 2013.1483
8540 | 2023-12-22 20:00 | 121.2163 | 65.03 | 10 | 0 | 0 | 0 | 1862.4632
8541 | 2023-12-22 21:00 | 108.1601 | 65.03 | 10 | 0 | 0 | 0 | 1731.9009
8542 | 2023-12-22 22:00 | 112.0189 | 65.03 | 10 | 0 | 0 | 0 | 1770.4886
8543 | 2023-12-22 23:00 | 117.1209 | 53.53 | 10 | 0 | 0 | 0 | 1706.5092
8544 | 2023-12-23 00:00 | 114.9555 | 53.53 | 10 | 0 | 0 | 0 | 1684.8546
8545 | 2023-12-23 01:00 | 95.7366 | 53.53 | 10 | 0 | 0 | 0 | 1492.6664
8546 | 2023-12-23 02:00 | 77.5222 | 53.53 | 20 | 10 | 0 | 9.5 | 2621.0442
8547 | 2023-12-23 03:00 | -58.7274 | 53.53 | 20 | 10 | 0 | 19 | -103.9473
8548 | 2023-12-23 04:00 | 81.6308 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1493.8824
8549 | 2023-12-23 05:00 | 99.1002 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 76.3151
8550 | 2023-12-23 06:00 | 82.4989 | 53.53 | 20 | 10 | 0 | 20 | 2720.5777
8551 | 2023-12-23 07:00 | 102.8145 | 53.53 | 10 | 0 | 0 | 20 | 1563.4455
8552 | 2023-12-23 08:00 | 108.709 | 53.53 | 10 | 0 | 0 | 20 | 1622.3898
8553 | 2023-12-23 09:00 | 119.0682 | 53.53 | 0 | 0 | 10 | 10 | 0
8554 | 2023-12-23 10:00 | 123.4684 | 53.53 | 0 | 0 | 10 | 0 | 0
8555 | 2023-12-23 11:00 | 104.2253 | 53.53 | 20 | 10 | 0 | 9.5 | 3155.106
8556 | 2023-12-23 12:00 | 108.3899 | 53.53 | 20 | 10 | 0 | 19 | 3238.3976
8557 | 2023-12-23 13:00 | 118.7959 | 53.53 | 0 | 0 | 10 | 9 | 0
8558 | 2023-12-23 14:00 | 109.9453 | 53.53 | 11.5789 | 1.5789 | 0 | 10.5 | 1892.8722
8559 | 2023-12-23 15:00 | 107.4587 | 53.53 | 20 | 10 | 0 | 20 | 3219.7749
8560 | 2023-12-23 16:00 | 119.7415 | 53.53 | 10 | 0 | 0 | 20 | 1732.7152
8561 | 2023-12-23 17:00 | 135.7086 | 53.53 | 0 | 0 | 10 | 10 | 0
8562 | 2023-12-23 18:00 | 122.7435 | 53.53 | 10 | 0 | 0 | 10 | 1762.7355
8563 | 2023-12-23 19:00 | 127.5429 | 53.53 | 0 | 0 | 10 | 0 | 0
8564 | 2023-12-23 20:00 | 98.2959 | 53.53 | 20 | 10 | 0 | 9.5 | 3036.5185
8565 | 2023-12-23 21:00 | 100.0087 | 53.53 | 10 | 0 | 0 | 9.5 | 1535.3868
8566 | 2023-12-23 22:00 | 106.8471 | 53.53 | 0.5 | 0 | 9.5 | 0 | 80.1886
8567 | 2023-12-23 23:00 | 101.135 | 53.53 | 10 | 0 | 0 | 0 | 1546.6497
8568 | 2023-12-24 00:00 | 94.6037 | 53.53 | 10 | 0 | 0 | 0 | 1481.3372
8569 | 2023-12-24 01:00 | 96.066 | 53.53 | 10 | 0 | 0 | 0 | 1495.9603
8570 | 2023-12-24 02:00 | 74.0609 | 53.53 | 20 | 10 | 0 | 9.5 | 2551.8174
8571 | 2023-12-24 03:00 | 84.5552 | 53.53 | 0.5 | 0 | 9.5 | 0 | 69.0426
8572 | 2023-12-24 04:00 | 69.7524 | 53.53 | 20 | 10 | 0 | 9.5 | 2465.6489
8573 | 2023-12-24 05:00 | 74.3545 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1413.4608
8574 | 2023-12-24 06:00 | 70.1945 | 53.53 | 20 | 10 | 0 | 20 | 2474.49
8575 | 2023-12-24 07:00 | 104.247 | 53.53 | 10 | 0 | 0 | 20 | 1577.7703
8576 | 2023-12-24 08:00 | 100.4551 | 53.53 | 10 | 0 | 0 | 20 | 1539.8507
8577 | 2023-12-24 09:00 | 111.1374 | 53.53 | 10 | 0 | 0 | 20 | 1646.6741
8578 | 2023-12-24 10:00 | 126.7821 | 53.53 | 0 | 0 | 10 | 10 | 0
8579 | 2023-12-24 11:00 | 127.2001 | 53.53 | 0 | 0 | 10 | 0 | 0
8580 | 2023-12-24 12:00 | 100.4412 | 53.53 | 20 | 10 | 0 | 9.5 | 3079.4243
8581 | 2023-12-24 13:00 | 113.2396 | 53.53 | 1.5 | 0 | 8.5 | 1 | 250.1544
8582 | 2023-12-24 14:00 | 104.4801 | 53.53 | 20 | 10 | 0 | 10.5 | 3160.2028
8583 | 2023-12-24 15:00 | 103.3762 | 53.53 | 20 | 10 | 0 | 20 | 3138.1233
8584 | 2023-12-24 16:00 | 110.0616 | 53.53 | 10 | 0 | 0 | 20 | 1635.916
8585 | 2023-12-24 17:00 | 137.037 | 53.53 | 0 | 0 | 10 | 10 | 0
8586 | 2023-12-24 18:00 | 130.8257 | 53.53 | 0 | 0 | 10 | 0 | 0
8587 | 2023-12-24 19:00 | 121.0711 | 53.53 | 10 | 0 | 0 | 0 | 1746.0107
8588 | 2023-12-24 20:00 | -69.3723 | 53.53 | 20 | 10 | 0 | 9.5 | -316.8457
8589 | 2023-12-24 21:00 | -72.2191 | 53.53 | 20 | 10 | 0 | 19 | -373.7822
8590 | 2023-12-24 22:00 | 100.8436 | 53.53 | 10 | 0 | 0 | 19 | 1543.7358
8591 | 2023-12-24 23:00 | 95.4236 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1646.3287
8592 | 2023-12-25 00:00 | 109.4927 | 53.53 | 0 | 0 | 10 | 10 | 0
8593 | 2023-12-25 01:00 | 107.4225 | 53.53 | 0 | 0 | 10 | 0 | 0
8594 | 2023-12-25 02:00 | 87.8595 | 53.53 | 20 | 10 | 0 | 9.5 | 2827.7895
8595 | 2023-12-25 03:00 | 87.6217 | 53.53 | 20 | 10 | 0 | 19 | 2823.0332
8596 | 2023-12-25 04:00 | 89.0669 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1576.0713
8597 | 2023-12-25 05:00 | 93.296 | 53.53 | 10 | 0 | 0 | 20 | 1468.2597
8598 | 2023-12-25 06:00 | 90.0438 | 53.53 | 10 | 0 | 0 | 20 | 1435.7375
8599 | 2023-12-25 07:00 | 106.8541 | 53.53 | 10 | 0 | 0 | 20 | 1603.841
8600 | 2023-12-25 08:00 | 122.1005 | 65.03 | 10 | 0 | 0 | 20 | 1871.3052
8601 | 2023-12-25 09:00 | 125.9296 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 95.4798
8602 | 2023-12-25 10:00 | 115.0574 | 65.03 | 20 | 10 | 0 | 20 | 3601.7473
8603 | 2023-12-25 11:00 | 118.4567 | 65.03 | 10 | 0 | 0 | 20 | 1834.8673
8604 | 2023-12-25 12:00 | 129.3244 | 65.03 | 0 | 0 | 10 | 10 | 0
8605 | 2023-12-25 13:00 | 111.8565 | 65.03 | 20 | 10 | 0 | 19.5 | 3537.7304
8606 | 2023-12-25 14:00 | 136.859 | 65.03 | 0 | 0 | 10 | 9.5 | 0
8607 | 2023-12-25 15:00 | -73.8548 | 65.03 | 20 | 10 | 0 | 19 | -176.4959
8608 | 2023-12-25 16:00 | 116.4377 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 2005.6961
8609 | 2023-12-25 17:00 | 127.6976 | 66.4 | 10 | 0 | 0 | 20 | 1940.9759
8610 | 2023-12-25 18:00 | 157.0932 | 66.4 | 0 | 0 | 10 | 10 | 0
8611 | 2023-12-25 19:00 | 130.3944 | 65.03 | 0 | 0 | 10 | 0 | 0
8612 | 2023-12-25 20:00 | 110.4106 | 65.03 | 10 | 0 | 0 | 0 | 1754.4058
8613 | 2023-12-25 21:00 | 111.2667 | 65.03 | 10 | 0 | 0 | 0 | 1762.9675
8614 | 2023-12-25 22:00 | 114.6257 | 65.03 | 10 | 0 | 0 | 0 | 1796.5571
8615 | 2023-12-25 23:00 | 106.5525 | 53.53 | 10 | 0 | 0 | 0 | 1600.8246
8616 | 2023-12-26 00:00 | 107.9213 | 53.53 | 10 | 0 | 0 | 0 | 1614.5126
8617 | 2023-12-26 01:00 | 92.5704 | 53.53 | 11.0526 | 1.0526 | 0 | 1 | 1614.7941
8618 | 2023-12-26 02:00 | 89.3307 | 53.53 | 20 | 10 | 0 | 10.5 | 2857.214
8619 | 2023-12-26 03:00 | 89.0322 | 53.53 | 20 | 10 | 0 | 20 | 2851.2443
8620 | 2023-12-26 04:00 | 98.0375 | 53.53 | 10 | 0 | 0 | 20 | 1515.6751
8621 | 2023-12-26 05:00 | 100.9233 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 77.2267
8622 | 2023-12-26 06:00 | 87.5294 | 53.53 | 20 | 10 | 0 | 20 | 2821.188
8623 | 2023-12-26 07:00 | 115.8346 | 53.53 | 10 | 0 | 0 | 20 | 1693.6465
8624 | 2023-12-26 08:00 | 111.8629 | 65.03 | 10 | 0 | 0 | 20 | 1768.9294
8625 | 2023-12-26 09:00 | 125.3697 | 65.03 | 0 | 0 | 10 | 10 | 0
8626 | 2023-12-26 10:00 | 114.9532 | 65.03 | 10.5263 | 0.52632 | 0 | 10.5 | 1894.56
8627 | 2023-12-26 11:00 | 111.4205 | 65.03 | 20 | 10 | 0 | 20 | 3529.0094
8628 | 2023-12-26 12:00 | 117.5444 | 65.03 | 10 | 0 | 0 | 20 | 1825.7443
8629 | 2023-12-26 13:00 | 131.9527 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 98.4914
8630 | 2023-12-26 14:00 | 120.2934 | 65.03 | 20 | 10 | 0 | 20 | 3706.4676
8631 | 2023-12-26 15:00 | 133.0648 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 99.0474
8632 | 2023-12-26 16:00 | 113.8688 | 65.03 | 20 | 10 | 0 | 20 | 3577.9761
8633 | 2023-12-26 17:00 | 143.1327 | 66.4 | 0 | 0 | 10 | 10 | 0
8634 | 2023-12-26 18:00 | 129.4558 | 66.4 | 10 | 0 | 0 | 10 | 1958.5585
8635 | 2023-12-26 19:00 | 135.6467 | 65.03 | 0 | 0 | 10 | 0 | 0
8636 | 2023-12-26 20:00 | 115.5774 | 65.03 | 10 | 0 | 0 | 0 | 1806.0741
8637 | 2023-12-26 21:00 | 119.386 | 65.03 | 10 | 0 | 0 | 0 | 1844.1601
8638 | 2023-12-26 22:00 | 115.8514 | 65.03 | 10 | 0 | 0 | 0 | 1808.814
8639 | 2023-12-26 23:00 | 103.9261 | 53.53 | 20 | 10 | 0 | 9.5 | 3149.1218
8640 | 2023-12-27 00:00 | 116.4545 | 53.53 | 10.5263 | 0.52632 | 0 | 10 | 1789.3106
8641 | 2023-12-27 01:00 | 125.9279 | 53.53 | 0 | 0 | 10 | 0 | 0
8642 | 2023-12-27 02:00 | 84.8818 | 53.53 | 20 | 10 | 0 | 9.5 | 2768.2354
8643 | 2023-12-27 03:00 | 78.3138 | 53.53 | 20 | 10 | 0 | 19 | 2636.8768
8644 | 2023-12-27 04:00 | 92.9382 | 53.53 | 10 | 0 | 0 | 19 | 1464.6823
8645 | 2023-12-27 05:00 | 86.5339 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1548.0742
8646 | 2023-12-27 06:00 | 87.9341 | 53.53 | 10 | 0 | 0 | 20 | 1414.6412
8647 | 2023-12-27 07:00 | 113.4378 | 53.53 | 10 | 0 | 0 | 20 | 1669.6783
8648 | 2023-12-27 08:00 | 115.6994 | 65.03 | 10 | 0 | 0 | 20 | 1807.2936
8649 | 2023-12-27 09:00 | 116.9611 | 65.03 | 10 | 0 | 0 | 20 | 1819.9109
8650 | 2023-12-27 10:00 | 118.1586 | 65.03 | 10 | 0 | 0 | 20 | 1831.8857
8651 | 2023-12-27 11:00 | 132.752 | 65.03 | 0 | 0 | 10 | 10 | 0
8652 | 2023-12-27 12:00 | 119.1248 | 65.03 | 10 | 0 | 0 | 10 | 1841.5485
8653 | 2023-12-27 13:00 | 111.1545 | 65.03 | 20 | 10 | 0 | 19.5 | 3523.6909
8654 | 2023-12-27 14:00 | 111.3618 | 65.03 | 10.5263 | 0.52632 | 0 | 20 | 1856.7557
8655 | 2023-12-27 15:00 | 119.9646 | 65.03 | 10 | 0 | 0 | 20 | 1849.9465
8656 | 2023-12-27 16:00 | 111.7134 | 65.03 | 10 | 0 | 0 | 20 | 1767.4342
8657 | 2023-12-27 17:00 | 124.5438 | 66.4 | 10 | 0 | 0 | 20 | 1909.4383
8658 | 2023-12-27 18:00 | 139.1495 | 66.4 | 0 | 0 | 10 | 10 | 0
8659 | 2023-12-27 19:00 | 139.5972 | 65.03 | 0 | 0 | 10 | 0 | 0
8660 | 2023-12-27 20:00 | 111.2843 | 65.03 | 10 | 0 | 0 | 0 | 1763.1429
8661 | 2023-12-27 21:00 | 116.2007 | 65.03 | 10 | 0 | 0 | 0 | 1812.3068
8662 | 2023-12-27 22:00 | 115.3498 | 65.03 | 10 | 0 | 0 | 0 | 1803.7979
8663 | 2023-12-27 23:00 | 113.8505 | 53.53 | 10 | 0 | 0 | 0 | 1673.8047
8664 | 2023-12-28 00:00 | 113.8714 | 53.53 | 10 | 0 | 0 | 0 | 1674.0142
8665 | 2023-12-28 01:00 | 95.3386 | 53.53 | 10 | 0 | 0 | 0 | 1488.6857
8666 | 2023-12-28 02:00 | 87.1581 | 53.53 | 20 | 10 | 0 | 9.5 | 2813.7619
8667 | 2023-12-28 03:00 | 93.1006 | 53.53 | 10 | 0 | 0 | 9.5 | 1466.3059
8668 | 2023-12-28 04:00 | 86.0019 | 53.53 | 20 | 10 | 0 | 19 | 2790.6374
8669 | 2023-12-28 05:00 | 89.1713 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1577.225
8670 | 2023-12-28 06:00 | 95.2129 | 53.53 | 10 | 0 | 0 | 20 | 1487.4295
8671 | 2023-12-28 07:00 | 109.5127 | 53.53 | 10 | 0 | 0 | 20 | 1630.4267
8672 | 2023-12-28 08:00 | 133.1994 | 65.03 | 0 | 0 | 10 | 10 | 0
8673 | 2023-12-28 09:00 | 128.9552 | 65.03 | 0 | 0 | 10 | 0 | 0
8674 | 2023-12-28 10:00 | 118.0247 | 65.03 | 10 | 0 | 0 | 0 | 1830.547
8675 | 2023-12-28 11:00 | 117.4562 | 65.03 | 10 | 0 | 0 | 0 | 1824.8622
8676 | 2023-12-28 12:00 | 104.5294 | 65.03 | 20 | 10 | 0 | 9.5 | 3391.187
8677 | 2023-12-28 13:00 | 116.5656 | 65.03 | 11.0526 | 1.0526 | 0 | 10.5 | 2007.1098
8678 | 2023-12-28 14:00 | 110.5564 | 65.03 | 20 | 10 | 0 | 20 | 3511.7276
8679 | 2023-12-28 15:00 | 120.6138 | 65.03 | 10 | 0 | 0 | 20 | 1856.4383
8680 | 2023-12-28 16:00 | 120.0715 | 65.03 | 10 | 0 | 0 | 20 | 1851.0153
8681 | 2023-12-28 17:00 | 139.7019 | 66.4 | 0 | 0 | 10 | 10 | 0
8682 | 2023-12-28 18:00 | 146.9094 | 66.4 | 0 | 0 | 10 | 0 | 0
8683 | 2023-12-28 19:00 | 133.7021 | 65.03 | 10 | 0 | 0 | 0 | 1987.3206
8684 | 2023-12-28 20:00 | 138.4492 | 65.03 | 10 | 0 | 0 | 0 | 2034.7922
8685 | 2023-12-28 21:00 | 115.7039 | 65.03 | 10 | 0 | 0 | 0 | 1807.3392
8686 | 2023-12-28 22:00 | 105.7729 | 65.03 | 10 | 0 | 0 | 0 | 1708.0293
8687 | 2023-12-28 23:00 | 105.019 | 53.53 | 20 | 10 | 0 | 9.5 | 3170.9804
8688 | 2023-12-29 00:00 | 106.2533 | 53.53 | 10 | 0 | 0 | 9.5 | 1597.8335
8689 | 2023-12-29 01:00 | 113.7581 | 53.53 | 0.5 | 0 | 9.5 | 0 | 83.6441
8690 | 2023-12-29 02:00 | 82.7142 | 53.53 | 20 | 10 | 0 | 9.5 | 2724.8836
8691 | 2023-12-29 03:00 | 86.7605 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1550.5788
8692 | 2023-12-29 04:00 | 87.7192 | 53.53 | 10 | 0 | 0 | 10.5 | 1412.4922
8693 | 2023-12-29 05:00 | 85.7535 | 53.53 | 20 | 10 | 0 | 20 | 2785.6704
8694 | 2023-12-29 06:00 | 95.7886 | 53.53 | 10 | 0 | 0 | 20 | 1493.1856
8695 | 2023-12-29 07:00 | 114.2021 | 53.53 | 10 | 0 | 0 | 20 | 1677.3208
8696 | 2023-12-29 08:00 | 129.3739 | 65.03 | 0 | 0 | 10 | 10 | 0
8697 | 2023-12-29 09:00 | 116.5349 | 65.03 | 10 | 0 | 0 | 10 | 1815.6491
8698 | 2023-12-29 10:00 | 129.7587 | 65.03 | 0 | 0 | 10 | 0 | 0
8699 | 2023-12-29 11:00 | 110.5029 | 65.03 | 20 | 10 | 0 | 9.5 | 3510.6571
8700 | 2023-12-29 12:00 | 110.3818 | 65.03 | 20 | 10 | 0 | 19 | 3508.2363
8701 | 2023-12-29 13:00 | 111.2681 | 65.03 | 11.0526 | 1.0526 | 0 | 20 | 1948.5584
8702 | 2023-12-29 14:00 | 118.9675 | 65.03 | 10 | 0 | 0 | 20 | 1839.9749
8703 | 2023-12-29 15:00 | 129.7571 | 65.03 | 0.5 | 0 | 9.5 | 10.5 | 97.3936
8704 | 2023-12-29 16:00 | 114.7666 | 65.03 | 20 | 10 | 0 | 20 | 3595.9329
8705 | 2023-12-29 17:00 | 130.567 | 66.4 | 10 | 0 | 0 | 20 | 1969.6698
8706 | 2023-12-29 18:00 | 132.3296 | 66.4 | 0 | 0 | 10 | 10 | 0
8707 | 2023-12-29 19:00 | 138.5858 | 65.03 | 0 | 0 | 10 | 0 | 0
8708 | 2023-12-29 20:00 | 110.5609 | 65.03 | 10 | 0 | 0 | 0 | 1755.9093
8709 | 2023-12-29 21:00 | 110.2014 | 65.03 | 10 | 0 | 0 | 0 | 1752.3137
8710 | 2023-12-29 22:00 | 105.5958 | 65.03 | 10 | 0 | 0 | 0 | 1706.2578
8711 | 2023-12-29 23:00 | 104.958 | 53.53 | 10 | 0 | 0 | 0 | 1584.8797
8712 | 2023-12-30 00:00 | 111.4901 | 53.53 | 10 | 0 | 0 | 0 | 1650.2007
8713 | 2023-12-30 01:00 | 101.5896 | 53.53 | 10 | 0 | 0 | 0 | 1551.1964
8714 | 2023-12-30 02:00 | 75.9221 | 53.53 | 20 | 10 | 0 | 9.5 | 2589.0413
8715 | 2023-12-30 03:00 | 92.1222 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1609.8401
8716 | 2023-12-30 04:00 | 76.8729 | 53.53 | 20 | 10 | 0 | 20 | 2608.0579
8717 | 2023-12-30 05:00 | 94.1758 | 53.53 | 10 | 0 | 0 | 20 | 1477.0582
8718 | 2023-12-30 06:00 | 93.9885 | 53.53 | 10 | 0 | 0 | 20 | 1475.1854
8719 | 2023-12-30 07:00 | 101.3219 | 53.53 | 0.5 | 0 | 9.5 | 10.5 | 77.426
8720 | 2023-12-30 08:00 | -32.1591 | 53.53 | 20 | 10 | 0 | 20 | 427.4185
8721 | 2023-12-30 09:00 | 135.5844 | 53.53 | 0 | 0 | 10 | 10 | 0
8722 | 2023-12-30 10:00 | 113.9783 | 53.53 | 10 | 0 | 0 | 10 | 1675.0834
8723 | 2023-12-30 11:00 | 108.5834 | 53.53 | 20 | 10 | 0 | 19.5 | 3242.2688
8724 | 2023-12-30 12:00 | 119.2035 | 53.53 | 10 | 0 | 0 | 19.5 | 1727.3353
8725 | 2023-12-30 13:00 | 116.7616 | 53.53 | 10 | 0 | 0 | 19.5 | 1702.9157
8726 | 2023-12-30 14:00 | 122.9442 | 53.53 | 0 | 0 | 10 | 9.5 | 0
8727 | 2023-12-30 15:00 | 106.3931 | 53.53 | 20 | 10 | 0 | 19 | 3198.4622
8728 | 2023-12-30 16:00 | 113.4047 | 53.53 | 11.0526 | 1.0526 | 0 | 20 | 1845.0675
8729 | 2023-12-30 17:00 | 118.4143 | 53.53 | 10 | 0 | 0 | 20 | 1719.4431
8730 | 2023-12-30 18:00 | 131.4303 | 53.53 | 0 | 0 | 10 | 10 | 0
8731 | 2023-12-30 19:00 | 125.7268 | 53.53 | 0 | 0 | 10 | 0 | 0
8732 | 2023-12-30 20:00 | 108.0973 | 53.53 | 10 | 0 | 0 | 0 | 1616.2726
8733 | 2023-12-30 21:00 | 104.8244 | 53.53 | 10 | 0 | 0 | 0 | 1583.5443
8734 | 2023-12-30 22:00 | 104.085 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1659.1054
8735 | 2023-12-30 23:00 | 95.1656 | 53.53 | 20 | 10 | 0 | 10 | 2973.911
8736 | 2023-12-31 00:00 | 107.5884 | 53.53 | 10 | 0 | 0 | 10 | 1611.1842
8737 | 2023-12-31 01:00 | 114.9852 | 53.53 | 0 | 0 | 10 | 0 | 0
8738 | 2023-12-31 02:00 | 77.0533 | 53.53 | 20 | 10 | 0 | 9.5 | 2611.6657
8739 | 2023-12-31 03:00 | 85.4145 | 53.53 | 10 | 0 | 0 | 9.5 | 1389.4447
8740 | 2023-12-31 04:00 | 84.3592 | 53.53 | 10 | 0 | 0 | 9.5 | 1378.892
8741 | 2023-12-31 05:00 | 80.9591 | 53.53 | 11.0526 | 1.0526 | 0 | 10.5 | 1486.4586
8742 | 2023-12-31 06:00 | 71.7123 | 53.53 | 20 | 10 | 0 | 20 | 2504.8466
8743 | 2023-12-31 07:00 | 92.8166 | 53.53 | 10 | 0 | 0 | 20 | 1463.4662
8744 | 2023-12-31 08:00 | 105.6765 | 53.53 | 10 | 0 | 0 | 20 | 1592.0652
8745 | 2023-12-31 09:00 | 99.0582 | 53.53 | 10 | 0 | 0 | 20 | 1525.8821
8746 | 2023-12-31 10:00 | 124.0391 | 53.53 | 0 | 0 | 10 | 10 | 0
8747 | 2023-12-31 11:00 | 113.8139 | 53.53 | 1 | 0 | 9 | 1 | 167.3439
8748 | 2023-12-31 12:00 | 110.6746 | 53.53 | 10 | 0 | 0 | 1 | 1642.0461
8749 | 2023-12-31 13:00 | 98.8575 | 53.53 | 20 | 10 | 0 | 10.5 | 3047.7499
8750 | 2023-12-31 14:00 | 100.3631 | 53.53 | 20 | 10 | 0 | 20 | 3077.8611
8751 | 2023-12-31 15:00 | 110.8808 | 53.53 | 10 | 0 | 0 | 20 | 1644.1075
8752 | 2023-12-31 16:00 | 131.0498 | 53.53 | 0 | 0 | 10 | 10 | 0
8753 | 2023-12-31 17:00 | 121.1712 | 53.53 | 10 | 0 | 0 | 10 | 1747.0116
8754 | 2023-12-31 18:00 | 133.2937 | 53.53 | 0 | 0 | 10 | 0 | 0
8755 | 2023-12-31 19:00 | 122.5461 | 53.53 | 10 | 0 | 0 | 0 | 1760.7613
8756 | 2023-12-31 20:00 | 106.3161 | 53.53 | 20 | 10 | 0 | 9.5 | 3196.921
8757 | 2023-12-31 21:00 | 116.8897 | 53.53 | 0.5 | 0 | 9.5 | 0 | 85.2099
8758 | 2023-12-31 22:00 | 103.4338 | 53.53 | 10.5263 | 0.52632 | 0 | 0.5 | 1652.2502
8759 | 2023-12-31 23:00 | 96.2232 | 53.53 | 20 | 10 | 0 | 10 | 2995.0632

## DR Analysis
Event # | Day of Year | Date | Start Hour | Duration (h) | Baseline Import (MW) | Actual Import (MW) | Curtailed (MWh) | Capacity Claim (MW)
1 | 151 | 2023-06-01 | 16:00 | 2 | 16 | 2 | 16 | 10
2 | 152 | 2023-06-02 | 18:00 | 2 | 8 | 6 | 8 | 4
3 | 155 | 2023-06-05 | 16:00 | 2 | 16 | 2 | 16 | 10
4 | 156 | 2023-06-06 | 20:00 | 2 | 16.1053 | 2.1974 | 15.6053 | 4.75
5 | 158 | 2023-06-08 | 20:00 | 2 | 16.1053 | 7.2105 | 5.5789 | 9.75
6 | 159 | 2023-06-09 | 16:00 | 2 | 14 | 8 | 4 | 10
7 | 162 | 2023-06-12 | 16:00 | 2 | 14 | 3 | 14 | 10
8 | 163 | 2023-06-13 | 16:00 | 2 | 14 | 3 | 14 | 10
9 | 164 | 2023-06-14 | 16:00 | 2 | 14 | 3.25 | 13.5 | 10
10 | 169 | 2023-06-19 | 20:00 | 2 | 16.1053 | 6.9474 | 6.1053 | 9.5
11 | 170 | 2023-06-20 | 16:00 | 2 | 12 | 4 | 12 | 10
12 | 173 | 2023-06-23 | 19:00 | 2 | 4.1 | 10 | 0 | 4.1
13 | 176 | 2023-06-26 | 16:00 | 2 | 10.2105 | 4.8947 | 10.2105 | 9.5
14 | 177 | 2023-06-27 | 16:00 | 2 | 10.2105 | 4.8947 | 10.2105 | 10
15 | 178 | 2023-06-28 | 20:00 | 2 | 14 | 3.25 | 13.5 | 4.75
16 | 180 | 2023-06-30 | 20:00 | 2 | 12 | 4.25 | 11.5 | 4.75
17 | 184 | 2023-07-04 | 20:00 | 2 | 12 | 4.25 | 11.5 | 4.75
18 | 185 | 2023-07-05 | 16:00 | 2 | 12.6316 | 3.9342 | 12.1316 | 10
19 | 187 | 2023-07-07 | 16:00 | 2 | 12.6316 | 3.6842 | 12.6316 | 10
20 | 190 | 2023-07-10 | 16:00 | 2 | 12.6316 | 8.6842 | 2.6316 | 10
TOTAL | [6 empty] | 209.1053
Annual DSU Revenue Model
Enrolled Capacity (MW) | 8.2925
DSU Eligible (≥4 MW) | Yes
EirGrid Capacity Payment (€) | 1144365
Total DR Revenue (€) | 1144365
Annual Peak Discharge (MWh) | 5043
BESS Deficit (€) | -23733.8319
Net (€) | 1120631.1681

## Cost Comparison
Month | Grid-Only Cost (€) | BESS Import Cost (€) | Savings (€) | Savings (%) | Grid-Only Emissions (tCO₂) | BESS Emissions (tCO₂) | Emissions Saved (tCO₂)
January | 1237067.4034 | 1175506.6661 | 61560.7374 | 4.976% | 1674 | 1692.6099 | -18.6099
February | 1062614.8352 | 957645.3104 | 104969.5248 | 9.878% | 1512 | 1530.6691 | -18.6691
March | 1139051.7376 | 1054701.8584 | 84349.8792 | 7.405% | 1674 | 1691.6092 | -17.6092
April | 956769.8681 | 850615.3827 | 106154.4855 | 11.1% | 1620 | 1646.2599 | -26.2599
May | 997234.9819 | 884199.4993 | 113035.4826 | 11.33% | 1674 | 1689.7678 | -15.7678
June | 1012051.0899 | 939695.4337 | 72355.6562 | 7.149% | 1620 | 1641.0789 | -21.0789
July | 1003356.1467 | 934647.7318 | 68708.4149 | 6.848% | 1674 | 1696.1211 | -22.1211
August | 1013719.0555 | 940361.7615 | 73357.294 | 7.236% | 1674 | 1698.1697 | -24.1697
September | 1079378.3693 | 1002098.9495 | 77279.4198 | 7.16% | 1620 | 1637.1947 | -17.1947
October | 1087163.9898 | 987169.5567 | 99994.4331 | 9.198% | 1674 | 1695.5171 | -21.5171
November | 1106045.8103 | 1034963.9107 | 71081.8996 | 6.427% | 1620 | 1641.9553 | -21.9553
December | 1213181.4199 | 1128787.0231 | 84394.3968 | 6.956% | 1674 | 1694.8243 | -20.8243

## Beta Sensitivity
Beta | Discount Formula | Optimal P (MW) | Optimal E (MWh) | Adj. DR Revenue (EUR) | Adj. Net Cost (EUR) | Savings vs Grid-Only (EUR)
0 | 1 - 0.00 * (P / 10) | 10 | 20 | 1144365 | 16142911.8758 | 1168098.8319
0.05 | 1 - 0.05 * (P / 10) | 10 | 20 | 1087146.75 | 16200130.1258 | 1110880.5819
0.1 | 1 - 0.10 * (P / 10) | 10 | 20 | 1029928.5 | 16257348.3758 | 1053662.3319
0.15 | 1 - 0.15 * (P / 10) | 10 | 20 | 972710.25 | 16314566.6258 | 996444.0819
0.2 | 1 - 0.20 * (P / 10) | 10 | 20 | 915492 | 16371784.8758 | 939225.8319
0.25 | 1 - 0.25 * (P / 10) | 10 | 20 | 858273.75 | 16429003.1258 | 882007.5819
0.3 | 1 - 0.30 * (P / 10) | 10 | 20 | 801055.5 | 16486221.3758 | 824789.3319
0.35 | 1 - 0.35 * (P / 10) | 10 | 20 | 743837.25 | 16543439.6258 | 767571.0819
0.4 | 1 - 0.40 * (P / 10) | 10 | 20 | 686619 | 16600657.8758 | 710352.8319
0.45 | 1 - 0.45 * (P / 10) | 10 | 20 | 629400.75 | 16657876.1258 | 653134.5819
0.5 | 1 - 0.50 * (P / 10) | 10 | 20 | 572182.5 | 16715094.3758 | 595916.3319
Adjusted Net Cost by Config and Beta
Config | β=0.00 | β=0.05 | β=0.10 | β=0.15 | β=0.20 | β=0.25 | β=0.30 | β=0.35 | β=0.40 | β=0.45 | β=0.50
2MW/2MWh | 17304264.0573 | 17304264.0573 | 17304264.0573 | 17304264.0573 | 17304264.0573 | 17304264.0573 | 17304264.0573 | 17304264.0573 | 17304264.0573 | 17304264.0573 | 17304264.0573
2MW/4MWh | 17306263.9413 | 17306263.9413 | 17306263.9413 | 17306263.9413 | 17306263.9413 | 17306263.9413 | 17306263.9413 | 17306263.9413 | 17306263.9413 | 17306263.9413 | 17306263.9413
2MW/8MWh | 17379448.7977 | 17379448.7977 | 17379448.7977 | 17379448.7977 | 17379448.7977 | 17379448.7977 | 17379448.7977 | 17379448.7977 | 17379448.7977 | 17379448.7977 | 17379448.7977
4MW/4MWh | 17297517.4068 | 17297517.4068 | 17297517.4068 | 17297517.4068 | 17297517.4068 | 17297517.4068 | 17297517.4068 | 17297517.4068 | 17297517.4068 | 17297517.4068 | 17297517.4068
4MW/8MWh | 17301517.1749 | 17301517.1749 | 17301517.1749 | 17301517.1749 | 17301517.1749 | 17301517.1749 | 17301517.1749 | 17301517.1749 | 17301517.1749 | 17301517.1749 | 17301517.1749
4MW/16MWh | 17447886.8877 | 17447886.8877 | 17447886.8877 | 17447886.8877 | 17447886.8877 | 17447886.8877 | 17447886.8877 | 17447886.8877 | 17447886.8877 | 17447886.8877 | 17447886.8877
6MW/6MWh | 16702890.7564 | 16720527.1564 | 16738163.5564 | 16755799.9564 | 16773436.3564 | 16791072.7564 | 16808709.1564 | 16826345.5564 | 16843981.9564 | 16861618.3564 | 16879254.7564
6MW/12MWh | 16582620.4086 | 16604044.9086 | 16625469.4086 | 16646893.9086 | 16668318.4086 | 16689742.9086 | 16711167.4086 | 16732591.9086 | 16754016.4086 | 16775440.9086 | 16796865.4086
6MW/24MWh | 16820390.9776 | 16841268.9976 | 16862147.0176 | 16883025.0376 | 16903903.0576 | 16924781.0776 | 16945659.0976 | 16966537.1176 | 16987415.1376 | 17008293.1576 | 17029171.1776
8MW/8MWh | 16500184.106 | 16531537.706 | 16562891.306 | 16594244.906 | 16625598.506 | 16656952.106 | 16688305.706 | 16719659.306 | 16751012.906 | 16782366.506 | 16813720.106
8MW/16MWh | 16357211.6422 | 16394604.1222 | 16431996.6022 | 16469389.0822 | 16506781.5622 | 16544174.0422 | 16581566.5222 | 16618959.0022 | 16656351.4822 | 16693743.9622 | 16731136.4422
8MW/32MWh | 16691351.0676 | 16727087.5476 | 16762824.0276 | 16798560.5076 | 16834296.9876 | 16870033.4676 | 16905769.9476 | 16941506.4276 | 16977242.9076 | 17012979.3876 | 17048715.8676
10MW/10MWh | 16297477.4556 | 16346467.4556 | 16395457.4556 | 16444447.4556 | 16493437.4556 | 16542427.4556 | 16591417.4556 | 16640407.4556 | 16689397.4556 | 16738387.4556 | 16787377.4556
10MW/20MWh | 16142911.8758 | 16200130.1258 | 16257348.3758 | 16314566.6258 | 16371784.8758 | 16429003.1258 | 16486221.3758 | 16543439.6258 | 16600657.8758 | 16657876.1258 | 16715094.3758
10MW/40MWh | 16562311.1576 | 16616855.6576 | 16671400.1576 | 16725944.6576 | 16780489.1576 | 16835033.6576 | 16889578.1576 | 16944122.6576 | 16998667.1576 | 17053211.6576 | 17107756.1576